2022-04-29 09:46 | NO | NO | NO | 20220003 | 36421 | 2022-01-07 14:10 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-12-08 16:43 | EASTERN | YES | 2021 | E. 11 MILE ROAD | ROYAL OAK | OAKLAND | MI | 48067 | 42.4899 | -83.1414 | [5 empty] | YES |  |  |  | 2021-12-08 23:49 | 1324037 | 1324232 | NATURAL GAS |  | 3421 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-12-08 16:43 | NO |  |  | 2021-12-08 17:08 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | UNKNOWN |  |  |  |  | 4 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 3 | 9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 575 | 575 | 15392 | 15392 | 0 | 0 |  | 4.18 | 14300 | 14300 | 0 | 0 | 30267 | 23653.8980107119 | 30267 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 2016-07-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | WATER | YES | B013270027 |  | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO MAINTAIN CLEARANCE | [169 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON WEDNESDAY, DECEMBER 8, 2021 AT APPROXIMATELY 16:43 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE EXCAVATION DAMAGE FROM THE CONTRACTOR PERFORMING (BORING) WORK IN THE 300 BLOCK OF ELEVEN MILE ROAD, ROYAL OAK, (OAKLAND COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:08 HOURS AND CONFIRMED A DAMAGED AND BLOWING 4-INCH NATURAL GAS PIPELINE AT 315 ELEVEN MILE ROAD. DISTRIBUTION EMPLOYEES WERE DISPATCHED AT 17:02 HOURS AND ARRIVED ONSITE AT APPROXIMATELY 18:34 HOURS. THE DISTRIBUTION CREW EXCAVATED AT REMOTE LOCATIONS AND APPLIED SQUEEZERS TO CONTAIN THE BLOWING GAS. THE DAMAGED PIPELINE SEGMENT WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FOOT OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE AND NORMAL OPERATIONS RESUMED ON THURSDAY, DECEMBER 9, 2021 AT APPROXIMATELY 14:00 HOURS. THREE COMMERCIAL CUSTOMERS EXPERIENCED A LOSS OF SERVICE AS A RESULT OF THE DAMAGE AND SUBSEQUENT REPAIR. CONSUMERS ENERGY SERVICE EMPLOYEES REMAINED ONSITE AND CONTINUOUSLY MONITORED THE LOCATION UNTIL THE GAS WAS CONTAINED AND THE PIPELINE SEGMENT WAS REPAIRED. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE DAMAGE.
2022-04-29 09:46 | NO | YES | NO | 20220004 | 36224 | 2022-01-08 15:17 | SUPPLEMENTAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2021-12-09 09:19 | CENTRAL | NO | 2021 | 3111 WYANDOTTE ST | KANSAS CITY | JACKSON | MO | 64111 | 39.0707 | -94.5884 |  | YES |  |  |  |  | YES |  |  | 2021-12-09 11:14 | 1324107 | 13242511324239 | NATURAL GAS |  | 9519 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2021-12-09 09:19 |  |  |  | 2021-12-09 09:45 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | UNKNOWN |  |  |  |  | 20 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 2.3 | [7 empty] | CLASS 3 LOCATION | 196989 | 196989 | 0 | 0 | 500 | 500 | 0 | 0 |  | 4.1195 | 39214 | 39214 | 0 | 0 | 236703 | 134039.146856181 | 236703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 63 | 100 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 213344010 |  | CONTRACT LOCATOR | NO | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO MAINTAIN THE MARKS | [169 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY CONTRACTOR WAS PERFORMING SEWER WORK AND WHILE BREAKING OUT A SEWER BOX THE COMPANY'S 20-INCH COATED STEEL GAS MAIN WAS STRUCK RESULTING IN A LEAK. A TEMPORARY REPAIR WAS MADE BY INSTALLING A STYLE 126 REPAIR SLEEVE. A PERMANENT REPAIR WAS MADE BY INSTALLING STOPPER FITTINGS TO ISOLATE THE SECTION OF MAIN AND REPLACE 13-FEET OF 20-INCH COATED STEEL MAIN. THE COMPANY'S FACILITIES WERE ACCURATELY MARKED ON DECEMBER 2, 2021 BUT WERE NO LONGER VISIBLE THE DAY OF THE INCIDENT. THE EXCAVATOR DID NOT REQUEST A RENEWAL OF THE LOCATE MARKS. A 48 HOUR UPDATE TO THE NRC WAS MADE ON DECEMBER 9, 2021 AT 15:46. REPORT NUMBER 1324251.
2022-04-29 09:46 | NO | NO | NO | 20220005 | 36217 | 2022-01-10 09:47 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-12-16 12:13 | EASTERN | YES | 2021 | 7224 ANNAPOLIS RD | HYATTSVILLE | PRINCE GEORGE COUNTY | MD | 20784 | 38.9481 | -76.89 |  | YES | [7 empty] | 2021-12-16 14:11 | 1324714 |  | NATURAL GAS |  | 67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-16 11:44 | OPERATOR/CONTRACTOR |  | 67 | NO | 8 | 2021-12-16 12:13 |  |  |  | 2021-12-16 12:53 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN FREQUENCY OR SEAMLESS | UNKNOWN | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC BURNT HOLE IN THE PIPE. SEE DESCRIPTION IN NARRATIVE. | CLASS 4 LOCATION | 500 | 500 | 108 | 108 | 8400 | 8400 | 383 | 383 | ADMINISTRATION COSTS | 3.01 | 202 | 202 | 0 | 0 | 9593 | 4459.05500301702 | 9593 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 25 | 192.619(A)(4) | 1970-11-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" WRPD NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [111 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [147 empty] | YES | [20 empty] | MARK AIESI | SUPERVISOR DOT PIPELINE SAFETY | mark.aiesi@washgas.com | 5714054623 |  | MARK AIESI | mark.aiesi@washgas.com | 5714054623 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON DECEMBER 16, 2021 AT APPROXIMATELY 1213 HOURS WASHINGTON GAS WAS NOTIFIED OF A GAS FED FIRE IN FRONT OF 7224 ANNAPOLIS ROAD, HYATTSVILLE, MD. WASHINGTON GAS DISPATCHED CREWS TO THE LOCATION WHO ARRIVED AND PERFORMED AN ASSESSMENT OF SITUATION, WHICH RESULTED IN THE IDENTIFICATION OF AN 8" WRPD MAIN LINE THAT WAS FEEDING THE CONTROLLED FIRE. NO WASHINGTON GAS CREWS, OR CONTRACTORS WERE WORKING AT THIS LOCATION AT THE TIME OF IGNITION. IT WAS DETERMINED THAT A TRANSFORMER SHORTED AT SURREY LANE AND ANNAPOLIS ROAD, WHICH RESULTED IN AN ELECTRICAL DISCHARGE THROUGH AN ADJACENT METAL FENCE INTO THE GROUND. THE METAL FENCE THAT IS ESTIMATED TO BE ROUGHLY 20 YEARS OLD WAS INSTALLED DIRECTLY OVER THE 8" WRPD MAIN. EVIDENCE SUGGESTS THAT THE ELECTRICAL DISCHARGE FROM THE TRANSFORMER TRAVELED DOWN THE FENCE AND DISCHARGED AT 7224 ANNAPOLIS ROAD, RESULTING IN AN ELECTRICAL ARC TO THE PIPE. THE GAS WAS TURNED OFF UTILIZING VALVES WHICH EXTINGUISHED THE FIRE. ONCE THE AREA WAS DEEMED SAFE, CREWS STARTED PERMANENT REPAIRS TO THE PIPE, INCLUDING ADDING NEW CATHODIC PROTECTION ANODES AND A TEST STATION. THE PIPE WAS REPAIRED USING A FULL SEAL CLAMP AND WAS NOT ABLE TO BE EXAMINED FOR PIPE SPECIFICATION AND WALL THICKNESS AS A RESULT. THERE WAS ONLY MINOR PROPERTY DAMAGE, WHICH WAS TO THE CHAIN LINK FENCE THAT HAD TO BE REMOVED TO REPAIR THE MAIN.
2022-04-29 09:46 | NO | YES | NO | 20220006 | 36261 | 2022-01-20 23:52 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2021-12-21 08:52 | MOUNTAIN | NO | 2021 | 5723 SHADY OAKS DRIVE | WINDSOR | LARIMER | CO | 80528 | 40.4833 | -104.9838 | [5 empty] | YES |  |  |  | 2022-01-06 12:58 | 1326030 | 1326116 | NATURAL GAS |  | 299 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-21 08:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 299 | NO | 0 | 2021-12-21 08:52 | YES | OPERATOR | 2021-12-21 08:53 | 2021-12-21 08:52 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 17 |  |  | 2708 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 700000 | 700000 | 21219 | 21219 | 2000 | 2000 | 0 | 0 |  | 5.02 | 1501 | 1501 | 0 | 0 | 724720 | 327214.157005001 | 724720 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2021-01-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | NO | [5 empty] | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [171 empty] | MARK NOLAN | PRINCIPAL ENGINEER | mark.nolan@xcelenergy.com | 303.571.3931 |  | TAMMY BOWIE | tammy.l.bowie@xcelenergy.com | 970-225-7865 | CHRIS AKINS | MANAGER PIPELINE COMPLIANCE | 303.571.3298 | christopher.a.akins@xcelenergy.com | A CONTRACTOR FOR HOME BUILDER WAS DIGGING TO LOWER WATER PIT WHEN 4" PE MAIN WAS DAMAGED AND BLOWING GAS IGNITED. NO LOCATE REQUEST WAS MADE; EXCAVATOR WAS DIGGING OFF OLD UTILITY MARKS. THE DAMAGED HOME AND SERVICE INTERRUPTIONS OCCURRED ON HOMES THAT WERE NOT YET SOLD OR OCCUPIED. LOCAL OPERATIONS OBSERVED THE FIRE AND RESPONDED TO SCENE BEFORE BEING NOTIFIED BY OUR DISPATCH OR LOCAL FIRE DEPARTMENT. A21A IGNITION TIME IS ESTIMATED, BUT GAS HAD IGNITED PRIOR TO OUR PERSONNEL'S ARRIVAL ON SCENE. D2A PROPERTY DAMAGE IS ESTIMATED.
2022-04-29 09:46 | NO | YES | NO | 20220007 | 36305 | 2022-02-04 19:20 | ORIGINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-01-06 23:39 | PACIFIC | NO | 2022 | 4244 BULLFROG RD | CLE ELUM | KITTITAS | WA | 98922 | 47.2041 | -120.9831 |  |  |  | YES | [5 empty] | 2022-01-06 20:39 | 1326070 | 1326135 | NATURAL GAS |  | 112 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-01-06 14:13 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 9 | NO | 0 | 2022-01-06 14:41 |  |  |  | 2022-01-06 15:30 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2008 | 2008 | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | EQUIPMENT BODY SEPARATED BY EXTERNAL LOAD | CLASS 4 LOCATION | 510450 | 500367.458988952 | 9457 | 9270.20287914295 | 1583 | 1551.73217274858 | 0 | 0 |  | 11 | 1232 | 1232 | 0 | 0 | 522722 | 231480.190809836 | 512421.394040844 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 50 | 60 | 192.619(A)(2) | 2008-05-02 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 8.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | HEAVY SNOWFALL | [212 empty] | MICHAEL KIDD | REGULATORY COMPLIANCE ANALYST | michael.kidd@pse.com | [5 empty] | YVONNE WANG | SUPERVISOR COMPLIANCE SUPPORT | 425-424-7477 | yvonne.wang@pse.com | ON JANUARY 6, 2022, CLE ELUM FIRE DEPARTMENT CALLED PSE AT 14:41 NOTIFYING OF A FIRE AT A COMMERCIAL METER SET THAT PROVIDED TWO PSIG TO A LAUNDRY BUSINESS. PSE'S GAS FIRST RESPONSE (GFR) PERSONNEL ARRIVED ONSITE AT 15:30 AND FOUND THAT THE OUTLET VALVE AT THE METER SET HAD BEEN TURNED OFF PRIOR TO THEIR ARRIVAL. THE FIRE HAD ALREADY BEEN EXTINGUISHED BY CLE ELUM FIRE DEPARTMENT. PSE'S GFR MADE THE SITUATION SAFE AND LOCKED OFF THE MSA VALVE AT 19:30 ON JANUARY 6, 2022. PSE'S CONTRACTOR INFRASOURCE (IFS) CUT AND CAPPED THE SERVICE ON JANUARY 7, 2022 AT 19:41. ONE CUSTOMER LOST SERVICE AND NO EVACUATION WAS REQUIRED. NO INJURIES OR FATALITIES OCCURRED IN CONNECTION TO THIS INCIDENT. THE CAUSE OF THE FIRE IS UNKNOWN AT THIS TIME AND UNDER INVESTIGATION. PSE NOTIFIED THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION (WUTC) ON JANUARY 6, 2022 AT 17:30 DUE TO UNINTENTIONAL IGNITION OF GAS. PSE MADE FIRST TELEPHONIC NOTICE TO DOT ON JANUARY 6, 2022 AT 20:39, NRC # 1326070 DUE TO ESTIMATED PROPERTY DAMAGES EXCEEDING $ 122,000. THE SECOND TELEPHONIC NOTICE WAS MADE TO DOT WITHIN 48 HOURS ON JANUARY 7, 2022 AT 16:22, NRC # 1326135.
2022-04-29 09:46 | NO | YES | NO | 20220008 | 36543 | 2022-02-07 11:14 | SUPPLEMENTAL | 7348 | DOMINION ENERGY WEST VIRGINIA | 48 COLUMBIA BLVD | CLARKSBURG | WV | 26301 | 2022-01-08 20:00 | EASTERN | NO | 2022 | 305 POWELL STREET | GLENVILLE | GILMER | WV | 26351 | 38.9327 | -80.8371 |  | YES | [7 empty] | 2022-01-08 21:10 | 1326175 | 1326260 | NATURAL GAS |  | 7446 | 4265 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-08 11:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-08 12:00 | 2022-01-08 12:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1947 | UNKNOWN |  |  |  |  | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 161269 | 158083.572815534 | 0 | 0 | 66868 | 65547.2058921995 | 0 | 0 |  | 3.361 | 25026 | 25026 | 14335 | 14335 | 267498 | 145973.572219413 | 262991.778707734 | 51 | 0 | 111 | 0 | 0 | 111 | 51 | 2.18 | 0.5 | 0.75 | 192.623 | 1947-11-08 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE ALREADY MONITORING SYSTEM PRESSURES DUE TO COLD WEATHER AND WERE AWARE OF THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [196 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [40 empty] | YES |  | YES | [30 empty] | CHELSEA MINUTELLI | GAS PIPELINE COMPLIANCE ANALYST | chelsea.m.minutelli@dominionenergy.com | 3046769284 |  | CHELSEA MINUTELLI | chelsea.m.minutelli@dominionenergy.com | 3046769284 | CAROL HAGER | MANAGER- GAS OPERATIONS PIPELINE INTEGRITY | 3304379557 | carol.m.hager@dominionenergy.com | ON 1/8/2022, DEWV PERSONNEL WERE MONITORING SYSTEM PRESSURES BECAUSE OF COLD WEATHER. IN THE COURSE OF DOING THIS, THEY IDENTIFIED A PRESSURE INCREASE FROM 8 OUNCES TO 10 OUNCES AT 11:00 HOURS; AND ANOTHER INCREASE FROM 10 OUNCES TO 35 OUNCES AT 12:00 HOURS. THE PRESSURE RETURNED TO 8 OUNCES AT 13:00 HOURS, WHICH IS BELIEVED TO BE FROM AN INCREASE IN TEMPERATURE RELIEVING MOISTURE AND ICE FROM THE REGULATORS. DURING THE EVENT, A LEAK WAS DISCOVERED ON A MAINLINE. THREE REGULATING STATIONS THAT FEED THE SYSTEM WERE SHUT IN, CREATING AN OUTAGE FOR 162 CUSTOMERS. THE MAINLINE LEAK WAS REPAIRED, THE SYSTEM WAS LEAK SURVEYED WITH NO ADDITIONAL HAZARDOUS LEAKS FOUND, AND SAFETY CHECKS AND RESTORATION OF CUSTOMERS WERE INITIATED BEGINNING ON THE MORNING OF 1/9/2022. SUPPLEMENTAL REPORTS WILL BE SUBMITTED FOR PENDING FINAL COSTS.
2022-04-29 09:46 | NO | NO | NO | 20220009 | 36309 | 2022-02-08 12:13 | ORIGINAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2021-02-23 11:55 | EASTERN | NO | 2021 | GATEWAY BLVD. & WESLEY CHAPEL BLVD. | WESLEY CHAPEL | PASCO | FL | 33544 | 28.2382 | -82.3616 |  |  |  | YES | [5 empty] | 2022-02-08 08:10 | 1328385 |  | NATURAL GAS |  | 357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-23 11:55 |  |  |  | 2021-02-23 11:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 80 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 31000 | 31000 | 42478 | 42478 | 0 | 0 |  | 9 | 3213 | 3213 | 0 | 0 | 76691 | 36768.9662826196 | 76691 | 50 | 0 | 821 | 0 | 0 | 821 | 50 | 45 | 45 | 60 | 192.619(A)(2) | 2004-12-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A 3RD PARTY LINE STRIKE TO OPERATOR'S SYSTEM, AND AS SUCH, THE CONTROLLER(S) OR CONTROL ROOM WERE NOT THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 028100002 | SUNSHINE STATE ONE CALL OF FLORIDA | FACILITY OWNER | YES | YES | YES | 18 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | [5 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 4074206667 | rharris@tecoenergy.com | THIRD PARTY CONTRACTOR STRUCK PEOPLES GAS SYSTEM'S MAIN DURING HDD OPERATION. UPON ARRIVAL ON SCENE AFTER THE REPORT OF THE DAMAGE, THE OPERATOR DID NOT IDENTIFY ANY PHYSICAL EVIDENCE THAT THE THIRD PARTY PERFORMED SPOT DIGGING TO IDENTIFY THE UTILITIES. PIPELINE WAS TOO DEEP TO DIG UP AND SQUEEZE, SO OPERATOR TURNED OFF CRITICAL VALVE STOPPING FLOW OF GAS. PRETESTED PIPELINE WAS INSTALLED, REPAIRS FINALIZED, AND RESTORATION COMPLETED.
2022-04-29 09:46 | NO | YES | NO | 20220010 | 36314 | 2022-02-08 16:05 | ORIGINAL | 12672 | MONROE NATURAL GAS DEPT, CITY OF | 300 W. CROWELL STREET | MONROE | NC | 28112 | 2022-01-04 17:15 | EASTERN | NO | 2022 | INTERSECTION OF ROCKY RIVER RD AND SECREST SHORT CUT RD. | MONROE | UNION | NC | 28110 | 35.0571 | -80.5936 | YES | [8 empty] | 2022-01-04 18:00 | 1325889 | 1326041, 1326048 | NATURAL GAS |  | 4266.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-04 15:09 | YES | OPERATOR | 2022-01-04 15:13 | 2022-01-04 15:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 127 | NO | YES |  |  |  |  | YES | CASED, BORED/DRILLED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2006 | 2004 |  |  |  |  | 6 | API 5L GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 52266 | 51233.6283896886 | 0 | 0 | 0 | 0 |  | 16.8755 | 71999 | 71999 | 0 | 0 | 124265 | 105972.057740491 | 123232.628389689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 265 | 275 | 192.619(A)(1) | 2006-03-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 5.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | BORING | WATER | YES | C213551031 | N/A | FACILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | DARWIN DE LOS SANTOS | NATURAL GAS ENGINEERING AND COMPLIANCE MANAGER | ddelossantos@monroenc.org | 7042824697 | 704-283-6492 | ROBERT MILLER | rmiller@monroenc.org | 704-282-4638 | DAVID LUCORE | DIRECTOR OF ENERGY SERVICES | 704-282-4602 | dlucore@monroenc.org | ON 01/04/2022 AT 3:09 PM - CDM SMITH STRUCK THE CITY OF MONROE'S 6-INCH STEEL 275 PSIG GAS MAIN WHILE MAKING A BORE ACROSS THE INTERSECTION OF ROCKY RIVER ROAD AND SECREST SHORTCUT ROAD IN MONROE NC. THE BORE WAS FOR THE INSTALLATION OF A 42 INCH WATER MAIN WITHIN A 54" CASING. THE GAS MAIN WAS PROPERLY LOCATED AND THE CONTRACTOR FAILED TO PERFORM DUE DILIGENCE IN ACCORDANCE WITH NORTH CAROLINA GENERAL STATUTES CHAPTER 87 ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT. THE GAS MAIN WAS RUPTURED BY THE AUGER BORE MACHINE CAUSING THE RELEASE OF NATURAL GAS AND REQUIRING THE REPAIR OF THE GAS LINE. REPAIRS TO THE CITY OF MONROE NATURAL GAS MAIN WERE FINALIZED ON 01/06/2022 AT 3:30 AM. ON 1/04/2022 AT 05:15 PM THE CITY OF MONROE DETERMINED THAT THE INCIDENT REPORTING THRESHOLD WAS GOING TO BE MET BEFORE THE FACILITIES COULD BE REPAIRED. THEREFORE A DETERMINATION OF FILING THE INITIAL INCIDENT WITH NRC WAS MADE. THE NRC NOTIFICATION WAS MADE AT APPROXIMATELY 6:00 PM ON 1/4/2022. THE ACTUAL INCIDENT THRESHOLD OF 3,000 MCF WAS NOT MET UNTIL APPROXIMATELY 1/05/2022 AT APPROXIMATELY 05:26 AM. CDM WAS NEGLIGENT IN THE FOLLOWING REQUIREMENTS: NC ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT - 87-122. EXCAVATOR RESPONSIBILITIES C) AN EXCAVATOR SHALL COMPLY WITH THE FOLLOWING: (3) PLAN THE EXCAVATION OR DEMOLITION TO AVOID DAMAGE TO OR MINIMIZE INTERFERENCE WITH FACILITIES IN OR NEAR THE CONSTRUCTION AREA. (9) AN EXCAVATOR SHALL NOT PERFORM ANY EXCAVATION OR DEMOLITION WITHIN THE TOLERANCE ZONE UNLESS THE EXCAVATOR COMPLIES WITH ALL OF THE FOLLOWING CONDITIONS: A. THE EXCAVATOR SHALL NOT USE MECHANIZED EQUIPMENT, EXCEPT, NONINVASIVE EQUIPMENT SPECIFICALLY DESIGNED OR INTENDED TO PROTECT THE INTEGRITY OF THE FACILITY, WITHIN THE MARKED TOLERANCE ZONE OF AN EXISTING FACILITY UNTIL: 1. THE EXCAVATOR HAS VISUALLY IDENTIFIED THE PRECISE LOCATION OF THE FACILITY OR HAS VISUALLY CONFIRMED THAT NO FACILITY IS PRESENT UP TO THE DEPTH OF EXCAVATION; 2. THE EXCAVATOR HAS TAKEN REASONABLE PRECAUTIONS TO AVOID ANY SUBSTANTIAL WEAKENING OF THE FACILITY'S STRUCTURAL OR LATERAL SUPPORT, OR BOTH, OR PENETRATION OR DESTRUCTION OF THE FACILITIES OR THEIR PROTECTIVE COATINGS: B. THE EXCAVATOR SHALL MAINTAIN CLEARANCE BETWEEN A FACILITY AND THE CUTTING EDGE POINT OF ANY MECHANIZED EQUIPMENT, TAKING INTO ACCOUNT THE KNOWN LIMIT OF CONTROL OF THE CUTTING EDGE OR POINT, AS MAY BE REASONABLY NECESSARY TO AVOID DAMAGE TO THE FACILITY. THE CITY OF MONROE ACCURATELY MARKED THE 6-INCH STEEL GAS LINE. CDM SMITH DID NOT COMPLY WITH THE REQUIREMENTS WITHIN THE TOLERANCE ZONE. CDM SMITH DID NOT VISUALLY INSPECT THE GAS FACILITY AT THE DEPTH OF THE EXCAVATION. CDM SMITH IS RESPONSIBLE FOR THE DAMAGE DUE TO NEGLIGENCE AND NON-COMPLIANCE WITH THE NC UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT.
2022-04-29 09:46 | NO | NO | NO | 20220011 | 36473 | 2022-02-14 15:41 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-01-28 06:38 | EASTERN | NO | 2022 | FERN HOLLOW BRIDGE | PITTSBURGH | ALLEGHENY | PA | 15221 | 40.4396 | -79.8995 | YES | [8 empty] | 2022-01-28 07:50 | 1327481 | 1327626 | NATURAL GAS |  | 871 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-28 06:38 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-28 07:30 | 2022-01-28 07:05 | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | PIPE THRU BRIDGE SUPPORT AND UNDERGROUND |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 16 | API-5L-B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 16 |  | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 22321 | 21880.1098091731 | 0 | 0 |  | 10.3951 | 9054 | 9054 | 0 | 0 | 31375 | 20273.7883971945 | 30934.1098091731 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 45 | 45 | 50 | 192.619(A)(1) | 1972-10-29 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCENTINEL T50 | 0.4 |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CASUAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE. PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [154 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | manager compliance | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412 258-4453 | edward.a.palombo@peoples-gas.com | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CAUSAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE AS THE EVIDENCE GATHERED TO DATE SUGGESTS THE PIPELINE WAS DAMAGED BY THE COLLAPSE. WHEN ALSO CONSIDERING THE RESPONSE TO THE RUPTURE STABILIZED THE SITUATION BEFORE ANY FIRE OR EXPLOSION EVENTS, THE NTSB SEES NO NEED TO CONDUCT ANY FURTHER EXAMINATION OF THE PIPE OR RELATED MATERIALS AND WILL NOT BE SECURING ANY SUCH MATERIALS FOR LATER TESTING. TEN PEOPLE WERE INJURED AS A RESULT OF THE BRIDGE COLLAPSE. NO INJURIES RELATED TO THE PIPELINE. THE PIPELINE WAS DAMAGED AT BOTH SIDES OF THE FERN HOLLOW BRIDGE: WEST SIDE ( 40.439536, -79.901115 ) AND EAST SIDE ( 40.439621, -79.899509 ).
2022-04-29 09:46 | NO | YES | YES | 20220013 | 36356 | 2022-02-17 21:08 | ORIGINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2022-01-18 11:10 | EASTERN | YES | 2022 | 869 FOX STREET | BRONX | BRONX COUNTY | NY | 10469 | 40.8186 | -73.8956 |  | YES |  | YES |  | YES |  |  |  | 2022-01-18 12:54 | 1326802 | 1326954 | NATURAL GAS |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2022-01-18 11:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-01-19 10:39 |  |  |  | 2022-01-18 11:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | UNKNOWN | UNKNOWN | [7 empty] | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [9 empty] | LEAK |  |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [5 empty] | CLASS 4 LOCATION | 50000 | 49012.3870103783 | 0 | 0 | 2824 | 2768.21961834617 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 52824 | 23303.9256779378 | 51780.6066287245 | 0 | 0 | 18 | 0 | 10 | 18 | 0 | 0.25 | 0.25 | 0.5 | 192.619(A)(2) | 1910-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO JURISDICTIONAL INVOLVEMENT | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | leono@coned.com | 7183192350 | 718-904-4607 | OSCAR LEON | leono@coned.com | 7183192350 | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 7183192350 | leono@coned.com | ON 1/18/22 AT 11:10, CON EDISON'S GERC RECEIVED A REPORT FROM THE FDNY OF AN ACTIVE BUILDING FIRE AND EXPLOSION AT 850 FOX STREET IN THE BRONX, WITH FDNY PERSONNEL ON LOCATION. NATURAL GAS WAS NOT REPORTED TO BE INVOLVED. CON EDISON GDS, GAS CONSTRUCTION, AND GAS ERG AND SUPERVISION WERE DISPATCHED TO THE LOCATION BY THE GERC. CON EDISON GAS ENGINEERING WAS NOTIFIED AND DEVELOPED AN ISOLATION PLAN INVOLVING CLOSURE OF DISTRIBUTION MAIN VALVE (MV) 94461 AND EXCAVATION OF A FIRE BANK AT INTERVALE AVENUE AND FOX STREET, OVER A 4-INCH LPPE GAS MAIN (INSTALLED IN 1988). CON EDISON GAS CONTROL WAS NOTIFIED AND REPORTED NORMAL OPERATING CONDITIONS AT NEARBY GAS REGULATOR STATION GR-128. AT 11:19, GDS ARRIVED AND BEGAN INVESTIGATING. GDS CORRECTED THE ADDRESS TO 869 FOX STREET AND CONFIRMED THAT A BUILDING EXPLOSION HAD OCCURRED AT THAT LOCATION. GDS ALSO REPORTED HAVING NO ACCESS TO THE HOS VALVE OR OUTDOOR METER SET AT 869 FOX STREET, WHICH IS SUPPLIED BY A 1 1/4-INCH LPPE GAS SERVICE LINE (INSTALLED IN 1986). GERC PROVIDED GDS WITH THE LOCATION OF MV 94461 (AT THE INTERSECTION OF TIFFANY STREET & FOX STREET). AT 11:48, GDS CLOSED MV 94461 TO BEGIN ISOLATING AND SHUTTING DOWN THE GAS MAIN. CON EDISON GAS CONSTRUCTION CREWS ARRIVED AND BEGAN EXCAVATING A FIRE BANK OVER THE 4-INCH LPPE GAS MAIN AT THE SOUTHEAST CORNER OF INTERVALE AVENUE AND FOX STREET. GDS CONDUCTED A SPECIAL SURVEY OF THE AREA AND DID NOT DETECT ANY NATURAL GAS LEAKS OR ODORS. ALL SUBSURFACE STRUCTURES AND TEST POINTS CHECKED DURING THE SPECIAL SURVEY WERE FOUND CLEAR OF NATURAL GAS READINGS. THE SPECIAL SURVEY WAS CONDUCTED WHILE THE GAS MAIN AND SERVICE LINES ON THE BLOCK WERE IN SERVICE AND BEFORE THEY WERE SHUT DOWN. GDS ALSO TOOK PRESSURE AND ODORANT READINGS AT 858 FOX STREET; BOTH WERE WITHIN ACCEPTABLE RANGE (7.9 INCHES WC FOR PRESSURE; 0.29% GAS-IN-AIR FOR ODORANT). AT 13:03, CON EDISON GAS CONSTRUCTION CREWS INSTALLED A SQUEEZE-OFF ON THE 4-INCH LPPE GAS MAIN IN THE FIRE BANK EXCAVATION, SHUTTING DOWN THE MAIN AND INTERRUPTING GAS SERVICE TO 18 SINGLE-FAMILY BUILDINGS. GAS CONSTRUCTION CREWS THEN CUT AND CAPPED THE SERVICE LINES SUPPLYING 865, 867 AND 869 FOX STREET. AT 18:48, GDS OPENED MV 94461, REINTRODUCING GAS INTO THE MAIN UP TO THE SQUEEZE-OFF. GDS CONDUCTED A DP-IR SURVEY OVER THE MAIN AND SERVICES LINES AND DID NOT DETECT ANY LEAKS. AT 19:08, GDS REMOVED THE SQUEEZE-OFF AND PERFORMED AN ADDITIONAL DP-IR SURVEY OF THE MAIN AND SERVICE LINES WITHOUT DETECTING ANY LEAKS. RESTORATION WAS COMPLETED AT 20:52. ON 1/18/22 AT 17:40, NYPD ARSON AND EXPLOSION SQUAD DETECTIVE DIMARE REPORTED THAT THE SOURCE OF THE EXPLOSION WAS UNKNOWN AND UNDER INVESTIGATION. ON 1/19/22 AT 10:39, FDNY CHIEF SAROCCO REPORTED THAT NATURAL GAS WAS BELIEVED TO BE INVOLVED WITH THE EXPLOSION. THERE IS, HOWEVER, NO INDICATION OF CON EDISON JURISDICTIONAL PIPING BEING INVOLVED AT THIS TIME. THIS INCIDENT REMAINS UNDER INVESTIGATION BY THE FDNY AND NYPD. THE EXPLOSION RESULTED IN TEN INJURIES AND ONE FATALITY, AND GREATER THAN $50,000 IN PROPERTY DAMAGE. PHSMA, DPS STAFF, AND NYCDEP WERE NOTIFIED AND UPDATED. NTSB INQUIRED AND WAS UPDATED. MEDIA WAS ON LOCATION.
2022-04-29 09:46 | YES | NO | NO | 20220014 | 36371 | 2022-02-22 17:24 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-01-23 00:26 | EASTERN | YES | 2022 | 228 W. WALTON BOULEVARD | PONTIAC | OAKLAND | MI | 48340 | 42.6783 | -83.309 | [7 empty] | YES | SERVICE TEE WAS TURNED DOWN SHUTTING OFF GAS FLOW | 2022-01-23 02:53 | 1327106 | 1327152 | NATURAL GAS |  | 101 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-01-23 00:26 | ALLOWED TO BURN OUT |  | 101 | YES | 0 | 2022-01-23 00:26 |  |  |  | 2022-01-23 01:13 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1992 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 299900 | 293976.297288249 | 1848 | 1811.49782390358 | 156 | 152.91864747238 | 0 | 0 |  | 3.41 | 344 | 344 | 0 | 0 | 302248 | 133584.633692551 | 296284.713759625 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 55 | 60 | 192.619(A)(2) | 1992-04-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [111 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON SUNDAY, FEBRUARY 23, 2022 AT APPROXIMATELY 00:26 HOURS CONSUMERS ENERGY WAS NOTIFIED OF AN EXPLOSION AT 228 W. WALTON BOULEVARD, PONTIAC (OAKLAND COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AT 00:29 HOURS AND ARRIVED AT THE SITE AT APPROXIMATELY 01:13 HOURS AND CONFIRMED AN EXPLOSION AND SUBSEQUENT FIRE OCCURRED AT THE ADDRESS. DUE TO THE WALL COLLAPSING ONTO THE METER THE GSW COULD NOT ACCESS THE METER AND A DISTRIBUTION CREW WOULD BE NEEDED TO RETIRE THE NATURAL GAS SERVICE LINE. THE CREW ARRIVED AT THE SITE AT APPROXIMATELY 01:55 HOURS, AN AREA WAS EXCAVATED NEAR THE SERVICE TEE ON THE MAIN. THE SERVICE WAS TURNED DOWN STOPPING THE GAS FROM BLOWING FROM THE CUSTOMER FUEL LINE INSIDE THE STRUCTURE. CONSUMERS ENERGY GSW PERFORMED A LEAK INVESTIGATION AT LOCATIONS SAFE TO ACCESS AND CONTINUED WITH THE INVESTIGATION NEAR THE STRUCTURE ONCE THE FIRE WAS EXTINGUISHED. NO UNDERGROUND GAS READS WERE DISCOVERED AT THE ACCESSIBLE LOCATIONS AND NO VISIBLE IGNITION OR GAS RELEASE AT THE REGULATED FACILITIES WAS OBSERVED BY CONSUMERS ENERGY EMPLOYEES WHILE ONSITE. DUE TO INCLEMENT WEATHER CONDITIONS FURTHER INVESTIGATION WAS POSTPONED UNTIL THE JOINT SCENE INVESTIGATION CAN BE SAFELY CONDUCTED. THE JOINT SCENE INVESTIGATION HAS BEEN SCHEDULED FOR MARCH 17TH & MARCH 18TH.
2022-04-29 09:46 | NO | YES | NO | 20220015 | 36377 | 2022-02-23 19:59 | ORIGINAL | 6243 | HAWAII GAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2022-01-24 11:15 | HAWAII-ALEUTIAN | NO | 2022 | WAIAKAMILO ROAD (BETWEEN HART ST & KALANI ST) | HONOLULU | HONOLULU | HI | 96817 | 21.3224 | -157.8782 | YES | [8 empty] | 2022-01-24 12:30 | 1327229 | 1327369 and 1327376 | SYNTHETIC GAS |  | 550 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 100 | 2022-01-24 09:02 | YES | OPERATOR | 2022-01-24 10:19 | 2022-01-24 09:15 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.625 | [6 empty] | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 4 LOCATION | 100000 | 98024.7740207566 | 25000 | 24506.1935051891 | 20000 | 19604.9548041513 | 0 | 0 |  | 46.67 | 25669 | 25669 | 0 | 0 | 170669 | 93528.9568060234 | 167804.922330097 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | 33 | 50 | 192.619(C) | 1999-03-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | AUGER | SEWER (SANITARY/STORM) | YES | 22000022 |  | UNKNOWN/OTHER | YES | NO | NO |  | OTHER | SUBJECT TO INVESTIGATION | [172 empty] | CHRISTOPHER HALL | IMP ENGINEER | chall@hawaiigas.com | 808-594-5553 |  | CHRIS HALL | chall@hawaiigas.com | 808-594-5553 | KEVIN NISHIMURA | VICE PRESIDENT OPERATIONS | 808-594-5573 | knishimu@hawaiigas.com | INCIDENT SUMMARY ON MONDAY, JANUARY 24, 2022, FRANK COLUCCIO CONSTRUCTION ("FCC") WAS PERFORMING A SEWER INSTALLATION ON A PORTION OF WAIAKAMILO ROAD IN HONOLULU, HAWAII, WITH AN AUGER. AT APPROXIMATELY 9:02 A.M., ON THE PORTION OF WAIAKAMILO ROAD BETWEEN HART STREET AND KALANI STREET, THE AUGER STRUCK A HAWAI'I GAS ("HG") UNDERGROUND 8-INCH PIPELINE ("SUBJECT SEGMENT"). THE AUGER CAUSED AN APPROXIMATELY 3-INCH LONG FRACTURE ALONG THE TOP OF THE PIPELINE. THE SUBJECT SEGMENT BEGAN TO LEAK GAS. HG'S FIRST RESPONDER ARRIVED ON SITE AT APPROXIMATELY 9:15 A.M. AND CONFIRMED THE DAMAGE TO THE SUBJECT SEGMENT. DUE TO THE MAGNITUDE OF THE LEAK, HG CALLED THE HONOLULU FIRE DEPARTMENT ("HFD") AT APPROXIMATELY 10:19 A.M. TO ASSIST IN SECURING THE ROADWAY AND TO HELP MONITOR THE HOT ZONE. HG'S MAINTENANCE CREW ARRIVED ON SITE AT APPROXIMATELY 10:30 A.M. AND BEGAN ASSESSING REPAIRS. AT APPROXIMATELY 11:15 A.M., HFD BEGAN EVACUATING NEARBY COMMERCIAL BUILDINGS. HG WAS ABLE TO STOP THE FLOW OF GAS TO THE SUBJECT SEGMENT AT APPROXIMATELY 5:35 P.M., JANUARY 24, 2022. FINAL REPAIRS WERE COMPLETED AT APPROXIMATELY 11:00 P.M., JANUARY 24, 2022. HAWAI'I GAS INVOLVEMENT PRIOR TO INCIDENT HG INSTALLED THE SUBJECT SEGMENT IN 1940. THE SUBJECT SEGMENT IS AN 8-INCH BARE STEEL PIPE. HG MAPS AND RECORDS CONTAIN NO INDICATION THAT THE SUBJECT SEGMENT WAS REPAIRED, ALTERED OR EXCAVATED SINCE ITS INSTALLATION. ON MONDAY, JANUARY 3, 2022, FCC SUBMITTED ONE CALL TICKET NUMBER 22000022 TO THE HAWAII ONE CALL CENTER INDICATING THAT FCC WOULD BE EXCAVATING "ON WAIAKAMILO ROAD BETWEEN DILLINGHAM BOULEVARD AND HART STREET (EWA SIDE OF ROAD)" ("EXCAVATION AREA"). IN RESPONSE TO TICKET NO. 22000022, HG REVIEWED GIS MAPS OF THE EXCAVATION AREA AND DETERMINED THAT AN UNDERGROUND MAIN LINE WAS LOCATED WITHIN THAT AREA. ON JANUARY 10, 2022, HG PERSONNEL ATTEMPTED TO PERFORM TONING ON THE UNDERGROUND MAIN LINE IN THE EXCAVATION AREA BUT NOTED THAT THE LOCATION OF THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL. ALSO, PLEASE NOTE THAT THIS INVESTIGATION IS STILL ONGOING.
2022-04-29 09:46 | NO | YES | YES | 20220016 | 36388 | 2022-02-25 10:24 | ORIGINAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-01-27 10:58 | EASTERN | YES | 2022 | 217 BOSWELL RD | BALTIMORE | BALTIMORE COUNTY | MD | 21229 | 39.2819 | -76.7044 | [7 empty] | YES | TWO LEAKING CAST IRON JOINTS WERE ENCAPSULATED AND RENEWED ONE CAST IRON SERVICE AT INCIDENT | 2022-01-27 19:17 | 1327461 | N/A | NATURAL GAS |  | 0.003 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-01-27 10:28 | ALLOWED TO BURN OUT |  | 0 | YES | 0 | 2022-01-27 10:59 |  |  |  | 2022-01-27 11:45 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1920 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 12000 | 11762.9728824908 | 1200 | 1176.29728824908 | 0 | 0 | EMERGENCY RESPONSE PERSONNEL AND EQUIPMENT | 4.45 | 0 | 0 | 0 | 0 | 13200 | 5823.33444928022 | 12939.2701707399 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 10 | 10 | 10 | 192.623 | 1920-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | [145 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | LEAKING CAST IRON JOINT | [11 empty] | YES | GAS FROM A LEAKING CAST IRON JOINT IGNITED CAUSING A MANHOLE COVER TO LIFT STRIKING A BALTIMORE CITY WELDING CONTRACTOR. |  | YES |  |  |  | OTHER | PACKING MATERIAL USED TO SEAL CAST IRON JOINTS DRIED RELEASING NATURAL GAS | NO | [86 empty] | JEFFREY WEATHERHOLTZ | MANAGER - GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-470-8858 | 410-470-9549 |  |  |  | DANIEL A NORDEN | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | 410-470-6435 | daniel.a.norden@bge.com | ON 1/27/2022, A CITY OF BALTIMORE CONTRACTOR WAS WELDING ON A WATER MAIN ON FREDERICK AVENUE NEAR THE INTERSECTION OF BOSWELL ROAD. WHILE PERFORMING THE WELDING OPERATION, AN IGNITION OCCURRED WHICH CAUSED A NEARBY MANHOLE COVER TO RAISE AND STRIKE A NEARBY CONTRACTOR, CAUSING INJURY TO THE CONTRACTOR'S FOOT AND REQUIRING OVERNIGHT IN-PATIENT HOSPITALIZATION. NATURAL GAS WAS CONFIRMED IN THE LOCALIZED AREA AND SURVEYS WERE IMMEDIATELY CONDUCTED TO FIND THE SOURCE OF THE LEAK. AN ADJACENT MEDIUM PRESSURE 12" CAST IRON NATURAL GAS MAIN WAS FOUND TO HAVE TWO LEAKY JOINTS AND THEY WERE SUBSEQUENTLY REPAIRED AS WELL AS RENEWING AN INTERCONNECTED NATURAL GAS SERVICE LINE. POST-INCIDENT SURVEYS WERE COMPLETED, AND NO READINGS WERE DETECTED SUCH THAT THE JOB COULD BE CLOSED OUT.. NOTE : PART A 21C IS NOTED AS 0.0 HOWEVER ACTUAL (MCF) IS 0.003.TO MATCH PART A 7. THIS ONLINE FORM WILL NOT ACCEPT THAT NUMBER.
2022-04-29 09:46 | NO | YES | NO | 20220017 | 36393 | 2022-02-25 16:16 | ORIGINAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2022-01-27 08:10 | CENTRAL | NO | 2022 | 8500 E PARMER LANE | MANOR | TRAVIS | TX | 78653 | 30.3511 | -97.5885 | YES | [8 empty] | 2022-01-27 08:32 | 1327404 | 1327531 | NATURAL GAS |  | 25858 | 0.71 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-27 01:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-27 00:42 | 2022-01-27 01:30 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2016 | 2015 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.237 | [6 empty] | OTHER | [8 empty] | THIRD PARTY VEHICLE STRUCK ABOVE GROUND STATION PIPING AND SHEERED FABRICATION AT 2 CIRCUMFERENTIAL WELDS BETWEEN PIPE AND REDUCERS. | CLASS 1 LOCATION | 0 | 0 | 250000 | 245061.935051891 | 1115 | 1092.97623033144 | 0 | 0 |  | 5.78 | 149459 | 149459 | 4 | 4 | 400578 | 282904.43417467 | 395617.911282223 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 707 | 707 | 778 | 192.621 M | 2016-01-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE TO THE REGULATOR STATION BY THIRD-PARTY VEHICLE INITIATED SCADA ALARMS IN CONTROL ROOM. CONTROLLER FOLLOWED PROCEDURES TO INVESTIGATE ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 60 | YES |  | YES | [116 empty] | YES | [23 empty] | AMY MARK | REGULATORY COMPLIANCE SPECIALIST | amy.mark@onegas.com | 512-407-1571 |  | BRYAN WEEKS | bryan.weeks@onegas.com | 512-407-1529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 512-407-1529 | bryan.weeks@onegas.com | THIRD-PARTY VEHICLE RAN OFF THE ROADWAY TRAVELING WESTBOUND ON EAST PARMER LANE AT A HIGH SPEED AND CRASHED THROUGH FENCING, CONCRETE-FILLED STEEL BOLLARD POSTS WITH WELDED STEEL CROSSBARS, AND THE TEXAS GAS SERVICE (TGS) REGULATOR STATION AT SUBJECT LOCATION BEFORE DAMAGING AND COMING TO REST AGAINST ATMOS ENERGY'S METERING STATION, WHICH FEEDS TGS'S STATION AND DISTRIBUTION SYSTEM. THE VEHICLE'S IMPACT CAUSED THE PIPING TO SEPARATE, LEADING TO AN UNINTENTIONAL RELEASE OF GAS FROM THE INLET AND OUTLET SIDES OF TGS'S REGULATOR STATION. AFTER DAMAGING THE ATMOS ENERGY METERING STATION, THE VEHICLE CAME TO REST ON TOP OF THE ATMOS ENERGY PIPING. ATMOS ENERGY'S MEASUREMENT INSTRUMENTATION WAS DAMAGED AND COULD NOT PROVIDE A VOLUME OF GAS THAT FLOWED THROUGH THE STATION DURING AND AFTER THE INCIDENT. TGS HAS NO KNOWLEDGE OF THE DAMAGE ESTIMATES FOR ATMOS FACILITIES OR THE VEHICLE AT FAULT FOR THE INCIDENT.
2022-04-29 09:46 | NO | YES | NO | 20220018 | 36409 | 2022-03-02 10:16 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 40 SYLVAN RD. | WALTHAM | MA | 02451 | 2022-02-01 07:42 | EASTERN | YES | 2022 | CUMBERLAND HILL RD BET AUGUSTINE ST AND FOUNDERS DR | WOONSOCKET | PROVIDENCE | RI | 02895 | 41.9925 | -71.4864 | [6 empty] | YES |  |  | 2022-02-02 19:28 | 1327936 | 1328004 | NATURAL GAS |  | 8500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 60 | 2022-02-02 11:00 | YES | OPERATOR | 2022-02-01 11:00 | 2022-02-01 11:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 25 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN - POSSIBLE OXYACETYLENE | 0.375 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 27 | 0.1 |  | CLASS 4 LOCATION | 0 | 0 | 300000 | 294074.32206227 | 50000 | 49012.3870103783 | 0 | 0 |  | 7.21 | 61285 | 61285 | 0 | 0 | 411285 | 224982.61565423 | 404371.709072648 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 47.9 | 50 | 60 | 192.621 M | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT CAUSE WAS A CRACK IN A WELD. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [145 empty] | BUTT WELD |  |  | PIPE | [28 empty] | YES | [11 empty] | YES |  |  |  | NO | [55 empty] | YES | [30 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | JOSEPH F. CURLEY | joseph.curley@nationalgrid.com | 4013329815 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | THIS EVENT WAS DISCOVERED IN RESPONSE TO AN ODOR CALL FROM A COMMERCIAL LOCATION AT FORTIN DRIVE IN WOONSOCKET, RI RECEIVED AT APPROX. 11:00 AM ON 2/1/2022. TWO RESPONDERS INITIALLY RESPONDED AND REQUESTED ADDITIONAL SUPPORT TO LOCATE THE LEAK WITH BLOWING GAS AT CUMBERLAND HILL ROAD. ADDITIONAL SUPPORT ARRIVED TO HELP LOCATE THE LEAK AS WELL AS MUTUAL AID PERSONNEL. ADDITIONAL CREWS WORKED OVERNIGHT INTO THE NEXT DAY TO CONTINUE WORK IN LOCATING THE LEAK. ENGINEERING REVIEWED FACILITY MAPS TO DETERMINE THE APPROPRIATE ISOLATION VALVES TO SHUT OFF GAS SUPPLY AND INITIATE REPAIRS WHILE CREWS WORKED TO LOCATE THE IDENTIFIED VALVES; HOWEVER, SIGNIFICANT SNOWFALL FROM 01/28 THROUGH 1/30/22 HINDERED THE CREWS' EFFORTS. DUE TO THE SCOPE OF THE PROJECTED CUSTOMER IMPACT, A DECISION WAS MADE TO ISOLATE THE AFFECTED MAIN USING WELDED STOPPLE FITTINGS. AT 8:00 PM ON 2/2/2022 THE LEAK WAS SECURED. TWO BUILDINGS WERE EVACUATED, WITH AN ESTIMATED 50-60 PEOPLE IN THESE COMMERCIAL PROPERTIES AS ESTIMATED BY THE FD. APPROXIMATELY 5'6" OF 12" STEEL PIPE WERE REPLACED WITH PLASTIC. WE ARE REPORTING THIS INCIDENT SOLELY BASED ON THE VOLUME OF GAS RELEASED. NO INJURIES WERE INVOLVED IN THIS INCIDENT AND RESPONSE AND RESTORATION COSTS ARE RELATED TO THE REPAIR OF THE MAIN AND RESTORATION OF TWO CUSTOMERS THAT WERE SHUT OFF DURING THE RESPONSE.
2022-04-29 09:46 | NO | YES | NO | 20220019 | 36417 | 2022-03-03 13:41 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-02-16 10:20 | EASTERN | NO | 2022 | 944 MCELHANEY ROAD | TRAVELERS REST | GREENVILLE | SC | 29690 | 34.9544 | -82.4665 | [6 empty] | YES |  |  | 2022-02-16 15:27 | 1329042 | 1329121 | NATURAL GAS |  | 8710 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-16 10:20 | NO |  |  | 2022-02-16 11:39 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | M10048 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 296000 | 290153.33110144 | 0 | 0 | 0 | 0 |  | 4 | 34840 | 34840 | 0 | 0 | 330840 | 170705.729297315 | 324993.33110144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 250 | 192.619(A)(2) | 1962-06-25 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | UTILITY | BORING | WATER | YES | 2112131188 |  | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | WATER COMPANY TAPPED A 8" HIGH PRESSURE STEEL MAIN INSTEAD OF THE WATER LINE CAUSING DAMAGE TO THE 8" MAIN. THE USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES.
2022-04-29 09:46 | NO | YES | NO | 20220020 | 36425 | 2022-03-04 14:28 | ORIGINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 40 SYLVAN RD. | WALTHAM | MA | 02451 | 2022-02-04 07:30 | EASTERN | NO | 2022 | 65 BAY 35TH STREET | BROOKLYN | KINGS | NY | 11232 | 40.6735 | -74.009 |  |  | YES | [6 empty] | 2022-02-04 08:55 | 1328059 | 1328218 | NATURAL GAS |  | 5.092 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-04 07:31 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2022-02-04 07:31 |  |  |  | 2022-02-04 07:54 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN - OEM ARRIVED ONSITE AFTER THE EVENT; NATIONAL GRID ARRIVED APPROX. 20 MINUTES LATER. CAUSE IS UNDER INVESTIGATION | CLASS 4 LOCATION | 750000 | 735185.805155674 | 7107 | 6966.62068965517 | 8300 | 8136.0562437228 | 0 | 0 |  | 7.47 | 38 | 38 | 0 | 0 | 765445 | 337712.014782962 | 750326.482089052 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 9 | 9.1 | 12 | 192.623 | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | NATIONAL GRID DISPATCH WAS NOTIFIED ON 02/04/22 AT 7:23 AM FROM THE OFFICE OF EMERGENCY MANAGEMENT THAT AN EXPLOSION HAD OCCURRED AT 67 BAY 35TH STREET, BROOKLYN NY. THE EXPLOSION FULLY DESTROYED 65 BAY 35TH STREET AND PARTIALLY DAMAGED 69 BAY 35TH STREET, CAUSING IT TO PARTIALLY COLLAPSE. SERVICES AT 65, 69 AND 71 BAY 35TH STREET WERE CUT OFF AT THE MAIN. WITH RESPECT TO PART E, QUESTION 3A, THE MAOP WAS ESTABLISHED IN ACCORDANCE WITH 49 CFR 192.623, EFFECTIVE IN 1970; HOWEVER THE PIPELINE WAS PREDOMINANTLY INSTALLED IN 1965. THREE HOMES WERE DAMAGED AND/OR DEMOLISHED AS A RESULT OF THIS INCIDENT. AT THIS TIME, WE CANNOT ESTIMATE THE COST OF THIS DAMAGE, BUT LIKELY TO EXCEED THE $750,000 PROVIDED IN PART D. THIS INCIDENT IS STILL UNDER INVESTIGATION AND NATIONAL GRID HAS NOT BEEN GRANTED ACCESS AT THIS POINT.
2022-04-29 09:46 | NO | YES | NO | 20220022 | 36437 | 2022-03-08 09:39 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-02-08 07:45 | CENTRAL | NO | 2022 | 11699 NW H K DODGEN LOOP | TEMPLE | BELL | TX | 76504 | 31.1412 | -97.3446 | YES | [5 empty] | YES |  |  | 2022-02-08 18:41 | 1328466 | 1328674 | NATURAL GAS |  | 5036 | 18 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 07:45 | YES | OPERATOR | 2022-02-08 08:05 | 2022-02-08 08:05 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 65 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1985 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 11 | 1 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 104000 | 101945.764981587 | 0 | 0 | 0 | 0 |  | 8.17 | 41144 | 41144 | 147 | 147 | 145291 | 93431.6769314259 | 143236.764981587 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 168 | 168 | 200 | 192.619(A)(2) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2252816180 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 20 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY WAS NOT LOCATED OR MARKED | [170 empty] | DALE GAMBRELL | COMPLIANCE SUPERVISOR | dale.gambrell@atmosenergy.com | 512-844-8270 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-957-3295 | marlo.sutton@atmosenergy.com | AT 07:45 ON FEBRUARY 8, 2022, A THIRD PARTY CONTRACTOR DAMAGED A 6" ATMOS DISTRIBUTION LINE WITH A TRACKHOE AT 11699 NW H K DODGEN LOOP IN TEMPLE TX, CAUSING A RELEASE OF GAS. THE DAMAGE CAUSED AN INTERRUPTION IN SERVICE FOR 1 CUSTOMER; CNG WAS BROUGHT IN TO SHORE UP SERVICE FOR OTHER CUSTOMERS. GAS LOSS EXCEEDED THE REPORTING THRESHOLD. SERVICE WAS RESTORED AT 03:32 ON FEBRUARY 9, 2022. IT WAS DETERMINED THAT THE PIPELINE WAS NOT MARKED BY THE LOCATOR.
2022-04-29 09:46 | NO | YES | NO | 20220024 | 36500 | 2022-03-25 16:52 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-02-25 09:33 | EASTERN | YES | 2022 | PORTAGE | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2816 | -85.5722 | [5 empty] | YES |  | YES | SQUEEZE-OFF ISOLATION NORTH END PIPELINE SEGMENT & BAGGING OFF ISOLATION SOUTH END PIPELINE SEGMENT | 2022-02-25 09:33 | 1329679 | 1329801 | NATURAL GAS |  | 2277 | 0.007 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 14:27 | NO |  |  | 2022-02-08 14:44 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1901 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 332405 | 325839.250083696 | 318 | 311.718781386006 | 0 | 0 |  | 4.48 | 10201 | 10201 | 0 | 0 | 342924 | 158532.15183165 | 336351.968865082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 192.623 | 1901-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | EROSION OF SUPPORT DUE TO OTHER UTILITIES | OTHER OUTSIDE FORCE DAMAGE | EROSION OF SUPPORT DUE TO OTHER UTILITIES | [111 empty] | EROSION OF SUPPORT DUE TO OTHER UTILITIES | [168 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON TUESDAY, FEBRUARY 8, 2022 AT APPROXIMATELY 14:27 HOURS CONSUMERS ENERGY WAS NOTIFIED BY OUR LEAK SURVEY CONTRACTOR (PERFORMING A DISCRETIONARY LEAK SURVEY) OF A POSSIBLE LEAK AT/NEAR 1004 PORTAGE ROAD, (KALAMAZOO COUNTY) KALAMAZOO, MI. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 14:44 HOURS AND CONFIRMED READS WHICH REQUIRED AN IMMEDIATE RESPONSE. A DISTRIBUTION CREW (CREW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 16:39 HOURS. THE CREW HAD RECENTLY COMPLETED A LEAK REPAIR ON A 6" CAST IRON PIPELINE AND BASED ON A PRELIMINARY INVESTIGATION AT THE SITE THOUGHT THE SOURCE COULD POTENTIALLY BE RESIDUAL GAS FROM THE INITIAL REPAIR. EXTRACTION EQUIPMENT WAS MOBILIZED TO REMOVE RESIDUAL GAS BUILD UP WHILE GSW'S AND THE CREW CONTINUED PINPOINTING TO DETERMINE IF THE SOURCE COULD BE ADDITIONAL LEAKS ON THE PIPELINE. OVER SEVERAL WEEKS, MULTIPLE LEAKS WERE DISCOVERED ON THE CAST IRON PIPELINE. A SEWER AND ROAD RECONSTRUCTION PROJECT COMPLETED IN NOVEMBER 2021 MAY HAVE COMPROMISED THE CAST IRON PIPELINE WHICH LED TO MULTIPLE LEAKS. ALL IDENTIFIED LEAKS WERE REPAIRED AND EXTRACTION EQUIPMENT WAS SIMULTANEOUSLY USED TO REMOVE RESIDUAL GAS FROM THE SOIL. CONSUMERS ENERGY PERSONNEL MONITORED THE SITE UNTIL ALL GAS READS WERE ZERO. A PIPELINE REPLACEMENT PROJECT, WHICH WOULD HAVE INCLUDED RETIRING THE 6" CAST IRON PIPELINE WAS SCHEDULED FOR 2023. HOWEVER DUE TO THE AGE AND CONDITION OF THE PIPELINE A PORTION OF THE REPLACEMENT PROJECT WAS EXPEDITED AND TENTATIVELY SCHEDULED TO BEGIN APRIL 2022. APPROXIMATELY 1100' OF 6" CAST IRON PIPELINE WAS RETIRED ON FEBRUARY 25, 2022.
2022-04-29 09:46 | NO | YES | NO | 20220025 | 36533 | 2022-03-31 18:46 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2022-03-01 10:37 | CENTRAL | NO | 2022 | 3 MILLERS CT | O'FALLON | SAINT CHARLES | MO | 63366 | 38.7758 | -90.7291 | [5 empty] | YES |  |  |  | 2022-03-01 12:33 | 1329957 | 1330159 | NATURAL GAS |  | 104.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-01 11:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 45 | YES | 3 | 2022-03-01 10:37 | NO |  |  | 2022-03-01 10:59 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 663261 | 650160.09641781 | 0 | 0 | 500 | 490.123870103783 | 0 | 0 |  | 6.12 | 641 | 641 | 0 | 0 | 664402 | 293564.109462921 | 651291.220287914 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 39.77 | 40 | 60 | 192.621 M | 2002-12-02 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 220521245 |  | CONTRACT LOCATOR | YES | YES | YES | 9 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY TELECOMMUNICATIONS EXCAVATOR STRUCK A 2-INCH PLASTIC GAS MAIN WHILE BORING. THE EXCAVATOR HAD VALID LOCATES AND THE MAIN WAS MARKED WITHIN TOLERANCE BUT THE EXCAVATOR FAILED TO POT-HOLE THE BORE CROSSING. THE COMPANY IDENTIFIED GAS READINGS IN TWO HOMES UPON ARRIVAL AND EVACUATED BOTH RESIDENCES. WHILE CREWS WERE WORKING TO SHUT DOWN THE MAIN 3 MILLERS CT EXPLODED AND SUBSEQUENTLY CAUGHT FIRE. CREWS IMMEDIATELY SHUT DOWN THE MAIN FOLLOWING THE EXPLOSION. THE EXPLOSION CAUSED DAMAGE TO SEVERAL NEARBY HOMES AND THE FIRE SPREAD TO 5 MILLERS CT. THE DAMAGED GAS MAIN WAS REPLACED WITH A 15-FOOT SEGMENT OF 2-INCH PLASTIC. GAS SERVICE WAS INTERRUPTED AT 21 HOMES AND 2 HOMES WERE CONDEMNED. A 48 HOUR UPDATE TO THE NRC WAS MADE ON MARCH 3, 2021 AT 13:38. REPORT NUMBER 1330159.
2022-04-29 09:46 | NO | YES | NO | 20220026 | 36557 | 2022-04-06 09:33 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-03-10 09:18 | CENTRAL | NO | 2022 | ENTIRE CITY | SEGUIN | GUADALUPE | TX | 78155 | 29.5701 | -97.9641 |  | YES |  | YES | [5 empty] | 2022-03-10 09:18 | 1330725 | 1331011 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-08 10:30 | NO |  |  | 2022-03-08 13:00 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | LOSS OF GAS SUPPLY FROM SUPPLIER | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1121224 | 1099077.29226649 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1121224 | 494641.086709073 | 1099077.29226649 | 0 | 0 | 4300 | 0 | 0 | 4300 | 0 | 0 | 0 | 0 | 192.619(A)(1) | 2022-03-08 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | NOTIFICATION FROM SUPPLIER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOSS OF GAS SUPPLY FORM SUPPLIER | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [231 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM SUPPLIER | [47 empty] | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 |  | MICHAEL MAXWELL | mike.d.maxwell@centerpointenergy.com | 830-643-6914 | RANDALL SANDERS | REGIONAL OPERATIONS DIRECTOR TEXAS | 713-207-5728 | randall.x.sanders@centerpointenergy.com | LOSS OF GAS SUPPLY FROM ENTERPRISE PIPELINE TO CENTERPOINT ENERGY DISTRIBUTION SYSTEM IN SEGUIN, & MCQUEENEY, TEXAS, FORCED CENTERPOINT ENERGY TO PERFORM RE-LITE OF APPROXIMATELY 4300 CUSTOMERS.
2022-04-29 09:46 | NO | YES | YES | 20220027 | 36558 | 2022-04-06 09:44 | ORIGINAL | 13302 | NATIONAL GAS & OIL CORP | 1500 GRANVILLE ROAD | NEWARK | OH | 43055 | 2022-02-23 15:22 | EASTERN | YES | 2022 | 811 BLACKS RD SE | HEBRON | LICKING | OH | 43025 | 39.9878 | -82.5205 |  |  | YES | YES | [5 empty] | 2022-02-23 15:22 | 1329557 |  | NATURAL GAS |  | 7 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2022-02-23 13:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7 | YES | 1 | 2022-02-23 14:10 | YES | OPERATOR | 2022-02-23 13:51 | 2022-02-23 14:17 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 1998 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 277236 | 271759.962504185 | 0 | 0 | 5000 | 4901.23870103783 | 0 | 0 |  | 39 | 273 | 273 | 0 | 0 | 282509 | 124826.101514727 | 276934.201205223 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 44 | 44 | 60 | 192.619(A)(1) | 1998-04-24 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 7 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL LEAK OF THIS KIND WAS NOT DETECTABLE ON SUCH A LARGE SYSTEM THAT IS MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | [56 empty] | TREES/VEGETATION ROOTS | [5 empty] | NO | [187 empty] | YES | [29 empty] | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | cstorts@theenergycoop.com | 740-348-1203 | 740-348-1131 |  |  |  | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | 740-348-1203 | cstorts@theenergycoop.com | ON WEDNESDAY, FEBRUARY 23, 2022, A HOMEOWNER REPORTED AN EXPLOSION AND CALLED 911. NATIONAL GAS & OIL COOPERATIVE WAS NOTIFIED APPROXIMATELY 10 MINUTES LATER. WHEN COOPERATIVE EMPLOYEES ARRIVED AT THE SCENE, THE SERVICE LINE CURB VALVE WAS SHUT AND THE FIRE DEPARTMENT EXTINGUISHED THE FLAMES. READINGS INDICATED THAT NATURAL GAS WAS PRESENT IN THE GROUND AROUND THE HOMEOWNER'S NATURAL GAS RISER. THE HOMEOWNER'S NATURAL GAS SERVICE LINE WAS TESTED AND LEAKAGE WAS FOUND AT THE RISER HEAD. ON TUESDAY, MARCH 22, 2022 AFTER ALL INSURANCE PARTIES AND FIRE AND EXPLOSION INVESTIGATORS COULD BE PRESENT, THE HOMEOWNER'S RISER WAS REMOVED AND THE SERVICE LINE CAPPED AT THE BASE OF THE RISER AND RETESTED. THE SERVICE LINE HELD THE PRESSURE TEST WITHOUT THE RISER. THE HOMEOWNER'S RISER WAS REMOVED AND SENT TO AN INDEPENDANT LABORATORY PLANNED FOR FURTHER INVESTIGATION (PLANNED FOR APRIL 21, 2022). THIS RISER WAS INSTALLED BY THE HOMEOWNER OR THE HOMEOWNER'S CONTRACTOR OR REPRESENTATIVE, NOT BY THE NATIONAL GAS & OIL COOPERATIVE.
2022-04-29 09:46 | NO | YES | NO | 20220028 | 36564 | 2022-04-08 10:32 | ORIGINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-03-10 14:50 | CENTRAL | NO | 2022 | 3307 89TH STREET | LUBBOCK | LUBBOCK | TX | 79412 | 33.513 | -101.8861 | [5 empty] | YES |  |  |  | 2022-03-10 16:55 | 1330768 | 1330843 | NATURAL GAS |  | 685 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-10 15:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | YES | 7 | 2022-03-10 15:09 | YES | OPERATOR | 2022-03-10 15:09 | 2022-03-10 15:09 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 2.375 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 7938 | 7781.20656176766 | 13455 | 13189.2333444928 | 166000 | 162721.124874456 | DAMAGE TO RESIDENCE. | 5.63 | 3857 | 3857 | 6 | 6 | 191256 | 87119.2588947149 | 187554.564780716 | 0 | 0 | 7 | 0 | 0 | 12 | 0 | 40 | 40 | 44 | 192.619(A)(2) | 2015-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 1 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [9 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2256245020 | TX811 | CONTRACT LOCATOR | YES | YES | YES | 40 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [142 empty] | YES | [26 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 8062206849 |  | MIKE CULP | mike.culp@atmosenergy.com | 8062206849 | MIKE CULP | COMPLIANCE MANAGER | 8062206849 | mike.culp@atmosenergy.com | CITY OF LUBBOCK, TX WHILE REPAIRING A SEWER SERVICE LINE TO THE ASSOCIATED ADDRESS, CUT A 2" NATURAL GAS LINE WITH A BACKHOE. THE GAS LINE WAS CORRECTLY MARKED WITH PAINT AND FLAGS BEFORE START OF EXCAVATION. ATMOS ENERGY WAS NOTIFIED OF THE DAMAGED LINE AT 15:09 AND ARRIVED ON SCENE AT 15:16. REMOTE EXCAVATIONS SITES WERE USED TO SQUEEZE THE PE LINE AND SHUT THE FLOW OF GAS OFF, AREA WAS MADE SAFE AT 16:37. ATMOS ENERGY'S INVESTIGATION OF THIS INCIDENT IS CURRENTLY ONGOING.
2022-04-29 09:46 | NO | YES | NO | 20220029 | 36565 | 2022-04-08 11:56 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2022-03-09 16:22 | PACIFIC | NO | 2022 | 3817 N CRESTLINE ST | SPOKANE | SPOKANE | WA | 99207 | 47.6928 | -117.3791 | YES | [8 empty] | 2022-03-09 16:37 | 1330648 | 1330830 | NATURAL GAS |  | 45 | 22 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2022-03-03 18:08 | NO |  |  | 2022-03-03 19:03 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1956 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2000 | 1960.49548041513 | 177000 | 173503.850016739 | 0 | 0 |  | 4.63 | 208 | 208 | 102 | 102 | 179310 | 79324.9415103935 | 175774.345497154 | 41 | 1 | 1127 | 0 | 0 | 1127 | 42 | 55 | 55 | 60 | 192.619(C) | 1956-06-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A PIPE LEAK THAT REQUIRED A SYSTEM OUTAGE TO REPAIR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2018-08-15 | NO | [12 empty] | NO | YES | CITY STREET | [9 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | PREVIOUS DAMAGE | [173 empty] | JOSHUA FORT | SR. GAS ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | TIM HARDING | tim.harding@avistacorp.com | 509-495-2784 | BRIAN SCHULTZ | MANAGER - NAT. GAS COMPLIANCE AND INTEGRITY | 509-495-2162 |  | brian.schultz@avistacorp.com | THE SPOKANE CITY WATER DEPARTMENT RESPONDED TO A LEAKING WATER SERVICE AT 3817 N CRESTLINE ST. PRIOR TO EXCAVATING, THE WATER CREW SMELLED NATURAL GAS IN THE AREA THEY WERE GOING TO DIG. THEY CONTACTED AVISTA TO REPORT THE GAS ODOR. AN AVISTA FIRST RESPONDER ARRIVED AND DETERMINED THAT AN AVISTA CONSTRUCTION CREW WOULD NEED TO INVESTIGATE THE LEAK. THE AREA WAS EXCAVATED AND THE LEAK LOCATION WAS FOUND TO BE ON THE BOTTOM OF THE STEEL GAS MAIN. THE LEAK WAS COMING FROM A CRACK OR SMALL HOLE INSIDE THE DENT. THIS DENT WAS LIKELY CAUSED BY EXCAVATION DAMAGE SOMETIME IN THE PAST. TO REPAIR THE LEAK, THE CREW NEEDED TO WELD A STEEL FITTING OVER THE DENT. PRIOR TO WELDING ON THE FITTING, THE CREW ATTEMPTED REDUCE THE GAS FLOW FROM THE LEAK BY INSERTING A PLUG. UNFORTUNATELY THIS CAUSED THE LEAK RATE TO INCREASE AND IT WAS DECIDED THAT THE SYSTEM SHOULD BE SHUT DOWN TO SAFELY WELD ON THE REPAIR FITTING. TEN VALVES IN THE SYSTEM WERE CLOSED AT MIDNIGHT ON 3/4/22. THIS CAUSED AN OUTAGE FOR 1169 CUSTOMERS. THE STEEL MAIN REPAIR WAS COMPLETE AT 01:00 3/4/22. ALL GAS METERS IN THE SYSTEM WERE SHUT OFF, THE SYSTEM WAS PURGED OF ANY AIR, AND CUSTOMER RELIGHTS STARTED AT 14:00 ON 3/4/22. RELIGHTS WERE COMPLETE AT 17:00 ON 3/5/22 WITH THE EXCEPTION OF SOME CUSTOMERS WHOSE HOMES WE WERE UNABLE TO ENTER. ON 3/9/22 IS WAS DETERMINED THAT THE INCIDENT COST HAD EXCEEDED THE FEDERAL THRESHOLD AND IT WAS REPORTED TO PHMSA (NRC).
2022-04-29 09:46 | NO | YES | NO | 20220030 | 36571 | 2022-04-12 21:21 | ORIGINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-03-13 01:55 | EASTERN | YES | 2022 | 908 COLLEGE AVENUE | HOUGHTON | HOUGHTON | MI | 49931 | 47.1221 | -88.5626 |  | YES |  |  |  | YES |  |  |  | 2022-03-13 09:05 | 1330926 | NA | NATURAL GAS |  | 2000 | 0.113 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-13 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 30 | 2022-03-13 01:55 |  |  |  | 2022-03-13 03:19 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1966 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNKNOWN AT THIS TIME. | [5 empty] | CLASS 3 LOCATION | 500000 | 490123.870103783 | 50000 | 49012.3870103783 | 50000 | 49012.3870103783 | 0 | 0 |  | 5.6071 | 11214 | 11214 | 1 | 1 | 611215 | 277612.25365798 | 599363.64412454 | 12 | 0 | 6 | 0 | 0 | 5 | 10 | 55 | 55 | 60 | 192.619(A)(2) | 1966-10-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RATE OF GAS VOLUME RELEASED WOULD NOT HAVE TRIGGERED ANY ALARMS OR AOCS THROUGH THE SCADA SYSTEM, AND THEREFORE THE CONTROLLERS WOULD NOT HAVE TAKEN ACTION. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | MIKE KOSHT | michael.kosht@semcoenergy.com | (906) 250-7196 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | TECH ARRIVED ON SITE, AND HOUGHTON FIRE DEPT. WAS ATTENDING TO STRUCTURE FIRE AT 908 COLLEGE AVE. ONCE FIRE WAS UNDER CONTROL, TECH WAS ABLE TO SECURE GAS TO 908 COLLEGE AVE. THROUGH THE LEAK INVESTIGATION PROCESS, TECH EVACUATED MULTIPLE BUILDINGS ON COLLEGE AVE. AND ON E LAKESHORE. TECH DETERMINED THERE WAS A PROBABLE UNDERGROUND LEAK, BASED ON LEL READINGS FOUND SURROUNDING THE SITE. GAS FLOW WAS CONTROLLED, AND THE SURROUNDING AREA WAS PURGED TO REDUCE GAS TO SAFE LEVELS. THE SOURCE OF GAS LEAK IS NOT YET DETERMINED DUE TO GROUND CONDITIONS (I.E, FROZEN GROUND, ETC). THE INCIDENT IS STILL UNDER INVESTIGATION AND SEMCO IS WORKING CLOSELY WITH MICHIGAN PUBLIC SERVICE COMMISSION THROUGHOUT THE PROCESS. A SUPPLEMENTAL REPORT WILL BE FILED WHEN FURTHER INVESTIGATIONS ARE ABLE TO BE CONDUCTED.
2022-04-29 09:46 | NO | YES | NO | 20220031 | 36574 | 2022-04-13 10:55 | ORIGINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2022-03-14 18:31 | EASTERN | YES | 2022 | 449 FIRST ST. | NEWBURGH | ORANGE | NY | 12550 | 41.5027 | -74.0278 |  |  | YES | [6 empty] | 2022-03-14 18:31 | 1331058 | 1331191 | NATURAL GAS |  | 3.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-14 16:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.4 | YES | 6 | 2022-03-14 16:32 |  |  |  | 2022-03-14 16:32 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1951 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL PIPE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE SERVICE PIPE TO THE BUILDING FOUNDATION IS 2" AND THE PIPE REDUCES TO 1 1/4" NEAR THE FOUNDATION WALL. | CLASS 3 LOCATION | 137000 | 134293.940408437 | 18500 | 18134.58319384 | 19000 | 18624.7070639438 | 0 | 0 |  | 9.713 | 33 | 33 | 0 | 0 | 174533 | 77020.7196881336 | 171086.23066622 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.34 | 0.34 | 0.5 | 192.623 | 1951-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [111 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL SERVICE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE CONTRACTOR INTENDED TO CUT THE PIPE. | [155 empty] | JERRY AMATO JR. | DIRECTOR OF GAS COMPLIANCE | jamato@cenhud.com | 845.486.5642 |  | JERRY AMATO | jamato@cenhud.com | 845-486-5642 | MARK MULPETER | MANAGER OF GAS OPERATIONS AND ENGINEERING | 845-486-5755 | mmulpeter@cenhud.com | AT 4:25 PM ON 3/14/2022, CENTRAL HUDSON WAS NOTIFIED BY THE CITY OF NEWBURGH OF A POSSIBLE GAS EXPLOSION AT 449 FIRST ST. IN NEWBURGH. THE FIRST CENTRAL HUDSON RESPONDER ARRIVED ON SITE AT 4:32 PM AND A SECOND CENTRAL HUDSON RESPONDER ARRIVED AT 4:33 PM. THE BUILDING WAS ON FIRE WHEN THE RESPONDERS ARRIVED. ADDITIONAL SUPPORTING PERSONNEL INCLUDING SUPERVISORS AND GAS CONSTRUCTION CREW WERE EN ROUTE. APPROXIMATELY 6 PEOPLE WERE EVACUATED BY THE FIRE DEPARTMENT. THE BUILDING AT 449 FIRST ST. WAS PRESENTLY BEING RENOVATED AND WAS FED BY A 4 INCH LOW PRESSURE CAST IRON MAIN AND 197 FT. LONG 2 INCH STEEL SERVICE. A CURB VALVE WAS PRESENT ON THE SERVICE. THERE WERE THREE GAS METERS LOCATED INSIDE THE BUILDING'S BASEMENT WITH VALVES THAT WERE CLOSED AND LOCKED ON OCTOBER 25TH 2021. A CENTRAL HUDSON REPRESENTATIVE ON SCENE ADVISED THE FIRE DEPARTMENT TO CONTAIN THE HOUSE FIRE BUT TO ALLOW THE NATURAL GAS TO BURN TO PREVENT A SECOND IGNITION. A POLICE OFFICER INFORMED AN ONSITE CENTRAL HUDSON SUPERVISOR OF A REPORT OF THE CUSTOMER'S CONTRACTOR CUTTING THE SERVICE LINE OR CUSTOMER PIPE INSIDE THE BUILDING. A COMMERCIAL REPRESENTATIVE STOPPED THE FLOW OF GAS TO THE HOUSE BY CLOSING THE CURB VALVE ON THE SERVICE AT APPROXIMATELY 5:00 PM. ELECTRIC TAPS FOR THIS ADDRESS WERE CUT AT APPROXIMATELY 5:05PM. BY THIS TIME, ADDITIONAL CH EMPLOYEES HAD ARRIVED ON THE SCENE TO ASSIST IN THE EMERGENCY RESPONSE. THE CENTRAL HUDSON SUPERVISOR INFORMED THE FIRE DEPARTMENT THAT THEY MAY PROCEED WITH EXTINGUISHING THE HOUSE FIRE. AFTER THE BUILDING WAS MADE ACCESSIBLE BY THE FIRE DEPARTMENT, ONE CENTRAL HUDSON PERSONNEL AND CITY OF NEWBURGH FIRE INVESTIGATOR INVESTIGATED THE BASEMENT OF THE HOUSE AND CONFIRMED THAT THE SERVICE PIPE AND CUSTOMER PIPE HAD BEEN CUT AND DISASSEMBLED IN MULTIPLE LOCATIONS INCLUDING AT LEAST ONE LOCATION OF UPSTREAM OF THE THREE LOCKED GAS METERS. CENTRAL HUDSON AND CONTRACTOR CREWS LEAK SURVEYED THE ENTIRE PROPERTY AND THE SURROUNDING AREA. NO NATURAL GAS LEAKS WERE FOUND AT 449 FIRST ST. THE AREA OF 244 VAN NESS ST. WAS ALSO LEAK SURVEYED, AS THE SERVICE TO 449 FIRST ST. WAS FED FROM THAT ROAD. NO LEAKS WERE FOUND AT EITHER ADDRESS. GAS ODORANT READINGS WERE TAKEN IN THE SURROUNDING AREA TO VERIFY APPROPRIATE ODORIZATION OF GAS. THE NATURAL GAS SERVICE TO 449 FIRST ST. WAS PERMANENTLY RETIRED THAT EVENING AND THE AREA WAS DECLARED SAFE AT 9:40 PM.
2022-04-29 09:46 | NO | YES | NO | 20220032 | 36593 | 2022-04-21 15:15 | ORIGINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-03-24 01:15 | EASTERN | NO | 2022 | HIGHWAY 9 | BOILING SPRINGS | SPARTANBURG | SC | 29316 | 35.059 | -81.9935 | [5 empty] | YES |  |  |  |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 0.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-24 01:52 | NO |  |  | 2022-03-24 01:52 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | IN A CREEK. | 72 | NO | YES | [6 empty] | YES | BORED/DRILLED | FAWN BRANCH TRIBUTARY 2 | 1 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | INVESTOR OWNED |  | MAIN |  | 2014 | UNKNOWN |  |  |  |  | 6 | MDPE | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | ASSUMED FAILED FUSION. | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 116500 | 114198.861734181 | 5500 | 5391.36257114161 | 0 | 0 |  | 0.1 | 0 | 0 | 0 | 0 | 122000 | 53821.7274857717 | 119590.224305323 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 32 | 68 | 70 | 192.619(A)(2) | 2014-07-10 | PRESSURE DID NOT EXCEED MAOP | OTHER | INJECTION |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | [145 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2014 | N/A | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | A PASSERBY IN A VEHICLE CALLED STATING THAT THEY SMELLED GAS. ONCE INVESTIGATED, GAS WAS FOUND BLOWING THROUGH THE WATER IN THE CREEK. A FAILED FUSION IS THE ASSUMED CAUSE OF THE LEAK. DUE TO THE NATURE OF THE PIPE BEING LOCATED IN THE CREEK, THE PIPE WAS NOT EXPOSED. THE TRUE CAUSE OF THE LEAK, HOLE SIZE, AND GAS VOLUMES COULD NOT BE DETERMINED. THE NRC WAS NOT NOTIFIED AT THE TIME OF INCIDENT BECAUSE THE ESTIMATED COST WAS BELIEVED TO BE BELOW THE 122K THRESHOLD. ACTUAL COST ARE NOT YET KNOWN. WILL FILE A SUPPLEMENTAL REPORT OR RETRACT ONCE FINAL COST ARE DETERMINED.
2022-04-29 09:46 | NO | YES | NO | 20220033 | 36609 | 2022-04-25 13:28 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-04-05 05:25 | CENTRAL | YES | 2022 | 4809 TROUP HWY | TYLER | SMITH | TX | 75703 | 32.2986 | -95.2662 |  |  |  | YES | [5 empty] | 2022-04-05 05:25 | 1332738 | 1332887 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-05 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2022-04-05 01:55 |  |  |  | 2022-04-05 02:25 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | REGULATOR BODY | [9 empty] | OTHER | [8 empty] | DURING A LOCAL STORM A PONTOON BOAT BELONGING TO TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. | CLASS 3 LOCATION | 125000 | 122530.967525946 | 300 | 294.07432206227 | 676 | 662.647472380315 | 0 | 0 |  | 4.72 | 5 | 5 | 0 | 0 | 125981 | 55581.5444252598 | 123492.689320388 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.619(A)(1) | 1970-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  |  | YES | THUNDER STORMS/HIGH WINDS | [177 empty] | YES |  |  | YES | [31 empty] | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 |  | JASON SURRATT | jason.surratt@centerpointenergy.com | 903-918-2290 | RANDALL SANDERS | DIRECTOR REGIONAL GAS OPERATIONS | 713-207-5728 | randall.x.sanders@centerpointenrgy.com | DURING A LOCAL THUNDER STORM A PONTOON BOAT ON TRAILER OWNED BY TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. RESULTING IN IGNITION OF GAS DAMAGING BUILDING AND CONTENTS.
2022-04-29 09:46 | NO | YES | YES | 20220034 | 36614 | 2022-04-26 17:01 | ORIGINAL | 32500 | AGRITEXGAS L P | 3100 MONTICELLO AVE SUITE 575 | DALLAS | TX | 75205 | 2022-04-06 10:00 | CENTRAL | YES | 2022 | FM 1057 & CR II | HEREFORD | DEAF SMITH | TX | 79045 | 34.9935 | -102.4735 | YES |  |  | YES | [5 empty] | 2022-04-06 10:00 | 2603 |  | NATURAL GAS |  | 20 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-04-06 10:00 | YES | OPERATOR | 2022-04-06 10:00 | 2022-04-06 10:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | OTHER | LIMITED PARTNERSHIP | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 2.5 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 2.5 | 2.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 1000 | 980.247740207566 | 250 | 245.061935051892 | 0 | 0 |  | 10.697 | 214 | 214 | 0 | 0 | 1464 | 797.895274566855 | 1439.30967525946 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 10 | 10 | 40 | 192.619(A)(4) | 2009-06-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | UTILITY | AUGER | ELECTRIC | YES | 2258448075 | TEXAS 811 | FACILITY OWNER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 6 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY COULD NOT BE FOUND/LOCATED | [170 empty] | ELIZA RAMOS | OFFICE MANAGER | erodriguez@agritexgas.com | 806-288-0493 | 806-288-1526 |  |  |  | MIKE SCHUMACHER | GENERAL MANAGER | 806-288-0493 | m.schumacher@agritexgas.com | DEAF SMITH ELECTRIC COOP WAS DIGGING IN THE AREA OF THE UNLOCATABLE GAS LINE AND HIT THE GAS LINE WITH THEIR AUGER. KEVIN FOSTER SERVICE TECHNICIAN FOR AGRITEXGAS, LP WAS ON SITE AND PROCEEDED TO REPAIR THE GAS LINE. WHILE HE WAS WORKING ON THE LINE REPAIR HE WAS OVERCOME BY THE GAS FUMES AND PASSED OUT. EMERGENCY PERSONNEL WAS CALLED TO THE AREA AND KEVIN WAS TRANSPORTED TO HEREFORD REGIONAL MEDICAL CENTER.