## gtgg2002to2009Fields
Gas Transmission and Gathering Systems Incident Reports for 2002 - 2009 (PHMSA Form 7100.2 Rev. 01-2002) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | DATE | Data as of date | Not on the form
SIGNIFICANT | VARCHAR2 | Identify if record meets the significant criteria or not: If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
SYSTEM_TYPE | VARCHAR2 | System Type = 'GT (Gas Transmission)’ when TYSYS_TEXT = TRANSMISSION or TRANSMISSION LINE OF DISTRIBUTION SYSTEM. System Type = 'GG (Gas Gathering)' when TYSYS_TEXT = GATHERING | Not on the form
RPTID | NUMBER | PHMSA DOT assigned unique identifier for report | Top of first page
DOR | DATE | Date when report was received at DOT | Top of first page
REPORT_TYPE | VARCHAR2 | Report Type (Original, Supplemental, Final) | Not on the form
OPERATOR_ID | NUMBER | Operator's OPS-issued Operator Identification number | PART A - GENERAL REPORT INFORMATION
OWNER_OPERATOR_ID | NUMBER | If Operator does not own the pipeline, enter Owner's 5-digit Identification Number | PART A - GENERAL REPORT INFORMATION
NAME | VARCHAR2 | Operator Name | PART A - GENERAL REPORT INFORMATION
OPSTREET | VARCHAR2 | Operator Address - Street | PART A - GENERAL REPORT INFORMATION
OPCITY | VARCHAR2 | Operator Address - City | PART A - GENERAL REPORT INFORMATION
OPCOUNTY | VARCHAR2 | Operator Address - County | PART A - GENERAL REPORT INFORMATION
OPSTATE | VARCHAR2 | Operator Address - State | PART A - GENERAL REPORT INFORMATION
OPZIP | VARCHAR2 | Operator Address - Zip | PART A - GENERAL REPORT INFORMATION
IHOUR | VARCHAR2 | Time of the incident | PART A - GENERAL REPORT INFORMATION
IDATE | DATE | Date of the Incident | PART A - GENERAL REPORT INFORMATION
IYEAR | NUMBER | Year incident occurred, derived from incident date | Not on the form
ACCITY | VARCHAR2 | Location of Incident - city | PART A - GENERAL REPORT INFORMATION
ACCOUNTY | VARCHAR2 | Location of Incident - county | PART A - GENERAL REPORT INFORMATION
ACSTATE | VARCHAR2 | Location of Incident - state | PART A - GENERAL REPORT INFORMATION
ACZIP | VARCHAR2 | Location of Incident - zip | PART A - GENERAL REPORT INFORMATION
MPVST | VARCHAR2 | Location of Incident - Mile post/valve station | PART A - GENERAL REPORT INFORMATION
SURVNO | VARCHAR2 | Location of Incident - Survey station number | PART A - GENERAL REPORT INFORMATION
LATITUDE | VARCHAR2 | Location of Incident - Latitude | PART A - GENERAL REPORT INFORMATION
LONGITUDE | VARCHAR2 | Location of Incident - Longitude | PART A - GENERAL REPORT INFORMATION
OFFSHORE_TEXT | VARCHAR2 | Onshore or Offshore | PART A - GENERAL REPORT INFORMATION
CLASS | NUMBER | Location Class as defined in 49 CFR 192.5 | PART A - GENERAL REPORT INFORMATION
OFFAREA | VARCHAR2 | Offshore area | PART A - GENERAL REPORT INFORMATION
BNUMB | VARCHAR2 | Offshore block number | PART A - GENERAL REPORT INFORMATION
OFFST | VARCHAR2 | Offshore state | PART A - GENERAL REPORT INFORMATION
OCS | VARCHAR2 | Did incident occur on outer continental shelf | PART A - GENERAL REPORT INFORMATION
IFED | VARCHAR2 | Did incident occur on Federal land? | PART A - GENERAL REPORT INFORMATION
INTER_TEXT | VARCHAR2 | Interstate or Intrastate | PART A - GENERAL REPORT INFORMATION
LRTYPE_TEXT | VARCHAR2 | Leak or Rupture | PART A - GENERAL REPORT INFORMATION
LRTYPEO | VARCHAR2 | Text describing Other for LRTYPE_TEXT field | PART A - GENERAL REPORT INFORMATION
LEAK_TEXT | VARCHAR2 | Type of Leak | PART A - GENERAL REPORT INFORMATION
PUNC_DIAM | NUMBER | Puncture diameter in inches | PART A - GENERAL REPORT INFORMATION
RUPTURE_TEXT | VARCHAR2 | Type of circumferential- separation | PART A - GENERAL REPORT INFORMATION
RUPLN | NUMBER | Length of rupture in inches | PART A - GENERAL REPORT INFORMATION
PROPLN | NUMBER | Length of propagation, total, both sides in feet | PART A - GENERAL REPORT INFORMATION
FATAL | NUMBER | Total number of fatalities | PART A - GENERAL REPORT INFORMATION
EFAT | NUMBER | Number of employee fatalities | PART A - GENERAL REPORT INFORMATION
GPFAT | NUMBER | Number of general public fatalities | PART A - GENERAL REPORT INFORMATION
NFAT | NUMBER | Number of non-employee contractor fatalities | PART A - GENERAL REPORT INFORMATION
INJURE | NUMBER | Total number of injured requiring inpatient hospitalization | PART A - GENERAL REPORT INFORMATION
EINJ | NUMBER | Number of employee injured | PART A - GENERAL REPORT INFORMATION
GPINJ | NUMBER | Number of general public injured | PART A - GENERAL REPORT INFORMATION
NINJ | NUMBER | Number of non-employee contractor injured | PART A - GENERAL REPORT INFORMATION
TOTAL_COST | NUMBER | Total dollar amount of property damages | PART A - GENERAL REPORT INFORMATION
TOTAL_COST_IN84 | Number | Converted Property Damage to 1984 dollars | Not on the form
TOTAL_COST_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
GASPRP | NUMBER | Total dollar amount of gas loss | PART A - GENERAL REPORT INFORMATION
GASPRPCURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
OPPRP | NUMBER | Total dollar amount of operator damage | PART A - GENERAL REPORT INFORMATION
OPPRPCURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
PPPRP | NUMBER | Total dollar amount of public/private property damages | PART A - GENERAL REPORT INFORMATION
PPPRPCURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
HIGHCON | VARCHAR2 | Release occur in a 'High Consequence Area' (Yes/No) | PART A - GENERAL REPORT INFORMATION
IGNITE | VARCHAR2 | Gas ignite (Yes/No) | PART A - GENERAL REPORT INFORMATION
EXPLO | VARCHAR2 | Explosion (Yes/No) | PART A - GENERAL REPORT INFORMATION
EVAC | VARCHAR2 | Evacuation (Yes/No) | PART A - GENERAL REPORT INFORMATION
EVACNO | NUMBER | Number of people evacuated | PART A - GENERAL REPORT INFORMATION
EVAC_REASON_TEXT | VARCHAR2 | Reason for evacuation | PART A - GENERAL REPORT INFORMATION
STHH | NUMBER | Elapsed Time Until Area Was Made Safe / Hours | PART A - GENERAL REPORT INFORMATION
STMN | NUMBER | Elapsed Time Until Area Was Made Safe / Minutes | PART A - GENERAL REPORT INFORMATION
TELRN | VARCHAR2 | NRC telephonic report number | PART A - GENERAL REPORT INFORMATION
TELDT | DATE | Date incident reported to NRC | PART A - GENERAL REPORT INFORMATION
INC_PRS | NUMBER | Pressure at point and time of incident | PART A - GENERAL REPORT INFORMATION
MAOP | NUMBER | Maximum allowable operating pressure | PART A - GENERAL REPORT INFORMATION
MAOPSEC1 | VARCHAR2 | MAOP est by 49 CFR section 192.619(a)(1) (Yes/No) | PART A - GENERAL REPORT INFORMATION
MAOPSEC2 | VARCHAR2 | MAOP est by 49 CFR section 192.619(a)(2) (Yes/No) | PART A - GENERAL REPORT INFORMATION
MAOPSEC3 | VARCHAR2 | MAOP est by 49 CFR section 192.619(a)(3) (Yes/No) | PART A - GENERAL REPORT INFORMATION
MAOPSEC4 | VARCHAR2 | MAOP est by 49 CFR section 192.619(a)(4) (Yes/No) | PART A - GENERAL REPORT INFORMATION
MAOPSECC | VARCHAR2 | MAOP est by 49 CFR section 192.619(c) (Yes/No) | PART A - GENERAL REPORT INFORMATION
OVERPRS | VARCHAR2 | Did an overpressurization occur relating to the incident (Yes/No) | PART A - GENERAL REPORT INFORMATION
PNAME | VARCHAR2 | Incident Report Prepared by | PART B - PREPARER AND AUTHORIZED SIGNATURE
PHONE | VARCHAR2 | Preparer's telephone number | PART B - PREPARER AND AUTHORIZED SIGNATURE
PEMAIL | VARCHAR2 | Preparer's telephone email | PART B - PREPARER AND AUTHORIZED SIGNATURE
TYSYS_TEXT | VARCHAR2 | Incident occurred on | PART C - ORIGIN OF THE INCIDENT
PRTFL_TEXT | VARCHAR2 | Failure occurred on | PART C - ORIGIN OF THE INCIDENT
PRTFO | VARCHAR2 | Text describing Other for PRTFL_TEXT field | PART C - ORIGIN OF THE INCIDENT
MLKD_TEXT | VARCHAR2 | Material involved | PART C - ORIGIN OF THE INCIDENT
MLKDO | VARCHAR2 | Text describing Other for MLKD_TEXT field | PART C - ORIGIN OF THE INCIDENT
PLAS_DUCT | VARCHAR2 | Plastic failure was ductile (Y/N) | PART C - ORIGIN OF THE INCIDENT
PLAS_BRIT | VARCHAR2 | Plastic failure was brittle (Y/N) | PART C - ORIGIN OF THE INCIDENT
PLAS_JNT | VARCHAR2 | Plastic failure was joint failure (Y/N) | PART C - ORIGIN OF THE INCIDENT
PRTSY_TEXT | VARCHAR2 | Part of system involved in incident | PART C - ORIGIN OF THE INCIDENT
PRTSYO | VARCHAR2 | Text describing Other for PRTSY_TEXT field | PART C - ORIGIN OF THE INCIDENT
PRTYR | NUMBER | Year the pipe or component which failed was installed | PART C - ORIGIN OF THE INCIDENT
NPS | NUMBER | Nominal pipe size in inches | PART D - MATERIAL SPECIFICATION
WALLTHK | NUMBER | Wall thickness in inches | PART D - MATERIAL SPECIFICATION
SPEC | VARCHAR2 | Specification | PART D - MATERIAL SPECIFICATION
SMYS | NUMBER | Specified Minimum Yield Strength (SMYS) | PART D - MATERIAL SPECIFICATION
SEAM | VARCHAR2 | Seam type | PART D - MATERIAL SPECIFICATION
VALVE | VARCHAR2 | Valve type | PART D - MATERIAL SPECIFICATION
MANU | VARCHAR2 | Pipe or valve manufactured by | PART D - MATERIAL SPECIFICATION
MANYR | NUMBER | Year manufactured | PART D - MATERIAL SPECIFICATION
LOCLK_TEXT | VARCHAR2 | Area of incident | PART E - ENVIRONMENT
LOCLKO | VARCHAR2 | Text describing Other for LOCLK_TEXT field | PART E - ENVIRONMENT
DEPTH_COV | NUMBER | Depth of cover in inches | PART E - ENVIRONMENT
CAUSE | VARCHAR2 | Apparent cause of incident | PART F - APPARENT CAUSE
CAUSE_DETAILS | VARCHAR2 | Detailed cause of accident | PART F – APPARENT CAUSE
MAP_CAUSE | VARCHAR2 | Cause by PHMSA for 20 year incident trending | Not on the form
MAP_SUBCAUSE | VARCHAR2 | SubCause by PHMSA for 20 year incident trending | Not on the form
PIPE_COAT_TEXT | VARCHAR2 | Pipe coating | PART F1 - CORROSION
VIS_EXAM_TEXT | VARCHAR2 | Visual examination | PART F1 - CORROSION
VIS_EXAMO | VARCHAR2 | Text describing Other for VIS_EXAM_TEXT field | PART F1 - CORROSION
COR_CAUSE_TEXT | VARCHAR2 | Cause of corrosion | PART F1 - CORROSION
COR_CAUSEO | VARCHAR2 | Text describing Other for COR_CAUSE_TEXT field | PART F1 - CORROSION
PROT | VARCHAR2 | Was corroded part under cathodic protection | PART F1 - CORROSION
CPYR | NUMBER | Year cathodic protection started | PART F1 - CORROSION
PREV_DAM | VARCHAR2 | Was pipe previously damaged in the area of corrosion | PART F1 - CORROSION
PREV_DAM_YR | NUMBER | How long previously damaged to incident (years) | PART F1 - CORROSION
PREV_DAM_MO | NUMBER | How long previously damaged to incident (months) | PART F1 - CORROSION
EARTH_MOVE_TEXT | VARCHAR2 | Type of Earth Movement | PART F2 - NATURAL FORCES
EARTH_MOVEO | VARCHAR2 | Text describing Other for EARTH_MOVE_TEXT field | PART F2 - NATURAL FORCES
FLOODS_TEXT | VARCHAR2 | Type of Heavy rains/floods | PART F2 - NATURAL FORCES
FLOODSO | VARCHAR2 | Text describing Other for FLOODS_TEXT field | PART F2 - NATURAL FORCES
TEMPER_TEXT | VARCHAR2 | Type of Temperature | PART F2 - NATURAL FORCES
TEMPERO | VARCHAR2 | Text describing Other for TEMPER_TEXT field | PART F2 - NATURAL FORCES
THIRD_PARTY_GRP_TEXT | VARCHAR2 | Type of Third Party Excavation Group | PART F3 - EXCAVATION
THIRD_PARTY_TYPE_TEXT | VARCHAR2 | Type of Excavation | PART F3 - EXCAVATION
THIRD_PARTY_TYPEO | VARCHAR2 | Text describing Other for THIRD_PARTY_TYPE_TEXT field | PART F3 - EXCAVATION
NOTIF | VARCHAR2 | Did operator get prior notification of excavation activity | PART F3 - EXCAVATION
NOTIF_MO | NUMBER | Month when notified | PART F3 - EXCAVATION
NOTIF_DAY | NUMBER | Day when notified | PART F3 - EXCAVATION
NOTIF_YR | NUMBER | Year when notified | PART F3 - EXCAVATION
NOTIF_RCVD_TEXT | VARCHAR2 | Notification received | PART F3 - EXCAVATION
MARKED | VARCHAR2 | Was pipeline marked | PART F3 - EXCAVATION
TEMP_MARK_TEXT | VARCHAR2 | Temporary markings | PART F3 - EXCAVATION
PERM_MARK | VARCHAR2 | Permanent markings | PART F3 - EXCAVATION
ACC_MARK_TEXT | VARCHAR2 | Marks were accurate or inaccurate | PART F3 - EXCAVATION
MKD_IN_TIME | VARCHAR2 | Were marks made within required time | PART F3 - EXCAVATION
FIRE_EXPLO_TEXT | VARCHAR2 | Fire/explosion as primary cause of incident | PART F4 - OTHER OUTSIDE FORCE DAMAGE
PIPE_BODY_TEXT | VARCHAR2 | Material - Body of Pipe | PART F5 - MATERIAL AND WELDS
PIPE_BODYO | VARCHAR2 | Text describing Other for PIPE_BODY_TEXT field | PART F5 - MATERIAL AND WELDS
COMPONENT_TEXT | VARCHAR2 | Material - Component | PART F5 - MATERIAL AND WELDS
COMPONENTO | VARCHAR2 | Text describing Other for COMPONENT_TEXT field | PART F5 - MATERIAL AND WELDS
JOINT_TEXT | VARCHAR2 | Material - Joint | PART F5 - MATERIAL AND WELDS
JOINTO | VARCHAR2 | Text describing Other for JOINT_TEXT field | PART F5 - MATERIAL AND WELDS
BUTT_TEXT | VARCHAR2 | Weld - Butt | PART F5 - MATERIAL AND WELDS
BUTTO | VARCHAR2 | Text describing Other for BUTT_TEXT field | PART F5 - MATERIAL AND WELDS
FILLET_TEXT | VARCHAR2 | Weld - Fillet | PART F5 - MATERIAL AND WELDS
FILLETO | VARCHAR2 | Text describing Other for FILLET_TEXT field | PART F5 - MATERIAL AND WELDS
PIPE_SEAM_TEXT | VARCHAR2 | Weld - Pipe seam | PART F5 - MATERIAL AND WELDS
PIPE_SEAMO | VARCHAR2 | Text describing Other for PIPE_SEAM_TEXT field | PART F5 - MATERIAL AND WELDS
FAIL_TYPE_TEXT | VARCHAR2 | Type of failure | PART F5 - MATERIAL AND WELDS
CONS_DEF_TEXT | VARCHAR2 | Type of construction defect | PART F5 - MATERIAL AND WELDS
PIPE_DAMAGE | VARCHAR2 | Was failure due to pipe damage sustained in transportation to the construction or fabrication site | PART F5 - MATERIAL AND WELDS
PRS_TEST | VARCHAR2 | Was part which leaked pressure tested before incident occurred | PART F5 - MATERIAL AND WELDS
TEST_MO | NUMBER | Month of pressure test | PART F5 - MATERIAL AND WELDS
TEST_DAY | NUMBER | Day of pressure test | PART F5 - MATERIAL AND WELDS
TEST_YR | NUMBER | Year of pressure test | PART F5 - MATERIAL AND WELDS
TEST_MED_TEXT | VARCHAR2 | Type of test medium | PART F5 - MATERIAL AND WELDS
TEST_MEDO | VARCHAR2 | Text describing Other for TEST_MED_TEXT field | PART F5 - MATERIAL AND WELDS
TEST_TP | NUMBER | Time held at test pressure in hours | PART F5 - MATERIAL AND WELDS
TEST_PRS | NUMBER | Estimated test pressure at point of incident, PSIG | PART F5 - MATERIAL AND WELDS
MALFUNC_TEXT | VARCHAR2 | Malfunction of control/relief equipment | PART F6 - EQUIPMENT AND OPERATIONS
MALFUNCO | VARCHAR2 | Text describing Other for MALFUNC_TEXT field | PART F6 - EQUIPMENT AND OPERATIONS
THREADS_TEXT | VARCHAR2 | Threads stripped, broken pipe coupling | PART F6 - EQUIPMENT AND OPERATIONS
THREADSO | VARCHAR2 | Text describing Other for THREADS_TEXT field | PART F6 - EQUIPMENT AND OPERATIONS
IO_TYPE_TEXT | VARCHAR2 | Type of Incorrect operation | PART F6 - EQUIPMENT AND OPERATIONS
IO_TYPEO | VARCHAR2 | Text describing Other for IO_TYPE_TEXT field | PART F6 - EQUIPMENT AND OPERATIONS
IO_DRUG | NUMBER | Employee that filed post-incident drug test | PART F6 - EQUIPMENT AND OPERATIONS
IO_ALCO | NUMBER | Employee that filed post-incident alcohol test | PART F6 - EQUIPMENT AND OPERATIONS
IO_SENIOR | VARCHAR2 | Were most senior employee(s) involved qualified (Y/N) | PART F6 - EQUIPMENT AND OPERATIONS
IO_SEN_HRS | NUMBER | Number of hours senior employee(s) on duty | PART F6 - EQUIPMENT AND OPERATIONS
MISC | VARCHAR2 | Describe Miscellaneous | PART F7 - OTHER
UNKNOWN_TEXT | VARCHAR2 | Unknown | PART F7 - OTHER
NARRATIVE | VARCHAR2 | Narrative | PART G - NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE EVENT

## gtgg2002to2009
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | SYSTEM_TYPE | RPTID | DOR | REPORT_TYPE | OPERATOR_ID | OWNER_OPERATOR_ID | NAME | OPSTREET | OPCITY | OPCOUNTY | OPSTATE | OPZIP | IHOUR | IDATE | IYEAR | ACCITY | ACCOUNTY | ACSTATE | ACZIP | MPVST | SURVNO | LATITUDE | LONGITUDE | OFFSHORE_TEXT | CLASS | OFFAREA | BNUMB | OFFST | OCS | IFED | INTER_TEXT | LRTYPE_TEXT | LRTYPEO | LEAK_TEXT | PUNC_DIAM | RUPTURE_TEXT | RUPLN | PROPLN | FATAL | EFAT | GPFAT | NFAT | INJURE | EINJ | GPINJ | NINJ | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | GASPRP | GASPRPCURRENT | OPPRP | OPPRPCURRENT | PPPRP | PPPRPCURRENT | HIGHCON | IGNITE | EXPLO | EVAC | EVACNO | EVAC_REASON_TEXT | STHH | STMN | TELRN | TELDT | INC_PRS | MAOP | MAOPSEC1 | MAOPSEC2 | MAOPSEC3 | MAOPSEC4 | MAOPSECC | OVERPRS | PNAME | PHONE | PEMAIL | TYSYS_TEXT | PRTFL_TEXT | PRTFO | MLKD_TEXT | MLKDO | PLAS_DUCT | PLAS_BRIT | PLAS_JNT | PRTSY_TEXT | PRTSYO | PRTYR | NPS | WALLTHK | SPEC | SMYS | SEAM | VALVE | MANU | MANYR | LOCLK_TEXT | LOCLKO | DEPTH_COV | CAUSE | CAUSE_DETAILS | MAP_CAUSE | MAP_SUBCAUSE | PIPE_COAT_TEXT | VIS_EXAM_TEXT | VIS_EXAMO | COR_CAUSE_TEXT | COR_CAUSEO | PROT | CPYR | PREV_DAM | PREV_DAM_YR | PREV_DAM_MO | EARTH_MOVE_TEXT | EARTH_MOVEO | FLOODS_TEXT | FLOODSO | TEMPER_TEXT | TEMPERO | THIRD_PARTY_GRP_TEXT | THIRD_PARTY_TYPE_TEXT | THIRD_PARTY_TYPEO | NOTIF | NOTIF_MO | NOTIF_DAY | NOTIF_YR | NOTIF_RCVD_TEXT | MARKED | TEMP_MARK_TEXT | PERM_MARK | ACC_MARK_TEXT | MKD_IN_TIME | FIRE_EXPLO_TEXT | PIPE_BODY_TEXT | PIPE_BODYO | COMPONENT_TEXT | COMPONENTO | JOINT_TEXT | JOINTO | BUTT_TEXT | BUTTO | FILLET_TEXT | FILLETO | PIPE_SEAM_TEXT | PIPE_SEAMO | FAIL_TYPE_TEXT | CONS_DEF_TEXT | PIPE_DAMAGE | PRS_TEST | TEST_MO | TEST_DAY | TEST_YR | TEST_MED_TEXT | TEST_MEDO | TEST_TP | TEST_PRS | MALFUNC_TEXT | MALFUNCO | THREADS_TEXT | THREADSO | IO_TYPE_TEXT | IO_TYPEO | IO_DRUG | IO_ALCO | IO_SENIOR | IO_SEN_HRS | MISC | UNKNOWN_TEXT | NARRATIVE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020022 | 2002-03-04 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO (ENRON) | PO BOX 1188 | HOUSTON | HARRIS | TX | 77251 | 1130 | 2002-01-26 | 2002 | [6 empty] | N27 43.413 | W96 34.013 | OFFSHORE |  | MUSTANG ISLAND | 758 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300000 | 937399.4657 | 1693544.2638 | 300000 | 249757.2816 | 1000000 | 1443786.9822 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 592303 | 2002-01-26 | 944 | 1440 | YES | NO | NO | NO | NO | NO | MERLIN MOSEMAN | 7133451625 | MERLIN.MOSEMAN@ENRON.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 24 | 0.41 | API 5LX | 60000 | DSAW |  | KAISER STEEL | 1981 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | PINHOLE LEAK | OTHER | UNKNOWN | YES | 1982 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020026 | 2002-04-03 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77040 | 418 | 2002-03-06 | 2002 | JEFFERSONVILLE | MONTGOMERY | KY | 40337 | NEAR MLV 107-3 | +5.0FT | N37 59' 34 | W 83 48' 29 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2011000 | 1541822.1477 | 2438284.6987 | 761000 | 633550.9709 | 1210000 | 1746982.2485 | 40000 | 57751.4793 | NO | NO | YES | NO | 0 |  | 7 | 0 | 595736 | 2002-03-06 | 670 | 750 | NO | NO | NO | NO | YES | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 26 | 0.38 |  | 52000 | DSAW |  | A O SMITH | 1950 | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | CRACK NEAR WELD SADDLE | [10 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | NO | [19 empty] | THERE WAS A RUPTURE IN THE COMPRESSOR STATION YARD, ON LINE 100-3 AT MLV 107-3, RESULTING IN A FIRE AND EXPLOSION. FAILURE STILL UNDER INVESTIGATION. 9-6-02 THE FAILURE ORIGINATED AT A LONGITUDINAL CRACK AT TOE OF A BRANCH REINFORCEMENT SADDLE FILLET WELD. CRACK PROPAGATED TO CRITICAL SIZE BY FATIGUE DUE TO EFFECTS OF OPERATING PRESSURE CYCLES. THE ROOT FLAW, FROM WHICH THE FATIGUE INITIATED, WAS A SMALL CRACK AT THE TOE OF THE SADDLE FILLET WELD.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20020027 | 2002-04-08 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | PO BOX 21628 | TULSA | TULSA | OK | 74121 | 1640 | 2002-03-13 | 2002 | TERREBONNE | TERREBONNE | LA |  | 3.98 |  | 29 12' 54.70 | 91 10' 40.42 | OFFSHORE |  | POINT AU-FER | 5 | LA | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190000 | 127783.2768 | 265761.8487 | 14000 | 11655.3398 | 176000 | 254106.5089 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 596481 | 2002-03-13 | 631 | 1440 | NO | YES | NO | NO | NO | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 16 | 0.31 | API 5LX | 52000 | FLASH WELD |  | A O SMITH | 1959 | UNDER WATER |  | 96 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | GENERAL | YES | 1959 | NO | [57 empty] | WHILE TRANSPORTING OPERATIONAL PERSONNEL BACK TO SHORE BUBBLES WERE NOTICED IN THE PIPELINE GENERAL LOCATION. THE BUBBLES WERE INVESTIGATED AND IT WAS DETERMINED THA THE N SHIP SHOALS 16-INCH WAS LEAKING. LEAK WAS EVALUATED AND REPAIRED WITH A LEAK CLAMP, THIS WAS THE FIRST LEAK REPORTED ON THIS LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020028 | 2002-04-02 | SUPPLEMENTAL FINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1630 | 2002-02-28 | 2002 | [6 empty] | 29 20 10.3694 | 092 00 44.3974 | OFFSHORE |  | SOUTH MARSH ISLAND | 236 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171342 | 111705.032 | 246647.8339 | 1200 | 999.0291 | 170142 | 245648.8047 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 595652 | 2002-03-05 | 900 | 1440 | YES | NO | NO | NO | NO | NO | JAMES R MCDONALD | 7138032494 | JIM.MCDONALD@EPROD.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 8 | 0.41 | GRADE B | 35000 |  |  | US STEEL | 1983 |  |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | GARLAND GASPARD OF EL PASO FIELD SERVICES WAS CONTACTED ABOUT A POSSIBLE LEAK ON IN SMI 236 AT 4:30PM, THURSDAY, FEBRUARY 28, 2002. MR. GASPARD CONTACTED MR. JOE HENNESSEY OF THE MMS TO DISCUSS THE INFORMATION REGARDING A REPORTED LEAK. MR. HENNESSEY STATED THAT CHEVRON/TEXACO WAS INVESTIGATING A LEAK AND THAT A DETERMINATION HAD NOT YET BEEN MADE AS TO WHETHER THE LEAK WAS ON THE EPFS LATERAL OR CHEVRON/TEXACO SALES LINE WHICH PARALLEL EACH OTHER. MR. GASPARD CONTACTED MR. JIM PRICE OF CHEVRON/TEXACO AT 5:05 PM THAT SAME DATE. MR. PRICE, LOCATED AT TEXACO'S SMI 236 PLATFORM INDICATED THAT THEY HAD NOTICED A LEAK AT APPROXIMATELY 10:00AM ON THE 28TH OF FEBRUARY. HE INDICATED GAS BUBBLES WERE VISIBLE AND THAT NO SHEEN WAS EVIDENT ON THE WATER. HE ALSO STATED THAT THEY HAD ORDERED A DIVING CREW TO INVESTIGATE. MR. PRICE ALSO STATED THAT HE FELT THE LEAK WAS ON THEIR LINE SINCE OUR LINE HAD BEEN OUT OF SERVICE AND THE PRESSURE GAUGE ON OUR LINE INDICATED ZERO PRESSURE ON OUR LINE. HE ALSO NOTED THAT THE VALVES ON THE EPFS LINE WERE CLOSED AND FINALLY THAT THEY BELIEVED THEY HAD NOTICED A PRESSURE DECLINE IN THEIR SYSTEM. FURTHERMORE, MR. PRICE CONTACTED MR. GASPARD AT APPROXIMATELY 9:05PM AND INFORMED MR. GASPARD THAT THE DIVERS HAD FOUND THE LEAK TO BE ON THE TEXACO/CHEVRON LINE. CHEVRON/TEXACO TOOK ACTIONS TO ISOLATE THEIR LINE AND BY THE FOLLOWING MORNING, THE BUBBLES HAD STOPPED. WEATHER CONDITIONS AND WATER CONDITIONS WERE ROUGH. ON TUESDAY, MARCH 5, 2002 THE WEATHER CLEARED AND CHEVRON/TEXACO WAS ABLE TO SEND DOWN ANOTHER DIVING CREW. THE DIVERS CONFIRMED THAT THE LEAK WAS ON THE EPFS LINE AND NOT ON THE CHEVRON/TEXACO LINE. MR. GASPARD RECEIVED THIS CONFIRMATION FROM THE DIVERS AT 9:00 AM ON THE MORNING OF MARCH 5, 2002. THE NRC WAS NOTIFIED BY JIM MCDONALD, EPFS COMPLIANCE DEPARTMENT, OF THIS INCIDENT AT 10:50 AM ON MARCH 5, 2002 AND THE INCIDENT WAS ASSIGNED CASE NUMBER 595652. A DECISION TO PREMANENTLY ABANDON THE SMI LATERAL WAS REACHED BY EPFS AND THE ABANDONMENT WAS COMPLETED ON MARCH 13, 2002. IN A FAX SENT BY MR. JOE HENNESSEY, MMS DATED 3/13/2002, EL PASO FIELD SERVICES RECEIVED CONFIRMATION THAT OUR ABANDONMENT PROCEDURE HAD BEEN APPROVED. THE ABANDONMENT WAS FOR AN 8 INCH GAS PIPELINE. SEGMENT NO 6872 ASSOCIATED WITH RIGHT OF WAY OCS-G 5941. FINAL PROJECT COST INCLUDING ABANDONMENT FEES AND GAS LOSS TOTALED $171.342.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020029 | 2002-04-11 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1130 | 2002-03-04 | 2002 | WEST FRIENDSHIP | HOWARD | MD |  | 1631.398 | 1448+44 |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 238566.5157 | 483277.1978 | 36070 | 30029.1505 | 313930 | 453248.0473 | 0 | 0 | NO | NO | NO | NO | 0 |  | 10 | 0 | 595713 | 2002-03-05 | 760 | 780 | NO | NO | NO | NO | YES | NO | B R LANDES | 7132152001 | BILL.R.LANDES@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 30 | 0.38 | API 5L | 52000 | DSA |  | NATIONAL TUBE | 1955 | UNDER GROUND |  | 46 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | MILL DEFECT | [10 empty] | MATERIAL DEFECT |  | NO | YES | 6 | 1 | 1981 | WATER |  | 8 | 1117 | [12 empty] | COMPANY EMPLOYEE WHILE MOWING ROW FOUND GAS ESCAPING FROM THE VENT PIPE OF THE CASED CROSSING OF HWY 40. AFTER PIPELINE WAS ISOLATED AND BLOWN DOWN, INVESTIGATION FOUND THE LEAK TO BE INSIDE THE EXTENDED CASING THAT WAS NOT UNDER THE ROAD PAVEMENT. FURTHER EXAMINATION FOUND THAT DUE TO A PIPE MILL DEFECT, AN INTERNAL CRACK DEVELOPED CAUSING THE PINHOLE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020030 | 2002-04-12 | SUPPLEMENTAL FINAL | 6660 |  | GREAT LAKES GAS TRANSMISSION CO | 5250 CORPORATE DRIVE | TROY | OAKLAND | MI | 48098 | 547 | 2002-03-15 | 2002 | CRYSTAL FALLS | IRON | MI | 49920 | MP 495.34 | 402+17 TO 402+86 | 46 04' 59N | 88 19'04W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 7 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104629 | 2157814.4594 | 4204460.9976 | 454734 | 378577.0922 | 2248783 | 3246763.6213 | 401112 | 579120.284 | NO | NO | NO | NO | 0 |  | 1 | 15 | 596599 | 2002-03-15 | 958 | 974 | YES | NO | NO | NO | NO | NO | ROBERT J CADORIN | 2482057669 | RCADORIN@GLGT.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 36 | 0.38 | API 5LX X-65 | 65000 | DSAW |  | BETHLEHEM STEEL | 1968 | UNDER GROUND |  | 96 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | SCC | STRESS CORROSION CRACKING |  | YES | 1968 | [58 empty] | UPON COMPLETION OF THE FAILURE INVESTIGATION, A FINAL REPORT WILL BE SUBMITTED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020031 | 2002-04-12 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET #100 | HOUSTON | HARRIS | TX | 77002 | 1315 | 2002-03-18 | 2002 | STREAMWOOD | COOK | IL | 60107 |  |  | 42.011172 | -88.170544 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1810 | 1732.2259 | 1512.9816 | 1800 | 1498.5437 | 10 | 14.4379 | 0 | 0 | NO | NO | NO | YES | 10 | PRECAUTIONARY | 1 | 0 |  |  | 582 | 687 | YES | NO | NO | NO | NO | NO | JAMES PHILLIPS | 3039147753 | JIM.PHILLIPS@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 1 | 0.13 | A-105 | 35000 | SEAMLESS |  |  |  | OPEN DITCH |  | 48 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020032 | 2002-04-15 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO (ENRON) | 1400 SMITH STREET | HOUSTON | HARRIS | TX | 77002 | 1115 | 2002-02-22 | 2002 | SIOUX FALLS | DAKOTA | NE |  | MP 1.4 |  | 46 26.3' | 96 23.4' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73000 | 68443.0653 | 63830.5854 | 68000 | 56611.6505 | 5000 | 7218.9349 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 594752 | 2002-02-22 | 600 | 700 | NO | NO | NO | NO | YES | NO | PATRICK L VAUGHAN | 7133451637 | PAT.VAUGHAN@ENRON.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1940 | 16 | 0.31 | SL | 42000 | SMLS |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | VANDALISM | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [65 empty] | LEAKING GAS WAS REPORTED BY A CONTRACTOR WHO WAS CHANGING LIGHT BULBS ON THE MISSOURI RIVER BRIDGE, AN AERIAL PIPELINE CROSSING OWNED BY NNG. THE GAS WAS LEAKING FROM A HOLE IN THE LOWER QUADRANT OF THE PIPE ABOUT 30 FEET ABOVE GROUND 35 FEET FROM THE WEST BRIDGE SUSPENSION LEG. INTERVIEWS WITH PERSONS WORKING IN THE VICINITY INDICATE THAT THE GAS MAY HAVE BEEN LEAKING FOR AS LONG AS TWO WEEKS BUT IT WAS NOT REPORTED BECAUSE IT WAS NOT DISCERNABLE FROM OTHER TRAFFIC AND INDUSTRIAL NOISE IN THE AREA. THE PUNCTURE WAS APPARENTLY CAUSED BY A LARGE CALIBER FIRE ARM. NO REMANTS OF PROJECTILE WERE FOUND. THE AFFECTED SECTION OF PIPE WAS ISOLATED, BLOWN DOWN, AND REPAIRED. NO DELIVERIES WERE INTERRUPTED AND THE PIPELINE WAS RETURNED TO SERVICE FOLLOWING REPAIR.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020033 | 2002-04-24 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 852 | 2002-03-26 | 2002 | RAWLINS | CARBON | WY |  | LINE 124A | 8400+00 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145000 | 132837.7951 | 132941.2736 | 125000 | 104065.534 | 20000 | 28875.7396 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 597655 | 2002-03-26 | 850 | 1000 | NO | NO | NO | NO | YES | NO | LOUIS A SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 36 | 0.36 | 5L | 70000 | DSAW |  | VALOUREC | 1982 | UNDER GROUND |  | 50 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | CRACK IN WELD |  |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 7 | 22 | 1982 | WATER |  | 8 | 1348 | [12 empty] | A LEAK WAS DISCOVERED DURING F 1 LEAK SURVEY OF WIC LINE, NEAR 8400+00. A CRACK IN A GIRTH WELD WAS FOUND.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020034 | 2002-04-24 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1430 | 2002-03-26 | 2002 | CLAY | JACKSON | OH |  | MLV 202-4 +14.0 | MP 14.0 | N39 05.339 | W82 27.054 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 57842.8578 | 76614.5803 | 40000 | 33300.9709 | 30000 | 43313.6095 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 597677 | 2002-03-26 | 645 | 790 | YES | NO | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 36 | 0.33 |  | 60000 | DSAW |  | BETHLEHEM STEEL | 1966 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1966 | NO | [57 empty] | THERE WAS A LEAK NEAR MP 202-4 + 14.0. WHILE CONDUCTING A C P SURVEY, PIPELINE PERSONNEL LOCATED A GAS LEAK. THE LEAK WAS THE RESULT OF EXTERNAL CORROSION. THE EXTERNAL CORROSION THINNED THE PIPE WALL TO A POINT THAT THE REMAINING LIGAMENT OF MATERIAL CRACKED IN A DUCTILE MANNER DUE TO HOOP STRESS FROM INTERNAL PRESSURE. THE VISUAL, CHEMICAL AND BIOLOGICAL FIELD DATA INDICATE THAT MICROBIOLOGICALLY INFLUENCED CORROSION (MIC)WAS THE PROBABLE CAUSE OF CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020035 | 2002-04-25 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 505 | 2002-03-19 | 2002 | FORT HILL | ASHLEY | AR | 71646 | 46.2 | 2438+52 | 33.36838 | -91.92806 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159000 | 124015.0227 | 188607.5286 | 67000 | 55779.1262 | 92000 | 132828.4024 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 55 | 596939 | 2002-03-19 | 420 | 450 | NO | NO | NO | NO | YES | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | DRESSER COUPLING | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 22 | 0.31 | API 5L | 30000 | MACHINE ELEC FUSION ARC WELD | NA | A O SMITH | 1929 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | FLOTATION | [52 empty] | THE PIPE PULLED APART IN THE BOTTOM OF A SMALL CREEK CROSSING. FROM THE INITIAL EVALUATION IT APPEARS THAT HIGH WATER DUE TO HEAVY RAINS CAUSED THE PIPELINE TO FLOAT AND SEPARATE AT A DRESSER COUPLING.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20020036 | 2002-05-01 | SUPPLEMENTAL FINAL | 26330 |  | ENOGEX INC (EX. MUSTANG FUEL CORP) | 515 CENTRAL PARK DRIVE | OKLAHOMA CITY | OKLAHOMA | OK | 73124 | 800 | 2002-02-08 | 2002 | PERRY | NOBLE | OK |  | BET MP 48 & 49 |  | N36 19 08.874 | W97 21 24.206 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 15 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 122458 | 104915.7321 | 126658.9411 | 82034 | 68295.2961 | 39924 | 57641.7515 | 500 | 721.8935 | NO | NO | NO | YES | 10 | PRECAUTIONARY | 0 | 40 | 593413 | 2002-02-08 | 685 | 780 | NO | YES | NO | NO | NO | NO | JOEY ROCKETT | 4055584692 | ROCKETJD@OGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 20 | 0.25 | X-52 |  | ERW |  |  |  | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | YES | FLAGS | YES | ACCURATE | [37 empty] | LINE 7 RUPTURED AFTER BEING HIT BY A THIRD PARTY EXCAVATING ON THE PIPELINE RIGHT OF WAY. NO REQUEST FOR LINE LOCATE WAS ISSUED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020038 | 2002-05-09 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1500 | 2002-04-14 | 2002 |  |  | LA |  | SV 509A-1121 | 0+00 | 28 35' 1.85 | 92 31' 1.92 | OFFSHORE |  | VERMILLION | 243 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 58788.9893 | 129329.5657 | 1000 | 832.5243 | 89000 | 128497.0414 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 599584 | 2002-04-14 | 912 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 12 | 0.5 |  | 42000 | SMLS |  | US STEEL | 1978 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1978 | NO | [57 empty] | THERE WAS A LEAK ON TGP LINE 509A- 1100, AT SV 509A-1121, IN VERMILLION BLOCK 243, GULF OF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS DUE TO GAS ESCAPING AROUND A RING TYPE JOINT (RTJ) GASKET, THAT HAD BEEN DAMAGED BY CORROSION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020039 | 2002-05-24 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION INC | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302 | 623 | 2002-05-24 | 2002 | CLENDENIN | KANAWHA | WV | 25045 | CORNWELL COMP. STATION | CORNWELL COMP. STATION | N/A | N/A | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | OTHER | DEHYDRATION SYSTEM FAILURE/FIRE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 40212.8993 | 56907.7814 | 25000 | 20813.1068 | 0 | 0 | 25000 | 36094.6746 | NO | YES | NO | NO | 0 |  | 0 | 37 | 600609 | 2002-04-24 | 320 | 500 | NO | NO | NO | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C_SCHWOEBLE@DOM.COM | TRANSMISSION | OTHER | DEHYDRATION SYSTEM | OTHER | DEHYDRATION UNIT/SYSTEM | NO | NO | NO | COMPRESSOR |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | NATCO | 1999 | ABOVE GROUND |  | 0 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | STILL UNDER INVESTIGATION | DEHYDRATION SYSTEM EXPERIENCED AN UPSET MODE. AN INSPECTION HAS INITIALLY BEEN COMPLETED BUT FURTHER INVESTIGATION IS NECESSARY TO RESOLVE THIS INCIDENT AND WILL BE FORWARDED AS A SUPPLEMENTAL REPORT. A MEETING WAS HELD WITH ED CLARKSON,DAVE HIPPCHEN AND DARRELL MCKOWN OF THE WV PSC ON MAY 24, 2002.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020040 | 2002-05-29 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY - PO BOX 58900 | SALT LAKE CITY | SALT LAKE | UT | 84158 | 805 | 2002-04-16 | 2002 | KALAMA | COWLITZ | WA |  | 1250.25 | 9818+33 SEC 14 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 124674.427 | 217325.7023 | 46000 | 38296.1165 | 124000 | 179029.5858 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 599797 | 2002-04-16 | 650 | 809 | NO | NO | NO | NO | YES | NO | LARRY D OLSEN SR | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.28 | 5LX52 | 1124 | LONGITUDINAL WELD |  | CONSOLIDATED WEST | 1956 | UNDER GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | PIPE WAS RESTING ON SHARP SOLID ROCK DURING PIPELINE ORIGINAL CONSTRUCTION
2022-01-31 10:32 | YES | YES | GG (Gas Gathering) | 20020041 | 2002-06-04 | ORIGINAL FINAL | 20132 |  | UNION OIL CO OF CALIFORNIA | 260 CAVIAR STREET | KENAI | KENAI PENINSULA | AK | 99611 | 1545 | 2002-04-15 | 2002 | KENAI | KENAI BOROUGH | AK | 99611 | VAULT BOX G 881+63 |  | 60 40' 32N | 151 22' 33W | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | VALVE VAULT DAMAGED | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 30000 | 24127.7396 | 34144.6688 | 15000 | 12487.8641 | 15000 | 21656.8047 | 0 | 0 | NO | NO | NO | YES | 0 | THREAT TO THE PUBLIC | 5 | 0 | 599737 | 2002-04-15 | 720 | 975 | NO | YES | NO | NO | NO | NO | RAND STEVEN PRICE | 9072835514 | PRICER@UNOCAL.COM | GATHERING | OTHER | CINDERBLOCK VALVE VAULT DAMAGED | STEEL |  | NO | NO | NO | OTHER | VALVE VAULT | 1965 | 10 | 0.34 | A106B |  | SEAMLESS | GATE | CRANE | 1965 | ABOVE GROUND |  | 48 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A ONE TON FLAT BED TRUCK WITH ONE PERSON DRIVING STRUCK A CINDERBLOCK VALVE VAULT (VAULT BOX G) AT A HIGH RATE OF SPEED, KNOCKING THE ROOF OFF THE TOP OF THE VAULT AND SHEARING OFF 3 TIERS OF THE CINDERBLOCK WALLS. THE TRUCK CAME TO REST ON TOP OF THE VAULT WITH A REAR WHEEL TOUCHING A CINDERBLOCK THAT CAME TO REST ON TOP OF THE VALVE. THE DRIVER WAS INJURED AND TAKEN TO THE LOCAL HOSPITAL WITH NON-LIFE THREATING INJURIES. THERE WAS NO GAS LEAK, FIRE OR EXPLOSION. THE PIPELINE WAS ISOLATED AND DEPRESSURED FROM 720 PSI TO 100 PSI TO ALLOW A 17 TON CRANE TO REMOVE THE TRUCK FROM ON TOP OF THE VAULT BOX. THE ROAD WAS BLOCKED TO PREVENT CARS PASSING UNTIL AFTER THE TRUCK WAS REMOVED. ONCE THERE WAS ACCESS TO THE VAULT AND IT WAS AGAIN VERIFIED THERE WAS NO GAS LEAK, A UNOCAL PIPELINE INSPECTOR INSPECTED THE VALVE AND PIPING IN WHAT WAS LEFT OF THE VAULT, CONCLUDING THAT THERE WAS MINOR DAMAGE TO THE VALVE HANDLE, BUT THE VALVE WAS STILL SERVICEABLE WITH NO REQUIREMENT FOR REPLACEMENT OR REPAIR. THE COATING HAD MINOR DAMAGE FROM THE FALLING BLOCKS AND THE PIPING WAS FIT FOR SERVICE, NO DENTS, GOUGES, OR SCRATHES. THE SITE WAS SECURED AND THE SYSTEM PRESSURE BACK UP TO NORMAL OPERATING PRESSURE. PLANS ARE TO REPAIR THE COATING DAMAGE; THE REMAINING BLOCK WALL WILL BE CUT DOWN TO GROUND LEVEL AND A NEW CONCRETE ROOF INSTALLED ON TOP SO IT IS FLUSH WITH THE GROUND; AND FOUR 6" BOLLARDS INSTALLED AT EACH CORNER OF THE VAULT AND PAINTED FOR HIGH VISIBILITY.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020043 | 2002-06-05 10:28 | SUPPLEMENTAL | 12690 |  | MONTANA POWER CO | 40 EAST BROADWAY | BUTTE | SILVER BOW | MT | 59701 | 1400 | 2002-05-18 | 2002 | REED POINT | SWEET GRASS | MT | 59069 | MP 0.95 | ~50+00 | 45DEG41MINN | 109DEG36MINE WGS84 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | UNKNOWN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 38668.1005 | 59964.0949 | 20000 | 16650.4854 | 30000 | 43313.6095 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 605010 | 2002-05-18 | 564 | 960 | YES | NO | NO | NO | NO | NO | JAY WATERMAN | 4064972441 | JAY.WATERMAN@NORTHWESTERN.COM | TRANSMISSION | OTHER | UNKNOWN | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 6 | 0.28 | API 5L GR B | 35000 | ERW | NA | LONESTAR STEEL | 1978 | UNDER WATER |  | 0 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | SCOURING | [52 empty] | THE NORTHWESTERN ENERGY LLC (FORMERLY MONTANA POWER CO) BIG COULEE TO REED POINT 6" NATURAL GAS TRANSMISSION PIPELINE FAILED IN THE YELLOWSTONE RIVER CROSSING ON MAY 18, 2002 DURING A HIGH WATER RUNOFF EVENT. THE APPARENT CAUSE OF THE FAILURE IS SCOURING. DUE TO THE EXTREME HIGH WATER, THE PIPELINE FAILURE POINT HAS NOT YET BEEN VISUALLY INSPECTED. THE FAILED SECTION IS SHUT-IN AND BLOWN DOWN. ARRANGEMENTS ARE BEING MADE FOR A REPLACEMENT RIVER CROSSING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020044 | 2002-06-11 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO (ENRON) | PO BOX 1188 | HOUSTON | HARRIS | TX | 77251 | 845 | 2002-05-02 | 2002 | TALLAHASSEE | LEON | FL |  | 0.00 | 0+00 | 30.3473 | 84.2576 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202000 | 193047.129 | 169392.4283 | 200000 | 166504.8544 | 2000 | 2887.574 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 601767 | 2002-05-02 | 1080 | 1235 | YES | NO | NO | NO | NO | NO | MERLIN MOSEMAN | 7133451625 | MERLIN.MOSEMAN@ENRON.COM | TRANSMISSION | OTHER | GASKET | OTHER | PHENOLIC | NO | NO | NO | PIPELINE |  | 1999 | [8 empty] | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | LEAK RESULTED FROM FAILURE OF 8" DIAMETER. CLASS 600 INSULATING TYPE FLANGE GASKET.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20020045 | 2002-06-14 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35203 | 1641 | 2002-05-16 | 2002 | CARY | SHARKEY | MS |  | N MAIN LOOP LINE | 5241 | 32^42'43 | -90^56'56 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LINE SEPARATED AT MECHANICAL COUPLING | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 37351 | 26541.0252 | 49433.4954 | 7351 | 6119.8859 | 30000 | 43313.6095 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 40 | 604558 | 2002-05-16 | 445 | 500 | NO | NO | NO | NO | YES | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | MECHANICAL COUPLING | STEEL |  | NO | NO | NO | PIPELINE |  | 1939 | 18 | 0.21 |  | 35000 | SEAMLESS |  | NATIONAL TUBE | 1939 | UNDER GROUND |  | 36 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | MECHANICAL COUPLINGS | [9 empty] | LINE SEPARATED AT THE COUPLING, MP 63.988 ON THE NORTH MAIN LOOP LINE NEAR THE ONWARD COMPRESSOR STATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020046 | 2002-06-17 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1617 | 2002-05-21 | 2002 | KENSINGTON | CARROLL | OH |  | MLV 214-3 + 8.315 | MP 214-3 + 439+08 | 40.708651 | -80.940615 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 56298.059 | 79670.8939 | 35000 | 29138.3495 | 35000 | 50532.5444 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 605596 | 2002-05-21 | 645 | 790 | NO | NO | YES | NO | NO | NO | LOUIS A SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 26 | 0.28 |  | 52000 | DSAW |  | NATIONAL TUBE | 1956 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | NO | [19 empty] | THERE WAS A LEAK NEAR MLV 214-3 + 439.08. LANDOWNER DISCOVERED DEAD VEGETATION IN VICINITY OF TGP PIPELINE. COMPANY INVESTIGATED FURTHER AND FOUND A LEAK. PIN HOLE LEAK WAS LOCATED ON THE LONGITUDINAL SEAM. MANUFACTURING DEFECT WAS DETERMINED TO BE THE CAUSE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20020047 | 2002-06-25 | ORIGINAL | 31547 |  | VOYAGEUR PIPELINE LLP | 13358 GARDEN GROVE | HOUSTON | HARRIS | TX | 77082 | 1515 | 2002-02-20 | 2002 | LONGVIEW | GREGG | TX | 75605 | 4.5 |  | 32.5418 | -94.7486 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO | NO | YES | 12 | THREAT TO THE PUBLIC | 3 | 0 |  | 2002-02-20 | 220 | 815 | NO | NO | YES | NO | NO | NO | GREG GEE | 9036632477 |  | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 8 | 0.25 | X-42 SMLS | 42000 |  |  | NATIONAL TUBE | 1956 | UNDER GROUND |  | 156 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1978 | NO | [57 empty] | APPARENT CORROSION IN BOTTOM OF PIPING CAUSING TWO HOLES IN PIPE. ONE HOLE APPROXIMATELY 3/8" IN DIAMETER, SECOND HOLE APPROXIMATELY 1/4" TO 3/8" LONG. HOLES WERE APPROXIMATELY 18" APART. BAKER CHEMICALS ANALYZED SECTION OF PIPE INDICATING CORROSION WAS BACTERIAL IN ORIGIN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020048 | 2002-06-28 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 200 | 2002-05-31 | 2002 | PATTERSON | ST MARYS | LA | 70392 |  |  | 29.724 | -91.342 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | VAPOR/AIR FROM NEW EQUIPMENT OPERATIONS IGNITED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1299865.1728 | 2886962.7018 | 1000 | 832.5243 | 1999000 | 2886130.1775 | 0 | 0 | NO | NO | YES | NO | 0 |  | 12 | 40 | 607583 | 2002-05-31 |  |  | NO | NO | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | TANK FACILITY | STEEL |  | NO | NO | NO | OTHER | STORAGE TANK FARM | 2002 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | OTHER | SEE DESCRIPTION | 0 | 0 | Y | 8 |  |  | AN EXPLOSION OCCURRED AT THE TANK TERMINAL FACILITY, RESULTING IN A FIRE. SEVERAL OIL AND DISTILLATE TANKS WERE DAMAGED. A NEW LOW PRESSURE TANK VENT SYSTEM WAS PLACED INTO OPERATION AND PRODUCED AN EXPLOSIVE MIXTURE OF HYDROCARBON VAPOR/AIR WITHIN THE DRY OIL TANK #1, AND THE LOW PRESSURE FLARE SYSTEM. THE LOW PRESSURE SUCTION SHUTDOWN SWITCH HAD BEEN DE-ACTIVATED, ALLOWING THE LOW PRESSURE BLOWER TO CONTINUE TO RUN, PULLING THE DEVELOPING EXPLOSIVE FUEL/AIR MIXTURE THROUGH THE FLARE SYSTEM. THE EXPLOSIVE MIXTURE WAS IGNITED WHEN IT WAS VENTED THROUGH THE LOW PRESSURE FLARE SYSTEM AND REACHED THE FLARE FLAME, WHERE IT FLASHED BACK AND BURNED AT THE DETONATION FLAME ARRESTOR OUTLET. AFTER THE DETONATION FLAME ARRESTOR BECAME COMPROMISED, THE FUEL/AIR MIXTURE FLASHED BACK TO THE BLOWER AND INTO DRY OIL TANK #1, RESULTING IN THE EXPLOSION AND FIRE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20020049 | 2002-07-10 | ORIGINAL | 19310 |  | TEXAS NATURAL GAS CO | 106 SOUTH FIRST ST | CROWELL | FOARD | TX | 79227 | 1030 | 2002-04-18 | 2002 | THALIA |  | TX | 79227 |  |  |  |  | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | OTHER | PRESSURE TESTING RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 318 | 90.9689 | 202.1302 | 0 | 0 | 140 | 202.1302 | 0 | 0 | NO | NO | YES | NO | 0 | [5 empty] | 100 | 140 | NO | NO | NO | NO | NO | NO | R E CULBERTSON | 8173329493 |  | TRANSMISSION | OTHER | RELIEF VALVE |  |  | NO | NO | NO | OTHER | RELIEF VALVE | [12 empty] | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | MR RICHARD HERNANDEZ & JAMES E MORCOM WERE PRESSURE TESTING A RELIEF VALVE. THE TEXAS RAILROAD COMMISSION REQUIRES TWICE THE AMOUNT OF PRESSURE THAT WE CARRY ON OUR LINES. I BLAME YOUR RAILROAD COMMISSION SOME FOR MAKING US PUT SO MUCH PRESSURE ON THE RELIEF. THIS IS THE FIRST ACCIDENT ON TEXAS NATURAL GAS SYSTEM IN 75 YEARS OF BUSINESS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020050 | 2002-07-10 | SUPPLEMENTAL FINAL | 11680 |  | TXU GAS DISTRIBUTION | 1601 BRYAN | DALLAS | DALLAS | TX | 75201 | 1530 | 2002-05-20 | 2002 | DALLAS | DALLAS | TX | 75209 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | 3RD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 66213.6497 | 141933.6474 | 4000 | 3330.0971 | 96000 | 138603.5503 | 0 | 0 | NO | NO | NO | NO | 0 |  | 13 | 30 |  | 2002-05-20 | 320 | 364 | NO | YES | NO | NO | NO | NO | ELLEN WEAVER | 2145334602 | EWEAVER1@ONCORGROUP.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM |  |  |  |  | NO | NO | NO | [14 empty] | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 5 | 16 |  | ONE-CALL SYSTEM | YES | FLAGS |  | ACCURATE | YES
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020051 | 2002-07-08 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1155 | 2002-06-11 | 2002 | SUTTON | WORCESTER | MA | 01590 | MLV 265E-101.1 | 265E-101.1+0.00 | N 42 9' 11 | W 71 43' 10 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57500 | 37362.2411 | 83017.7515 | 0 | 0 | 24750 | 35733.7278 | 32750 | 47284.0237 | NO | YES | NO | YES | 2 | PRECAUTIONARY | 1 | 35 | 610144 | 2002-06-11 | 50 | 902 | YES | NO | NO | NO | NO | NO | LOUIS A SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | N/A- NO FAILURE OF COMPONENT | STEEL |  | NO | NO | NO | OTHER | PIPELINE BLOW-OFF ASSEMBLY | 1990 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | GAS IGNITED DURING DEPRESSURIZATION OF PIPELINE FOR CONSTRUCTION PROJECT. |  | THERE WAS AN IGNITION OF GAS DURING A GAS VENTING OPERATION FOR A PIPELINE CONSTRUCTION PROJECT. NO INJURIES OR SIGNIFICANT DAMAGE TO FACILITIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020052 | 2002-07-01 | ORIGINAL | 2196 |  | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | DUTCHESS | NY | 12601 | 920 | 2002-05-29 | 2002 | POUGHKEEPSIE | DUTCHESS | NY | 12601 | MP 101-TEST STATION | 1 | W 73 56.162' | N41 43.481' | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162000 | 108971.5703 | 226558.3386 | 12000 | 9990.2913 | 150000 | 216568.0473 | 0 | 0 | YES | NO | NO | YES | 180 | PRECAUTIONARY | 2 | 8 | 606963 | 2002-05-29 | 450 | 750 | NO | YES | NO | NO | NO | NO | DAVID W MERTZ | 8454865521 | DMERTZ@CENHUD.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 12 | 0.25 | API 5L | 31 | BUTT WELD | N/A | REPUBLIC STEEL | 1969 | UNDER GROUND |  | 156 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR |  |  | NO |  |  |  |  | NO | [40 empty] | BUFFALO DRILLING USING A 36" AUGER, DRILLED TO A DEPTH OF THIRTEEN FEET AND STRUCK THE 12" MP GAS TRANSMISSION LINE. BUFFALO DRILLING WAS PREPARING TO INSTALL A CONCRETE PILE TO SUPPORT A WATER PLANT SLUDGE DEWATERING TANK. NO CALL FOR A MARK OUT WAS MADE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20020053 | 2002-07-17 18:02 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | PO BOX 770000 | SAN FRANCISCO | SAN FRANCISCO | CA | 94177-0001 | 910 | 2002-06-11 | 2002 | FRESNO | FRESNO | CA | 93727 | 35.65 |  | 36.623611 | -119.835630 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 12 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 60000 | 51345.0767 | 62176.7105 | 40000 | 33300.9709 | 20000 | 28875.7396 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 5 | 610268 | 2002-06-11 | 625 | 650 | NO | NO | YES | NO | NO | NO | JEFF BORDERS | 4159735568 | JPB0@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 16 | 0.28 | API 5L-X42 | 42000 | ELECTRIC RESISTANCE WELD |  | UNKNOWN |  | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | AGRICULTURE OPERATIONS | NO |  |  |  |  | YES | STAKES | YES | ACCURATE | YES | [36 empty] | CONTRACTOR RIPPING BARREN TEN-ACRE PARCEL USING A 355 KOMATSU CRAWLER WITH A SING SIX-FOOT LONG RIPPING SHANK, DIAGONALLY CROSSED LINE 138, CAUSING THE LINE TO RUPTURE. COMPANY PIPELINE MARKERS CLEARLY IDENTIFIED THE PIPE. NOTE: CONTRACTOR DID NOT NOTIFIED THE CALIFORNIA ONE-CALL SYSTEM, HOWEVER THERE WERE PERMANENT LINE MARKERS VISIBLE AND PLACED CORRECTLY. IN ATTEMPTING TO SAVE THIS ON-LINE FORM, THE SYSTEM REQUIRES ENTRY FOR ITEMS F3.D.I, F3.D.II, F3.D.III, AND F3.D.IV. EVEN THOUGH, IN THIS INCIDENT, ITEMS F3.D.I AND F.3.D.IV DO NOT APPLY BECAUSE THERE WAS NO ONE-CALL NOTIFICATION GIVEN.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020054 | 2002-07-16 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY - PO BOX 58900 | SALT LAKE CITY | SALT LAKE | UT | 84158 | 1650 | 2002-07-05 | 2002 | DUTCH JOHN | DAGGETT | UT |  | MP 354.2 | 18701+76 | 1N & 2N | 23E SEC 21 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 0 | 615767 | 2002-07-05 | 567 | 809 | NO | NO | NO | NO | YES | NO | LARRY D OLSEN SR | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 26 | 0.28 | 5LX52 |  | WELD |  | CONSOLIDATED WEST | 1955 | UNDER GROUND |  | 48 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE LEAK OCCURRED AS THE RESULT OF A ROCK IMPINGING ON THE PIPE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020055 | 2002-07-16 | SUPPLEMENTAL | 22617 |  | SOUTHERN STAR CENTRAL GAS PIPELINE | 4700 HIGHWAY 56 | OWENSBORO | DAVIESS | KY | 42301 | 410 | 2002-06-23 | 2002 | HUTCHISON | RENO | KS | 67501 | 181 + 1175 | 9553+74 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63885 | 41784.5037 | 91695.3639 | 885 | 736.784 | 60000 | 86627.2189 | 3000 | 4331.3609 | NO | NO | NO | NO | 0 |  | 0 | 0 | 612709 | 2002-06-23 | 740 | 900 | NO | NO | YES | NO | NO | NO | DAVID SINCLAIR-PIPELINE SAFETY SPECIALIST | 2708524424 | DAVID.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 20 | 0.38 | 52000 | 1950 | EFW |  | A O SMITH | 1947 | UNDER GROUND |  | 66 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 6 | 10 | 2002 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | ON JUNE 6, 2002 LYONS DISTRICT RECEIVED A ONE CALL ON REPLACING A GAS LINE IN SEC 31,30 OF T 23S R 5 W OF RENO CO, KS FOR KANSAS GAS SERVICE BY BRB CONTRACTORS INC OF TOPEKA, KS. THIS WAS ON THE HUGOTON LINE ON THE WEST SIDE OF THE ARKANSAS RIVER AT HUTCHINSON, KANSAS. JOHN DUMOND RESPONDED TO THE ONE CALL (TICKET #204363). JOHN DUMOND MET JOHN KEENER WITH BRB CONTRACTORS OF TOPEKA, KS. JOHN DUMOND SPOTTED ALL THREE OF OUR LINES WHICH ALL RAN AT A DEPTH OF 63" TO 66". THE LINES WERE FLAGGED WITH YELLOW FLAGS THAT HAVE OUR NAME AND PHONE NUMBER ON THEM. JOHN DUMOND WROTE THE DEPTH OF EACH LINE ON THE FLAGS AT EACH LOCATION WHERE HE SPOTTED THE LINES WITH A LINE FINDER AND PROBED EACH LOCATION WITH A SPOTTING BAR. BRB IS THE GENERAL CONTRACTOR FOR KANSAS GAS SERVICE WHICH IS A DIVISION ON ONOEK. A&L UNDERGROUND IS A SUB-CONTRACTOR OF BRB CONTRACTORS INC DOING THE DIRECTIONAL BORE OF THE ARKANSAS RIVER. A&L UNDERGROUND AND BRB WERE ASKED TO EXPOSE OUR LINES TO THE BOTTOM OF EACH LINE WHERE WE COULD SEE THE DRILL STEM AND BITS WERE WELL BELOW OUR LINE. THEY SAID THAT THEY DIDN'T WANT TO DO THIS BECAUSE THEY WOULD LOSE THE CIRCULATION OF THEIR DRILLING MUD. THE DRILL STEM WORE A HOLE IN THE BOTTOM OF THE SOUTH 20" RIVER CROSSING. BILL WHITEHEAD WAS CALLED AT 4:10 AM SUNDAY MORNING JUNE 23, 2002, BY JOHN DUMOND, BILL CALLED OPERATIONS CONTROL ON HIS WAY TO THE LOCATION. A & L UNDERGROUND HAD CALLED JOHN. JOHN DUMOND HAD BEEN WITH BOTH CONTRACTORS WHEN THEY STARTED TO BORE THE RIVER CROSSING, AND REPEATEDLY ASSURED JOHN DUMOND THAT THEY WERE 10' BELOW OUR LINE. WHEN JOHN DUMOND AND BILL WHITEHEAD GOT TO THE SITE, THE BORING CREW HAD MOVED AWAY FROM THE BORING RIG AND WERE WAITING FOR THEM. JOHN AND BILL GOT THERE ALONG WITH KANSAS GAS SERVICE. OPERATIONS CONTROL WAS NOT SEEING ANY LOSS OF PRESSURE. AFTER THEY DETERMINED THAT IT WAS OUR LINE, THEY STARTED SHUTTING IT IN. DAN JASO AND MIKE HUGGANS WERE CALLED OUT TO HELP OPERATE THE GATES TO SHUT THE LINE SEGMENT IN. THE LINE HAD 740 PSIG ON IT AT THE TIME. THERE WAS NO FIRE, INJURIES, EMERGENCY PERSONNEL OR MEDIA INVOLVED WITH THE INCIDENT. THE LINE WAS ALLOWED TO BLOW DOWN THROUGH THE DAMAGED SPOT BECAUSE OF THE GROUND WATER THAT SHOWED UP WHEN THEY STARTED DIGGING THE LINE OUT TO INSPECT IT. BRB AND KANSAS AND KANSAS GAS SERVICE BROUGHT IN TRACK MOUNTED BACKHOES TO DIG THE DAMAGED LINE OUT. GROUND WATER BECAME A MAJOR PROBLEM WHILE EXPOSING THE DAMAGED LINE. BRB BROUGHT IN A 6" & 8" DITCH PUMPS WHICH ALLOWED US TO SEE THE LINE WITH THE DRILL STEM UNDER IT. WE WERE NOT ABLE TO INSTALL A CLAMP ON THE LINE UNTIL ABOUT MIDNIGHT SUNDAY NIGHT JUNE 23, 2002. A & L UNDERGROUND GOT THE DRILL STEM AND REAMER AWAY FROM OUR LINE AND WILLIAMS EMPLOYEES WERE ABLE TO INSTALL TWO BANDS CLAMPS TO KEEP THE WATER OUT OF THE LINE. WE KEPT ABOUT 10-20 PSIG ON THE LINE BECAUSE OF THE WATER UNTIL THE LINE WAS READY TO REPAIR. BRB WAS HANDLING THE EXCAVATING OF THE DAMAGED LINE AND PUMPING THE WATER ALONG WITH INSTALLATION OF SAND POINTS TO DRY THE HOLE UP ENOUGH SO WE COULD MAKE THE REPAIR. DUE TO PUMP PROBLEMS, THE PERMANENT LINE REPAIR WASN'T COMPLETED UNTIL WEDNESDAY JUNE 26 AT 9:00 AM. RONNIE YOUNG AND PETE GARCIA, WILLIAMS GAS PIPELINE COMPANY WELDERS, INSTALLED A FULL-ENCIRCLEMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020056 | 2002-07-17 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 850 | 2002-06-16 | 2002 | [6 empty] | 28-15'24 | 91-48'29 | OFFSHORE |  | EUGENE ISLAND | 333 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240000 | 156147.5694 | 346111.555 | 650 | 541.1408 | 239350 | 345570.4142 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 611146 | 2002-06-16 | 925 | 1440 | YES | NO | NO | NO | NO | NO | C W TILL | 3374754226 | BWTILL@CMSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1976 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | US STEEL | 1976 | UNDER WATER |  | 96 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1976 | NO | [57 empty] | DIVING CONTRACTOR MOBILIZED TO INVESTIGATE BUBBLES AND POSSIBLE SHEEN ON THE WATER. NO SHEEN WAS FOUND, BUT BUBBLES WERE EVIDENT. THE INVESTIGATION REVELAED THAT THE BUBBLES WERE COMING FROM TWO SOURCES LOCATED APPROXIMATELY 20 FEET APART. THE FIRST LOCATION REVEALED LEAKING SEALS ON BOLT-ON REPAIR CLAMP INSTALLED IN 1991. THE SECOND LOCATION REVEALED TWO PINHOLE LEAKS, WHICH WERE TWO INCHES APART. TWO NEW BOLT-ON REPAIR CLAMPS WERE INSTALLED. THE LATERAL WAS BATCH TREATED WITH BIOCIDES AND CONTINUOUS INJECTION CORROSION INHIBITOR EQUIPMENT WAS INSTALLED. PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020057 | 2002-07-26 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1045 | 2002-07-02 | 2002 | COLORADO SPRINGS | EL PASO | CO |  | LINE 9A | 2528+89 |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52000 | 46764.7714 | 49403.8892 | 42000 | 34966.0194 | 10000 | 14437.8698 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 15 | 615371 | 2002-07-02 | 450 | 614 | NO | NO | NO | NO | YES | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 20 | 0.22 | 5L | 52000 | FLASH WELD |  | A O SMITH | 1963 | UNDER GROUND |  | 50 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | CONTRACTOR STRUCK THE 9A PIPELINE WHILE EXCAVATING NEAR THE PIPELINE, AND CAUSED THE DAMAGE, RESULTING IN A LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020058 | 2002-07-26 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1400 | 2002-06-28 | 2002 |  |  | AL |  | 58.600 | 2891+8 | X 2,923,795 | Y 10,027,281 | OFFSHORE |  | VIOSKA KNOLL | 82 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500500 | 325368.4222 | 722309.7533 | 500 | 416.2621 | 500000 | 721893.4911 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 614295 | 2002-06-28 | 1500 | 2180 | NO | YES | NO | NO | NO | NO | B R LANDES | 7132152001 | BILL.R.LANDES@WILLIAMS.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2001 | 36 | 1.25 | API 5L | 65000 | DSA | 36 | EQUIP VALVE & SUPPLY | 2001 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | YES | 3 | 2 | 2002 | WATER |  | 8 | 3441 | [12 empty] | DURING A RECENT DIVE BY AN OFFSHORE CONTRACTOR DISENGAGING THE LOCKED OPEN MECHANISM ON THE CHECK VALVE IN 95 FEET OF WATER A LEAK WAS LOCATED. IT WAS DETERMINED THAT THE PLUG WAS NOT PROPERLY TIGHTENED OR WAS CROSSTHREADED. THE DIVER WAS ABLE TO CONDUCT THE INTENT OF THE DIVE WITH THE ROV BUT DID NOT ATTEMPT ANY REMEDIATION ON THE LEAK FOR SAFETY PURPOSES. THE LEAK IS OF VERY SMALL MAGNITUDE AND FROM THE DIVER'S DESCRIPTION THE BUBBLES ARE DISSIPATING WITHIN THE WATER COLUMN AT ABOUT 25 FEET. WE ARE IN THE PROCESS OF EVALUATING THE SITUATION AND PLANNING A REPAIR PROCEDURE AND DATE. A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN REPAIR IS MADE. SUPPLEMENTAL REPORT: ON NOVEMBER 13, 2002, THE MINOR PIPELINE LEAK WAS RESOLVED BY TIGHTENING THE PLUG AND REPRESSURING THE LINE AND OBSERVING NO FURTHER LEAKAGE. SUSSEQUENTLY, ALL PIPELINE VALVES WERE RETURNED TO THEIR NORMAL OPERATIONAL POSITIONS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020059 | 2002-08-01 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 2603 AUGUSTA | HOUSTON | HARRIS | TX | 77057 | 1045 | 2002-06-28 | 2002 |  | EAST CARROLL | LA |  | MP 44 VALVE 811 | 2284+80 | 32 56 18.72 | -91 06 30.44 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 110302.9851 | 232112.225 | 10000 | 8325.2427 | 150000 | 216568.0473 | 5000 | 7218.9349 | NO | NO | NO | NO | 0 |  | 8 | 30 | 614360 | 2002-06-28 | 780 | 1008 | YES | NO | NO | NO | NO | NO | HENRY WANG, CODES AND STANDARDS, MODIFIED BY MARY FRIEND | 7132674371 | HWANG@NISOURCE.COM, MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 30 | 0.44 | X60 | 60000 | DSAW |  | KAISER STEEL | 1968 | UNDER GROUND |  | 90 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | LIQUID/SLUDGE | YES | 1968 | NO | [57 empty] | FOUND LIQUID/SLUDGE ON BOTTOM OF PIPE WHERE LEAK OCCURRED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020061 | 2002-07-26 | ORIGINAL | 31650 |  | GREKA ENERGY | 2801 B SANTA MARIA WAY | SANTA MARIA | SANTA BARBARA | CA | 93455 | 1130 | 2002-07-08 | 2002 | SANTA MARIA |  | CA | 93455 | SUEY JUNCTION |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | BACKHOE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 | COMPANY POLICY | 0 | 0 | 616254 | 2002-07-10 | 70 | 200 | NO | NO | NO | NO | NO | NO | FRANK SMITH | 8053478700 | FWS@GREKAENERGY.COM | TRANSMISSION | OTHER | 1 | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 6 | 0.2 | X42 |  | X-TRU COAT |  |  |  | OPEN DITCH |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | PIPELINE |  | YES |  |  |  | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | A BACKHOE REMOVING UNOCAL'S 12" PIPELINE WEST OF GREKA ENERGY'S SUEY JUNCTION VALVE BOX BROKE A 1" LINE COMING OFF GREKA'S 6" GAS PIPELINE. THIS 1" LINE WAS UNKNOWN BOTH TO GREKA AND UNOCAL. THIS LINE LOOKED LIKE IT HAD BEEN HOT-TOPPED FOR FUEL WITHOU ANY APPROVALS. GREKA WAS NOTIFIED BY THE WORK CREW WHEN THE LINE BROKE AND GREKA SHUT DOWN ITS COMPRESSOR SO A PLUG COULD BE INSTALLED. IT TOOK ABOUT 2 HOURS TO ACCOMPLISH THE REPAIRS AND THE COMPRESSOR WAS TURNED BACK ON.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020062 | 2002-08-19 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1210 | 2002-07-28 | 2002 | FLORENCE | PINAL | AZ | 85232 | MP 18+ | 992+35.30 | 33.06251 | 111.43598 | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16000 | 11508.7048 | 20900.046 | 3600 | 2997.0874 | 12400 | 17902.9586 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 15 | 618110 | 2002-07-28 | 400 | 475 | NO | NO | YES | NO | NO | NO | LOUIS A SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1936 | 6 | 0.15 |  | 24000 | ERW |  | REPUBLIC | 1936 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | RAILROAD |  | NO |  |  |  |  | YES |  | YES | ACCURATE | YES | [36 empty] | AT APPROXIMATELY 12:10 PM, MST, A COPPER BASIN RAILROAD FRONT END LOADER WAS IN THE PROCESS OF INSTALLING A 48" CULVERT SECTION WHEN IF STRUCK A 6" EL PASO NATURAL GAS PIPELINE (LINE 2026), BETWEEN MP 18 & MP 19, SEVERING IT. AN EPNG CREW RESPONDED AND SHUT INVALVES 2 & 3. THERE WERE NO INJURIES OR FIRE REPORTED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020064 | 2002-08-23 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1100 | 2002-07-24 | 2002 |  |  | LA |  | SV 509A-401 | 0+00 | N 2828.680 | W 9238.070 | OFFSHORE |  | EAST CAMERON | 271 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238000 | 157736.7869 | 337508.6747 | 10000 | 8325.2427 | 228000 | 329183.432 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 617692 | 2002-07-24 | 1200 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 16 | 0.38 |  | 52000 | SMLS |  | U S S | 1973 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1973 | NO | [57 empty] | THERE WAS A LEAK ON TGP LINE 509A-400, AT SV 509A-401, IN EAST CAMERON BLOCK 271, GULF OF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS DUE TO INTERNAL CORROSION. THE LEAK WAS REPAIRED BY INSTALLING A 16" PLIDCO REPAIR CLAMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020065 | 2002-08-23 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1515 | 2002-07-23 | 2002 |  |  | LA |  | MP 523Q-102+17.83 | 941+36 | 28DEG 34' 56.2 | 91DEG 14' 0 | OFFSHORE |  | SHIP SHOAL | 197 |  | YES | NO | INTERSTATE | OTHER | LEAK AT REPAIR CLAMP ON BODY BLEED VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 56775.9378 | 119665.5799 | 5000 | 4162.6214 | 80000 | 115502.9586 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 617605 | 2002-07-23 | 990 | 1200 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | LEAK AT DAMAGED REPAIR CLAMP | STEEL |  | NO | NO | NO | PIPELINE |  | 1997 | 36 | 0.6 |  | 60000 | DSAW |  |  | 1978 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE LEAK OCCURRED ON TGP LINE 523Q-100, NEAR SV 523Q-102 + 17.83, IN SHIP SHOAL BLOCK 197, GULF OF MEXICO. THE SMALL LEAK WAS DUE TO 1/2" BODY BLEED VALVE ON CLAMP INSTALLED IN 1997, AND APPARENTLY DAMAGED BY A SHRIMPER'S NET.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020066 | 2002-08-23 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1715 | 2002-07-24 | 2002 | GULF OF MEXICO |  | LA |  | MP 2.88 | 152 + 80 | 28 DEG 47' 27.6 | 91 DEG 43' 42.0 | OFFSHORE |  | EUGENE ISLAND | 175 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 56775.9378 | 119665.5799 | 5000 | 4162.6214 | 80000 | 115502.9586 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 617750 | 2002-07-24 | 1125 | 1300 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 10 | 0.34 |  | 46000 | ERW |  | AMERICAN STEEL | 1967 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | UNDETERMINED | OTHER | UNDETERMINED | YES | 1967 | NO | [57 empty] | THE LEAK OCCURRED ON ANR 10" LINE 736-32, REPORTED BY BRITISH PETROLEUM IN EUGENE ISLAND BLK. 158, GULF OF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS DUE TO A PINHOLE ON THE PIPE, CAUSED BY INTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020068 | 2002-08-27 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1320 | 2002-07-28 | 2002 |  |  | LA |  | SV 507F-1001 | 0+00 | 29 24' 36 | 92 53' 75 | OFFSHORE |  | EAST CAMERON | 49 CG |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153000 | 100342.9296 | 219065.6202 | 3000 | 2497.5728 | 150000 | 216568.0473 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 5 | 618120 | 2002-07-28 | 490 | 1310 | NO | NO | YES | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 |  | 42000 | SMLS | 12 | NORDSTROM | 1958 | OTHER | ON PLATFORM |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1972 | NO | [57 empty] | THE LEAK OCCURRED ON TGP LINE 507F-1000, AT SV 507F-1001, ON THE CENTRAL GATHERING PLATFORM, EAST CAMERON BLOCK 49, GULF OF MEXICO. THE LEAK WAS DUE TO GAS ESCAPING AROUND A NORDSTROM PLUG VALVE, THAT HAD BEEN DAMAGED BY INTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020069 | 2002-09-05 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACCORKLE AVENUE | CHARLESTON | KANAWHA | WV | 25314 | 2315 | 2002-08-05 | 2002 | CHARLESTON | PUTNAM | WV | 25312 |  | 3019+10 | 38 34' 26 | 81 13' 10 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2168040 | 1593824.1792 | 2764017.115 | 599040 | 498715.3398 | 1545000 | 2230650.8876 | 24000 | 34650.8876 | YES | NO | YES | YES | 0 | PRECAUTIONARY | 1 | 30 | 619048 | 2002-08-06 | 748 | 936 | NO | YES | NO | NO | NO | NO | CHRIS LEGG | 3043573227 | CLEGG@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 30 | 0.3 | API 5L-X65 | 65000 | ELECTRIC FUSION WELDED |  | REBUBLIC |  | UNDER GROUND |  | 120 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | AT APPROXIMATELY 11:15 P.M. ON AUGUST 5, 2002, COLUMBIA GAS TRANSMISSION CORPORATION'S (COLUMBIA) PIPELINE SM-80 LOOP (30") RUPTURED AND IGNITED.THE PIPELINE WAS OPERATING AT 748 PSIG AT THE TIME OF THE RUPTURE.COLUMBIA'S GAS CONTROL IMMEDIATELY WAS AWARE OF THE RUPTURE DUE TO THE RAPID DROP IN PRESSURE AND COLUMBIA FIELD EMPLOYEES SAW THE FLAMES FROM A COMPRESOR STATION APPROXIMATELY ONE MILE AWAY. THE RUPTURE OCCURRED IN A RURAL AREA NEAR THE COMMUNITY OF LANHAM, WV IN PUTNAM COUNTY. NO DEATHS OR INJURIES RESULTED FROM THE INCIDENT.THE NEAREST RESIDENTIAL DWELLING WAS APPROXIMATELY 500 YARDS AWAY AND UNDAMAGED. COLUMBIA QUICKLY RESPONDED BY CLOSING VALVES ON EITHER SIDE OF THE RUPTURE TO STOP THE FLOW OF GAS TO THE DAMAGED PORTION OF PIPELINE. BY 12:45 A.M., THE LINE WAS ISOLATED AND THE FLAMES QUICKLY DIMINISHED. THE CAUSE OF THE RUPTURE IS STILL UNDER INVESTIGATION, HOWEVER, PRELIMINARY INDICATIONS ARE THAT EXTERNAL STRESS, IN PARTICULAR THE WEIGHT OF A HILLSIDE SLIP, MAY HAVE LED TO THE RUPTURE. BASED ON THE PRELIMINARY FINDINGS, COLUMBIA AND THE US DEPARTMENT OF TRANSPORTATION'S OFFICE OF PIPELINE SAFETY HAVE JOINTLY DEVELOPED A PLAN OF ACTIONS COLUMBIA WILL TAKE TO SAFELY RESTORE SERVICE TO THE PIPELINE. THE PIPELINE REMAINS OUT OF SERVICE UNTIL THIS PLAN IS FULLY IMPLEMENTED. FINAL INVESTIGATION AND REPORTING INFORMATION WAS FILED WITH THE OPS EASTERN REGION OFFICE. ROOT CAUSE ANALYSIS INDICATES THAT THIS FAILURE WAS DUE TO SLOPE INSTABILITY, WHICH CREATED HIGH AXIAL STRESSES AT THE FAILURE ORIGIN AND PRODUCED BUCKLING NEAR THE ORIGIN OF FAILURE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020070 | 2002-09-05 | SUPPLEMENTAL FINAL | 18536 |  | SOUTHWEST GAS CORP | P O OX 98512 | LAS VEGAS | CLARK | NV | 89147 | 834 | 2002-08-06 | 2002 | HENDERSON | CLARK | NV | 89014 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171360 | 111846.4911 | 246417.0917 | 1620 | 1348.6893 | 169740 | 245068.4024 | 0 | 0 | YES | NO | NO | YES | 20 | PRECAUTIONARY | 5 | 29 | 619105 | 2002-08-06 | 288 | 300 | NO | YES | NO | NO | NO | NO | JOEL MARTELL | 7022212102 | JOEL.MARTELL@SWGAS.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.25 | API-5L | 24000 | ERW |  | KAISER STEEL COMPANY | 1956 | UNDER GROUND |  | 72 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DRILLING | YES | 6 | 26 | 2006 | ONE-CALL SYSTEM | YES | PAINT | YES | ACCURATE | YES | [36 empty] | ALLEN DRILLING, INC. WAS DRILLING POSTHOLES TO INSTALL NETTING SUPPORTS BETWEEN AN EXISTING GOLF COURSE AND AN APARTMENT COMPLEX. WHILE DRILLING FOR ONE OF THE POSTHOLES THE DRILL OPERATOR STRUCK AND PUNCTURED A 16" STEEL GAS TRANSMISSION LINE RESULTING IN A 1-INCH DIAMETER HOLE. IN ORDER TO CONTROL THE FLOW OF GAS AND MAKE REPAIRS A SECTION OF TRANSMISSION LINE WAS ISOLATED. ONCE THE REPAIRS WERE MADE THE LINE WAS PLACED BACK IN SERVICE. THE CONTRACTOR HAD A CURRENT USA ONE-CALL TICKET, HOWEVER, THE CONTRACTOR APPEARED TO BE OUTSIDE OF THE SPECIFIED WORK AREA. THERE WERE VISIBLE PERMANENT LINE MARKERS IN THE VICINITY OF THE WORK AREA, HOWEVER, THEY WERE NOT DIRECTLY OVER THE PIPELINE. THERE WAS APPROXIMATELY 5,600 CUSTOMER OUTAGES, NO IGNITION OF GAS OR INJURIES AS A RESULT OF THE INCIDENT. (ATTEMPTED TO OBTAIN LATITUDE AND LONGITUDE FROM THE RSPA NATIONAL PIPELINE MAPPING SYSTEM BUT WAS UNABLE AT THIS TIME DUE TO SECURITY CONCERNS)
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020071 | 2002-09-03 | SUPPLEMENTAL FINAL | 1007 |  | K N INTERSTATE GAS TRANSMISSION CO | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228 | 640 | 2002-07-22 | 2002 | LODGEPOLE | CHEYENNE | NE | 69149 |  | 723+26 | 41:02:51 | 102:43:50 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84683 | 73928.2442 | 84865.3266 | 61183 | 50936.3325 | 20000 | 28875.7396 | 3500 | 5053.2544 | NO | NO | YES | NO | 0 |  | 2 | 0 | 617420 | 2002-07-22 | 720 | 810 | NO | NO | NO | NO | YES | NO | JAMES PHILLIPS | 3039147753 | JIM_PHILLIPS@KINDERMORGAN.COM | TRANSMISSION | OTHER | INLINE DRIP UNDERNEATH PIPELINE | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 12 | 0.25 | API-5L | 42000 | ERW |  | YOUNGSTOWN PIPE | 1954 | UNDER GROUND |  | 42 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1955 | NO | [57 empty] | PREFERENTIAL CORROSION ON INTERIOR ERW SEAM WELD INITATED RUPTURE OF INLINE DRIP BELOW TRANSMISSION PIPELINE.INSTANTANEOUS RELEASE OF GAS WAS IGNITED PROBABLY BY OVERHEAD RURAL ELECTRIC POWER LINES. LOCAL FIRE DEPARTMET RESPONDED IMMEDIATELY TO THE EMERGENCY CALL AND BLOCKED ALL RURAL ROADS IN THE IMMEDIATE AREA. KMIGT PERSONNEL RESPONDED IMMEDIATELY AND ISOLATED PIPELINE SECTION FROM NATURAL GAS SOURCES. FIRE BURNED FARM CROPS IN VICINITY OF RUPTURE ALONG WITH THE POWER POLE AND SOME ELECTRIC POWER LINES. RURAL POWER COMPANY RESTORED SERVICE WITHIN A FEW DAYS. SAMPLES OF THE FAILED MATERIAL WERE SENT FOR EVLAUATION TO A METALLUGIST AT E N ENGINEERING IN CHICAGO, IL. ADDITIONAL MITIGATION IS BEING CONDUCTED IN ACCORDANCE WITH THE PLAN FILED WITH THE OPS CENTRAL REGION OFFICE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020072 | 2002-09-10 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1420 | 2002-08-19 | 2002 | GULF OF MEXICO |  | LA |  | MP 0+.057 |  | 29 DEG 14' 31.9 | 88 DEG 55' 37.0 | OFFSHORE |  | MAIN PASS | 72 |  | YES | NO | INTERSTATE | OTHER | CHECK VALVE LEAKED | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 63273.7189 | 134103.4498 | 5000 | 4162.6214 | 90000 | 129940.8284 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 620395 | 2002-08-19 | 1074 | 1728 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 6 | 0.43 |  | 42000 |  | 6 |  | 1980 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | O-RING | [7 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 1 | 1 | 1980 | WATER |  | 8 | 2160 | [12 empty] | THE LEAK OCCURRED ON A 6" KOCH LINE, OPERATED BY SNG IN MAIN PASS BLK. 72, GULF OF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS DUE TO THE O-RING FAILURE IN THE SUB-SEA CHECK VALVE, LOCATED NEAR THE BASE OF THE PLATFORM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020073 | 2002-09-16 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1230 | 2002-08-21 | 2002 | [6 empty] | 28-26.07' | 91-02.07' | OFFSHORE |  | SHIP SHOAL | 241 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137100 | 89137.1016 | 197839.2806 | 170 | 141.5291 | 136930 | 197697.7515 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 620682 | 2002-08-22 | 841 | 1202 | NO | YES | NO | NO | NO | NO | C W BUTCH TILL | 3374754226 | BWTILL@CMSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 8 | 0.34 | API 5LX | 52000 | SMLS |  | YOUNGSTOWN | 1968 | UNDER WATER |  | 96 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1972 | NO | [57 empty] | BUBBLES ON THE SURFACE WERE OBSERVED BY THE PLATFORM OPERATOR AND REPORTED TO TRUNKLINE. LATERAL SUPPLIES FUEL GAS TO THE PLATFORM AND OPERATES UNDER LOW FLOW CONDITIONS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020074 | 2002-09-13 | SUPPLEMENTAL FINAL | 12127 |  | MARATHON ASHLAND PIPE LINE LLC | 539 SOUTH MAIN STREET | FINDLAY | HANCOCK | OH | 45840 | 945 | 2002-08-20 | 2002 | CENTERVILLE | ST MARY | LA | 70522 | GARDEN CITY STATION |  | 29.7324 | 91.4437 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK AT Q WELD-O-LET | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120090 | 78059.6592 | 173329.3651 | 90 | 74.9272 | 120000 | 173254.4379 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 10 | 620803 | 2002-08-23 | 1010 | 1300 | YES | NO | NO | NO | NO | NO | TAD SCHELL | 4194213201 | TASCHELL@MAPLLC.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1997 | 24 | 0.63 | API 5L | 65000 | DSAW |  | BERG/NAPA | 1995 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FATIGUE FAILURE OF WELD DUE TO CYCLICAL LOADINGS |  | AT 09:45 A.M. ON AUGUST 20 THE NAUTILUS- OPERATIONS TECHNICIAN NOTICED GAS SEEPING FROM THE BASE OF A 2" WELD-O-LET IN NAUTILUS GARDEN CITY MANIFOLD ON THE 24" PIPING TO THE EXXON GAS PLANT. THE GAS FLOW TO EXXON WAS IMMEDIATELY SHUTDOWN. THE AFFECTED PIPING WAS ISOLATED (DOUBLE-BLOCKED IN BY CLOSING TWO UPSTREAM VALVES AND TWO DOWNSTREAM VALVES) AND THE AFFECTED LINE SECTION (APPROXIMATELY 60 FOOT LINE) WAS BLOWN DOWN. GAS DELIVERY TO THE ADJACENT NEPTUNE PLANT WAS ABLE TO CONTINUE SAFELY. NO PUBLIC OR ENVIRONMENTAL EXPOSURE WAS CAUSED BY THIS INCIDENT. THE 2" WELD-O-LET WAS LOCATED IN THE NAUTILUS MANIFOLD DOWNSTREAM OF THE EXXON ORIFICE METERS AND IMMEDIATELY UPSTREAM OF THE EXXON CONTROL VALVE (FV 3030). THE 2" WELD-O-LET WAS USED FOR A SAMPLE POINT AND WAS ONE OF THREE 2" WELD-O-LETS ON A 4 FT. LONG 24 IN DIAMETER JOINT OF PIPE. WET MAGNETIC PARTICLE TESTING CONFIRMED THAT THERE IS A CRACK IN THE PARENT PIPE EXTENDING ABOUT 2" ALONG THE PIPE AXIS TO EITHER SIDE OF THE FILLET WELD. THE ROOT CAUSE OF THE CRACK IS UNDETERMINED AT THIS TIME. THE SPECIMEN CONTAINING THE CRACK HAS BEEN SENT TO KIEFNER & ASSOCIATES IN COLUMBUS, OHIO FOR FAILURE ANALYSIS. AT THE TIME OF THE RELEASE, IT WAS BELIEVED THAT REPAIR COSTS WOULD BE LESS THAN $50,000. A DETERMINATION WAS MADE ON AUGUST 23, 2002 THAT REPAIR COSTS WOULD EXCEED $50,000 AND THE NRC WAS NOTIFIED. 4-18-03 LABORATORY ANALYSIS OF THE FAILED SPECIMEN INDICATED THAT THE FAILURE WAS DUE TO FATIGUE CRACKING FROM VIBRATION LOADINGS. THE CRACK INITIATED AT TOE OF FILLET WELD AT A SHARP CORNER BETWEEN THE FIRST PASS OF THE WELDMENT AND THE CARRIER PIPE BODY. KIEFNER AND ASSOCIATES WAS CONSULTED CONCERNING THE CAUSE CLASSIFICATION OF THIS EVENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020075 | 2002-09-19 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1000 | 2002-08-23 | 2002 |  |  |  |  | 0.53 | 27+98 | 2943.40W | 8832.96N | OFFSHORE |  | CHANDELEUR | 34 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237970 | 159847.5711 | 333250.7047 | 16895 | 14065.4976 | 221075 | 319185.2071 | 0 | 0 | NO | NO | NO | NO | 0 |  | 70 | 0 | 620918 | 2002-08-24 | 960 | 1000 | NO | YES | NO | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1988 | 16 | 0.44 | API-5LX | 52000 | DSAW | N/A | NAPA | 1988 | UNDER WATER |  | 120 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL CORROSION | OTHER | INTERNAL -UNKNOWN | YES | 1988 | NO | [57 empty] | THE CAUSE OF THE LEAK (INCIDENT) WAS APPARENT INTERNAL CORROSION. SUPPLEMENTAL REPORT WILL BE PROVIDED WHEN COSTS ARE MORE PRECISELY DETERMINED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020076 | 2002-10-08 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1400 | 2002-09-09 | 2002 | SHELBYVILLE | SHELBY | IN |  | MP 750.5 |  | 39.5990750 | -85.7751350 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LONG SEAM WELD CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131000 | 111691.4711 | 136567.5016 | 86000 | 71597.0874 | 45000 | 64970.4142 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 622411 | 2002-09-09 | 760 | 858 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 30 | 0.34 |  | 52000 | EW |  | A O SMITH | 1956 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | FLASH WELD |  | MATERIAL DEFECT |  | NO | YES | 7 | 8 | 1977 | WATER |  | 8 | 1208 | [12 empty] | A SMALL LEAK WAS DISCOVERED FOLLOWING AN AERIAL PATROL OVER AN AREA OF DEAD VEGETATION. UPON FURTHER INVESTIGATION, A NON-FUSION CRACK 1/4" LONG IN THE LONGITUDINAL SEAM WAS FOUND.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20020077 | 2002-10-11 | SUPPLEMENTAL FINAL | 4904 |  | EXXON CO USA - NEW ORLEANS PRODUCTION ORGANIZATION | 396, WEST GREENS ROAD | HOUSTON | HARRIS | TX | 77060 |  | 2002-10-03 | 2002 |  |  | LA |  |  |  | 29 08' 51.5 | -89 54' 02.0 | OFFSHORE |  | GRAND ISLE | 6 | LA | YES | NO | INTERSTATE | OTHER | CIRCUMFERNENTIAL AXIS/180 AT BOTH LEAK LOCATIONS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 194933.432 | 433136.0947 | 0 | 0 | 300000 | 433136.0947 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 625320 | 2002-10-08 | 900 | 1357 | NO | NO | NO | NO | NO | NO | JOHN J. LANE III, REGULATORY SPECIALIST | 2816541101 | JOHN.J.LANE@EXXONMOBIL.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6 | 0.31 | GRADE B |  | SEAMLESS |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE LILI | [51 empty] | TWO SECTION WERE DAMAGED DURING HURRICANE LILI BY CONTACT WITH AN ANCHOR OR OTHER DEBRIS. CAL DIVE INTERNATIONAL, INC. REPAIR PROCEDURE CALLED FOR EACH DAMAGE SECTION TO BE REPAIRED BY 1) LIFTING TO SURFACE, 2) CUTTING OUT SECTION, 3) WELDING ON FLANGES, 4) X-RAY OF WELDS, 5) INSTALLATION OF PRE-FABRICATED SPOOLS, 6) LOWERING AND 7) BURYING WITH THREE FEET OF COVER. REPAIR PROCEDURES APPROVED BY THE MMS ON 10/25=8/02 CALLED FOR REPAIR SPOOLS TO BE CONSTRUCTED OF API 5L GRADE B MATERIAL WITH A WALL THICKNESS OF .432 INCHES. PIPE FLANGES SPECIFIED TO BE 2200 PSIG FOR FOUR HOURS IN ACCORDANCE WITH ASME B.31.8 AND 49 CFR 192. FIELD WELDS WERE SPECIFIED TO BE 100% RADIOGRAPHED USING API 1104 ACCEPTANCE CRITERIA. PIPELINE WAS SUBSEQUENTLY LEAK TESTED AND IS CURRENTLY IN OPERATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020078 | 2002-10-03 | ORIGINAL FINAL | 11680 |  | TXU LONE STAR PIPELINE | 301 SOUTH HARWOOD STREET | DALLAS | DALLAS | TX | 75201 | 1630 | 2002-08-30 | 2002 | MIDLAND | MIDLAND | TX | 79701 | 16770+42 |  | 42'55 | 102 08'93 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98000 | 83915.1186 | 101453.4167 | 65500 | 54530.3398 | 32500 | 46923.0769 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 622580 | 2002-08-30 | 600 | 960 | YES | NO | NO | NO | NO | NO | ZORA RAOUFPOUR | 2148753889 | ZRAOUFP1@ONCORGROUP.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | [5 empty] | 2 | GROVE | 1972 | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | CONSTRUCTION DEFECT | PROCEDURE NOT FOLLOWED | NO | YES | 12 | 28 | 1972 | WATER |  | 8 | 1200 | [12 empty] | WELD TO VALVE FAILED DUE TO EXCESSIVE STRESSES. IN ORDER TO REPAIR THE FAILURE, 12.12 MILES OF 36" PIPELINE WAS VENTED TO ATMOSPHERE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020079 | 2002-10-18 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 820 | 2002-09-23 | 2002 | ANNISTON | CALHOUN | AL |  | 0.00 | 0+00 | 33 DEG 36'56.7 | 85 DEG. 47'11.2 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK DUE TO CRACK IN BODY OF 4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27500 | 22503.2943 | 30535.2014 | 15000 | 12487.8641 | 12500 | 18047.3373 | 0 | 0 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 1 | 0 | 623705 | 2002-09-23 | 436 | 500 | NO | NO | YES | NO | NO | NO | LOUIS A SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | [5 empty] | 4 IN CRANE 250S CHECK | CRANE | 1948 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | LEAK DISCOVERED ON ANNISTON #2 METER STATION TAP LINE, MP 0.00 (OFF OF 24" NORTH MAIN LOOP LINE AT MP 380.149). UPON INVESTIGATION,IT WAS DISCOVERED THAT THE 4" CHECK VALVE ON THE DOWNSTREAM SIDE OF THE TAP VALVE #2 HAD AN 8" LONG CRACK IN THE BODY OF THE VALVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020080 | 2002-10-17 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET #1000 | HOUSTON | HARRIS | TX | 77002 | 1400 | 2002-08-27 | 2002 | SHOREWOOD | WILL | IL | 60431 |  | 63612+00 | N41 30.446' | W88 11.285' | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 82916.7289 | 163474.2345 | 16000 | 13320.3883 | 101500 | 146544.3787 | 2500 | 3609.4675 | YES | NO | NO | NO | 0 |  | 1 | 30 | 621211 | 2002-08-27 | 395 | 596 | YES | NO | NO | NO | NO | NO | REBECCA VOSS FIELDS | 7133699418 | RBECCA_FIELDS@KINDERMOGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 30 | 0.34 | 5LX | 52000 | ERW |  |  |  | UNDER GROUND |  | 42 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | BACTERIAL CORROSION | NO |  | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020081 | 2002-10-17 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO (ENRON) | PO BOX 1188 | HOUSTON | HARRIS | TX | 77251 | 1425 | 2002-09-20 | 2002 | CITRONELLE | MOBILE | AL |  | MP 168.1 | 2071+94 | 31.033 N | 88.378 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160215 | 147173.1895 | 146106.3095 | 139400 | 116053.8835 | 20815 | 30052.426 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 623568 | 2002-09-20 | 815 | 975 | NO | NO | NO | NO | YES | NO | MERLIN MOSEMAN | 7133451625 | MERLIN.MOSEMAN@ENRON.COM | TRANSMISSION | OTHER | FILLET WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 2002 | 30 | 0.34 | API-5LX | 60000 | DSA |  |  |  | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | HOT TAP |  |  |  | MATERIAL DEFECT |  | NO | NO | [19 empty] | LEAK RESULTED FROM A CRACK IN A FILLET WELD DUE TO SUSPECTED SETTLEMENT OF HOT TAP CONNECTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020083 | 2002-11-04 | SUPPLEMENTAL FINAL | 1734 |  | BRIDGELINE GAS DISTRIBUTION LLC | 2811 HAYES ROAD | HOUSTON | HARRIS | TX | 77082 | 1310 | 2002-10-08 | 2002 | RESERVE | ST. JOHN THE BAPTIST | LA | 70068 | 14.6 | 721+48.69 | N3006.626 | W9032.030 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113453 | 76663.0441 | 157977.8534 | 9528 | 7932.2913 | 103925 | 150045.5621 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 | 0 | 626267 | 2002-10-15 | 700 | 1000 | NO | YES | NO | NO | NO | NO | HENRY L. LEGER | 3376548915 | HENRYLEGER@CHEVRONTEXACO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 20 | 0.34 | API 5 LX | 52000 | ERW | N/A | UNKNOWN |  | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | HF ERW |  | MATERIAL DEFECT |  | NO | YES | 12 | 10 | 1962 | WATER |  | 24 | 1250 | [12 empty] | THE CAUSE OF THE SUBJECT INCIDENT WAS DUE TO A SEAM FAILURE IN A JOINT OF 20-INCH PIPE LOCATED AT MILE POST 14.6 (STATION FOOTAGE 721+48.69) ON BRIDGELINE GAS DISTRIBUTION LLC'S RIVERLANDS PIPELINE SYSTEM. THE SUBJECT PIPELINE WAS INSTALLED IN CY 1962 AND WAS CONSTRUCTED WITH ERW PIPE. THE SEAM FAILURE WAS BARELY VISIBLE TO THE NAKED EYE. THE LEAK WAS CLASSIFIED AS A PINHOLE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020084 | 2002-10-28 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 730 | 2002-10-01 | 2002 | CUNNINGHAM | PRATT | KS | 67124 | WELL SITE WELL #36-12 |  | N37 39.569' | W98 28.928' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308000 | 210327.3288 | 424514.7211 | 33000 | 27473.301 | 0 | 0 | 275000 | 397041.4201 | NO | NO | NO | NO | 0 |  | 0 | 11 | 624452 | 2002-10-01 | 1460 | 1600 | YES | NO | NO | NO | NO | NO | PAT VAUGHAN | 4023987185 | PAT.VAUGHAN@DYNEGY.COM | TRANSMISSION | OTHER | DRIP BARREL | STEEL |  | NO | NO | NO | OTHER | STORAGE WELL METER | 1979 | 20 | 0.63 | API-5LX | 52000 | DSAW |  |  |  | INSIDE/UNDER BUILDING |  | 84 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1979 | NO | [57 empty] | GAS RELEASE OCCURRED WHEN THE METER RUN DRIP AT STORAGE WELL #36-12 RUPTURED. APPARENT CAUSE OF THE RUPTURE IS INTERNAL CORROSION ON THE BOTTOM OF THE 20 INCH DIAMETER DRIP BARREL. THE DRIP BARREL WAS CONSTRUCTED OF PIPE AND FITTINGS. THE FAILED PIPE SEGMENT WAS APPROXIMATELY 10 FEET LONG. THE FAILURE PROPOGATED LONGITUDINALLY ALONG THE BOTTOM OF THE DRIP BARREL IN BOTH DIRECTIONS FROM THE INITIAL POINT OF FAILURE UNTIL REACHING GIRTH WELDS ON BOTH ENDS OF THE FAILED PIPE SEGMENT. THE FAILURE SPLIT AND TURNED BOTH DIRECTIONS ALONG THE GIRTH WELD AT BOTH ENDS. THE PIPE REMAINED ATTACHED ON THE TOP AT BOTH ENDS FOLLOWING THE FAILURE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020085 | 2002-11-01 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1415 | 2002-10-04 | 2002 |  |  | LA |  | 524G-101+0.00 | 0+00 | N29 DEG 03'22.42 | W90 DEG 15' 08.04 | OFFSHORE |  | BAY MARCHAND | 5 | LA | NO | NO | INTERSTATE | OTHER | RISER & PIPELINE DAMAGED DURING HURRICANE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3850000 | 3227701.1403 | 4122112.5122 | 2350000 | 1956432.0388 | 1500000 | 2165680.4734 | 0 | 0 | NO | NO | NO | NO | 0 |  | 16 | 0 | 624915 | 2002-10-04 | 850 | 1235 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 16 | 0.38 |  | 42000 | SMLS |  | U.S.S | 1968 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | DAMAGE DUE TO HURRICANE | [51 empty] | THE LEAK OCCURRED ON TGP LINE 524G-100 IN BAY MARCHAND BLOCK 5 GULF OF MEXICO. THE RISER AND ASSOCIATED PIPELINE WAS DAMAGED, AS A RESULT OF HURRICANE LILI.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020086 | 2002-10-31 | ORIGINAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 2603 AUGUSTA | HOUSTON | HARRIS | TX | 77057 | 200 | 2002-10-03 | 2002 |  |  | LA |  | E1 309C |  | 28 17.881 | -91 42.948 | OFFSHORE |  | EUGENE ISLAND | 309C | LA | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 974667.1598 | 2165680.4734 | 0 | 0 | 1500000 | 2165680.4734 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 |  |  | 887 | 1250 | YES | NO | NO | NO | NO |  | HENRY WANG | 7132674371 | HWANG@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 26 | 0.56 | X-52 | 52000 | DSAW DOUBLE SUBMERGED ARC WELD |  | US STEEL CORPORATION | 1969 | UNDER WATER |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | PRODUCER'S EUGENE ISLAND 309C PLATFORM TOPPLED OVER DURING HURRICANE LILI. COLUMBIA GULF HAS 3 RISERS ON THIS FACILITY. TWO 6" LINES COMING FROM EL 309G AND EL 314J AND ONE 26" RISER THAT LEAVES THAT PLATFORM. ALL THREE LINES WERE DAMAGED SUBSEA. AN END CONNECTOR WILL BE INSTALLED AT THE END OF THE 26" LINE WITH A SUBSEA ASSEMBLY TO CONNECT THE TWO 6" LINES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020087 | 2002-11-13 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1820 | 2002-10-08 | 2002 | KELLOGG | JASPER | IA | 50135 | IAB-62501 MP41.728 | 2200+05 | N 41.74 | W92.72 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133900 | 97185.5125 | 173181.9706 | 32950 | 27431.6748 | 100950 | 145750.2959 | 0 | 0 | NO | NO | NO | YES | 60 | PRECAUTIONARY | 2 | 10 | 625359 | 2002-10-08 | 615 | 800 | NO | NO | NO | NO | YES | NO | CAROLYN DESCOTEAUX SR | 4023987495 | CAROLYN.DESCOTEAUX@DYNEGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 10 | 0.25 | API-5LX | 42000 | ERW |  | YOUNGTOWN STEEL | 1954 | UNDER GROUND |  | 38 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PHONE/CABLE |  | YES | 9 | 24 | 2002 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | ON SEPTEMBER 24, 2002 NORTHERN NATURAL GAS RECEIVED A ONE-CALL REQUEST FOR CABLE INSTALLATION IN JASPER COUNTY, SECTION 24, T80N, R18W. A NORTHERN REPRESENTATIVE MET WITH THE CONTRACTOR TUESDAY OCTOBER 8, 2002 AT THE EXCAVATION SITE AND FLAGGED THE LINE. THE CONTRACTOR INDICATED HE WOULD NOT BE READY TO CROSS NORTHERN'S LINE UNTL EARLY MORNING WEDNESDAY OCTOBER 9, 2002. LATE TUESDAY AFTERNOOD, AFTER NORMAL BUSINESS HOURS, THE NORTHERN EMPLOYEE RECEIVED A CALL ON HIS CELL PHONE FROM THE CONTRACTOR. THE CONTRACTOR COMMUNICATED HE HAD PROGRESSED FARTHER THAN EXPECTED AND WAS AT NORTHERN'S LINE READY TO CROSS. THE NORTHERN EMPLOYEE GAVE THE CONTRACTOR APPROVAL TO CROSS NORTHERN'S PIPELINE BELIEVING THAT NORTHERN'S PIPELINE WAS SUBSTANTIALLY DEEPER THAN THE CABEL PLOWING DEPTH.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20020088 | 2002-11-08 | SUPPLEMENTAL | 31296 |  | VENOCO, INC | 5464 CARPINTERIA AVE | CARPINTERIA | SANTA BARBARA | CA | 93105 | 1315 | 2002-10-15 | 2002 | PITTSBURG | CONTRA COSTA | CA | 94865 | 4455.86 |  | 38.032 | 121.989 | ONSHORE | 2 |  |  |  | NO | YES | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24000 | 19920.1112 | 26093.2096 | 14000 | 11655.3398 | 10000 | 14437.8698 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 | 626279 | 2002-10-15 | 450 | 740 | NO | NO | NO | NO | YES | YES | KEITH WENAL | 8057452259 | KWENAL@VENOCOINC.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12 | 0.25 | API5L | 3500 | ERW |  |  |  | UNDER GROUND |  | 108 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 10 | 7 | 2002 | ONE-CALL SYSTEM | YES |  | YES | ACCURATE | YES | [36 empty] | A THIRD PARTY CONTRACTOR WAS INSTALLING A WATER PIPELINE FOR A LOCAL WATER DEPARTMENT IN THE GENERAL VICINITY OF THE VENOCO GAS PIPELINE, BUT NOT NEAR THE PIPELINE. THE CONTRACTOR WAS MADE AWARE OF THE GAS PIPELINE LOCATION BY A VENOCO EMPLOYEE PERFORMING ROUTINE PIPELINE SYSTEM MONITORING. THE GAS PIPELINE LOCATION WAS DESCRIBED AND IDENTIFIED BY THE VENOCO EMPLOYEE TO THE CONTRACTRO SUPERVISOR ON SITE. PERMANENT PIPELINE MARKERS WERE IN PLACE IN THE IMMEDIATE AREA AND WERE POINTED OUT AS WELL AS A PIPELINE DESCRIPTION PROVIDED TO THE CONTRACTOR SUPERVISOR. FOLLOWING THE ABOVE EVENTS, THE CONTRACTOR BUILT A STAGING AREA DIRECTLY ABOVE THE VENOCO GAS PIPELINE FOR SLURRY MIXING OPERATIONS TO SUPPORT THE WATER PIPELINE PROJECT. THIS STAGING AREA WAS AWAY FROM THE TRENCHINGAND EXCAVATING ACTIVITIES DIRECTLY ASSOCIATED WITH LAYING THE WATER PIPELINE. DEVELOPMENT OF THE STAGING AREA INCLUDED TOPPIN A SMALL KNOLL WITHIN THE STAFING AREA TO ENABLE A LEVEL WORK LOCATION. THE GAS PIPELINE RAN DIAGONALLY THROUGH THE STAGING AREA FOLLOWING THE LOCAL TOPPGRAPHY. EXCAVATION BY THE CONTRACTOR OF THE ELEVATED AREA REMOVED APPROXIMATELY 9 FEET OF EARTH ABOVE AND PROTECTING THE PIPELINE. THE FINISHED ELEVATION OF THE STAGING AREA LEFT APPROXIMATELY 6" OF EARTH PROTECTING THE HIGHEST POINT OF THE PIPELINE. APPROXIMATELY TWO WEEKS AFTER COMPLETION AND USE OF THE STAGING AREA VENOCO'S CONTRACTOR FOR HANDLING UNDERGROUND SERVICE ALERT (USA) NOTIFICATIONS RESPONDED TO A USA NOTIFICATION REGARDING A WATER LINE INSTALLATION NEAR THE VENOCO GAS PIPELINE. THE VENOCO CONTRACTOR VISTED THE USA LOCATION, BUT THE ACTUAL WATER PIPELINE WORK WAS NOT NEAR THE VENOCO GAS PIPELINE. AT THAT TIME VENOCO'S CONTRACTOR TALKED WITH THE WATER PIPELINE PROJECT SUPERVISOR ON-SITE REGARDING THE LOCATION OF THE GAS PIPELINE INCLUDING THE PIPELINE LOCATION WITHIN THE WATER PROJECT STAGING AREA. A MATERIAL PILE EXISTED IN THE STAGING AREA TO SUPPORT A PUG MIXER AND SLURRY OPERATIONS. THE MATERIAL PILE WAS LOCATED DIRECTLY ABOVE THE GAS PIPELINE. A FRONT END LOADER WAS BEING USED TO MOVE MATERIAL FROM THE PILE TO THE PUG MIXER. OVER A PERIOD OF TIME, WHILE MOVING MATERIAL TO THE PUG MIXER THE FRONT END LOADER WAS ALSO REMOVING ADDITIONAL EARTH ABOVE THE PIPELINE. EVENTUALLY, WHILE SCRAPING THE GROUND MOVING INTO THE MATERIAL PILE FOR ANOTHER LOAD THE FRONT END LOADER BUCKET TORE A 4" X 6" HOLE IN THE GAS PIPELINE. THE PIPELINE AUTOMATICALLY ISOLATED ON LOW PRESSURE. THE WORKER EVACUATED THE AREA, THE AREA WAS SECURED AND ISOLATED BY THE CONTRACTOR UNTIL VENOCO RESPONDERS ARRIVED. DAMAGED SECTION WAS CUT OUT AND REPAIRED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020089 | 2002-11-19 | ORIGINAL | 6690 |  | GREAT PLAINS NATURAL GAS CO | 105 WEST LINCOLN AVE | FERGUS FALLS | OTTER TAIL | MN | 56537 | 300 | 2002-10-20 | 2002 | LIDA | PELICAN RAPIDS | MN |  | PELICAN RAPIDS | 890+04 | 46.5514641 | -96.0053101 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | BROKE OFF A 1/4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 45638.9473 | 100759.4574 | 500 | 416.2621 | 59500 | 85905.3254 | 10000 | 14437.8698 | NO | NO | NO | NO | 0 |  | 11 | 0 | 626861 | 2002-10-20 | 580 | 730 | YES | NO | NO | NO | NO | NO | DOUGLAS M LEE | 9999999999 | DOUG.LEE@MDU.COM | TRANSMISSION | OTHER | PRESSURE TAP NIPPLE | STEEL |  | NO | NO | NO | OTHER | VALVE SITE | 1971 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON SUNDAY, OCTOBER 20, 2002 AT APPROXIMATELY 3:00 A.M. MS. NICOLE HOTZFIELD WAS DRIVING HER FORD RANGER PICKUP WHEN IT LEFT A RURAL TOWNSHIP ROAD STRIKING AN EIGHT-INCH VALVE SITE ON GREAT PLAINS NATURAL GAS CO.'S (GPNG'S) TRANSMISSION PIPELINE NEAR PELICAN RAPIDS, MN. THIS VALVE SITE IS THE TAKE-OFF POINT FOR A THREE-INCH DIAMETER TRANSMISSION PIPELINE THAT SERVES PELICAN RAPIDS. AFTER THE ACCIDENT, THE DRIVER CALLED FOR 911 EMERGENCY SERVICES, AND THEN LEFT THE SCENE OF HER OWN ACCORD. EMERGENCY RESPONDERS CLOSED THE COUNTY ROAD WHILE GPNG EMPLOYEES DETERMINED THE BEST METHOD TO STOP THE RELEASE OF GAS WITHOUT UNNECESSARILY ENDANGERING ANYONE. AROUND NOON ON OCTOBER 20, THE PRESSURE ON THE LINE HAD BEEN LOWERED TO APPROXIMATELY 350 PSIG AND TWO-EMPLOYEES IN PERSONAL PROTECTIVE EQUIPMENT USED AN "EASYOUT" TO REMOVE A BROKEN 1/4" DIAMETER NIPPLE FROM WHERE A PRESSURE TAP WAS BROKEN AS A RESULT OF THE ACCIDENT. A NEW NIPPLE WAS THREADED IN A VALVE IN THE OPEN POSITION INSTALLED. FINALLY, THE VALVE WAS CLOSED, STOPPING THE UNCONTROLLED RELEASE OF NATURAL GAS. AT THIS POINT IT WAS UNCLEAR THAT THE DAMAGES WOULD EXCEED $50,000 AND THERE WAS NO EVIDENCE THAT THERE WERE INJURIES REQUIRING I-PATIENT CARE. ACCORDINGLY, THE INCIDENT WAS NOT REPORTED TO THE NATIONAL RESPONSE CENTER. MINNESOTA OFFICE OF PIPELINE SAFETY OFFICER SWEENEY WAS KEPT INFORMED THROUGHOUT THE EVENT. ON MONDAY, OCTOBER 21,2002,A TEAM ASSESSED THE DAMAGE AND DEVELOPED A COURSE OF ACTION TO REPLACE THE DAMAGED THREE-INCH PIPING THAT SERVES PELICAN RAPIDS AND TO MAKE THE REMAINDER OF THE VALVE SITE SAFE UNTIL THE NEXT WARM SEASON WHEN THE LINE CAN BE REMOVED FROM SERVICE WITHOUT JEOPARDIZING SERVICE TO THOUSAND OF CUSTOMERS. AT THIS TIME AN ESTIMATE WAS MADE FOR THE REPAIRS. THE TEMPORARY REPAIRS WOULD COST APPROXIMATELY $20,000 AND THE PERMANENT REPAIRS, APPROXIMATELY $40,000. THE HIGH COST IS DUE TO THE NEED FOR STOPPER FITTING AND TEMPORARY BYPASS PIPING WHILE REPAIRS ARE MADE. BASED ON THIS INFORMATION, GPNG IMMEDIATELY FIELD AN INCIDENT REPORT WITH THE NATIONAL RESPONSE CENTER, 1730 HOURS, OCTORBER 21, 2002. ON THURSDAY, OCTOBER 24, 2002 AT APPROXIMATELY 9:30 P.M CDT, TEMPORARY REPAIRS TO THE PIPING WERE COMPLETED. GPNG WILL COMPLETE FINAL REPAIRS IN THE SPRING OF 2003.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020090 | 2002-12-23 | ORIGINAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET 1000 | HOUSTON | HARRIS | TX | 77002 | 1845 | 2002-11-24 | 2002 | MINTURN | LAWRENCE | AR | 72445 | 767 |  | N36.00162' | W 91.05516' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 99441.2629 | 117134.4861 | 80000 | 66601.9417 | 25000 | 36094.6746 | 10000 | 14437.8698 | NO | NO | NO | NO | 0 |  | 3 | 15 | 630054 | 2002-11-24 | 829 | 858 | NO | NO | YES | NO | NO | NO | REBECCA VOSS FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 30 | 0.3 | 5L-X60 | 60000 | SUBMERGED ARC WELD |  | NATIONAL TUBE MILLS | 1962 | UNDER GROUND |  | 54 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | PITTING 1% DEEP | STRESS CORROSION CRACKING |  | NO |  | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020091 | 2002-02-19 | ORIGINAL | 19325 |  | TXU FUEL CO | 1601 BRYAN ST EP-17 | DALLAS | DALLAS | TX | 75201 | 400 | 2002-01-03 | 2002 | TRENTON | FANNIN | TX | 75490 |  | 772+42 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148000 | 130152.7331 | 146441.5752 | 110000 | 91577.6699 | 38000 | 54863.9053 | 0 | 0 | NO | NO | NO | YES | 0 | PRECAUTIONARY | 1 | 30 | 591564 | 2002-01-18 | 645 | 880 | NO | YES | NO | NO | NO | NO | KEITH COURTNEY | 2148752859 | KCOURT@TXU.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 10.75 | 0.19 | X42 | 42000 | ERW |  | US STEEL |  | UNDER GROUND |  | 2 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | EXAMINATION OF THE PIPELINE AT THE POINT OF RUPTURE, INDICATES THAT THE PIPELINE WAS STRUCK BY SOME TYPE OF EQUIPMENT SOME TIME IN THE PAST. THIS STRIKE LEFT SOME LARGE DENTS/SCRAPES ON THE TOP AND NEAR TOP OF THE PIPELINE. IT DOES NOT APPEAR THAT ANY TYPE OF EFFORT WAS MADE TO RECOAT THE DAMAGED AREA, NOR WAS THIS DAMAGE REPORTED TO ANYONE IN THE SHERMAN DISTRICT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020092 | 2002-02-15 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 737 | 2002-01-16 | 2002 | VALLEY ACRES | KERN | CA |  | 71.72 | 3787+32.2 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 163941.1946 | 221518.4983 | 110000 | 91577.6699 | 90000 | 129940.8284 | 0 | 0 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 2 | 30 | 591361 | 2002-01-16 | 366 | 400 | NO | NO | YES | NO | NO | NO | W JEFF KOSKIE | 6617758770 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION |  |  |  |  | NO | NO | NO |  |  |  | 26 | 0.25 | X41 | 41000 | FLASH WELD | [5 empty] | 48 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | OTHER | N/A |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | FAILURE AT WELD SITE OF BAND ON LINE 85 CAUSED CIRCUMFERENTIAL TEAR OF LINE. FAILURE INITATED AT MULTIPLE HYDROGEN CRACKS AT THE TOE OF THE FILLET WELD AND AT NUMEROUS ARC BURNS. THE HYDROGEN CRACKING OCCURRED IMMEDIATELY AFTER THE WELD WAS MADE AND WAS CONSISTENT WITH EXCESSIVE WELD COOLING RATES ON STEEL HAVING HIGH CARBON EQUIVALENT. ACTUAL YIELD STRENGTH OF PIPELINE AT INCIDENT IS 58,000 AS MEASURED. LOCATION LATITUDE - N 35 11 MIN 41.684 SEC LONGITUDE - W119 23 MIN 56.024 SEC SECTION F5 C IS UNKNOWN. CHECKED NO TO BYPASS FIELD
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020093 | 2002-03-14 | ORIGINAL FINAL | 13580 |  | NORTH CAROLINA NATURAL GAS CORP | 410 S WILMINGTON ST | RALEIGH | WAKE | NC | 27601 | 1500 | 2002-02-04 | 2002 | NEW BERN | CRAVEN | NC | 28560 | 26.48 | 1398+40 | 35.132 | 77.095 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141252 | 105010.5691 | 177766.5859 | 42815 | 35644.5267 | 98437 | 142122.0592 | 0 | 0 | YES | NO | NO | YES | 250 | PRECAUTIONARY | 0 | 45 | 593128 | 2002-02-05 | 503 | 642 | NO | YES | NO | NO | NO | NO | THEODORE R HODGES | 9195466369 | THEODORE.HODGES@PGNMAIL.COM | TRANSMISSION | OTHER | TAPPING TEE PULLED OFF OF MAIN | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 4 | 0.16 | API 5L | 35000 | ERW |  | MANNESMANN | 1959 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | WELL DRILLING WORK | NO |  |  |  |  | NO | [40 empty] | ON FEBRUARY 2, 2002 AT APPROXIMATELY 3:08PM, A CONTRACTOR WORKING FOR AN ENGINEER PERFORMING CONSULTING WORK FOR THE CITY OF NEW BERN WAS EXCAVATING AT A SITE JUST UPSTREAM OF NCNG'S NEW BERN TOWN BORDER STATION WHEN HE STRUCK AND RUPTURED THE 4-INCH STEEL TRANSMISSION LINE FEEDING THE STATION. IN A MATTER OF MINUTES AFTER THE INCIDENT HAD OCCURRED AND WAS ABLE TO ALERT NCNG EMERGENCY RESPONSE PERSONNEL IMMEDIATELY. EMERGENCY PERSONNEL ARRIVED AT THE SCENE WITHIN A MATTER OF 30 MINUTES AND WITH THE HELP OF LOCAL FIRE DEPARTMENT PERSONNEL WERE ABLE TO ESTABILISH A SAFE PERIMETER AROUND THE INCIDENT. MEASURES WERE TAKEN SHORTLY THEREAFTER TO START CURTAILING CUSTOMERS AND MONITORING DISTRIBUTION PRESSURES AT LOW POINTS ON THE SYSTEM. DURING THE NIGHT, A MUELLER FITTING WAS INSTALLED AND A 2-INCH BYPASS INSTALLED AROUND THE DAMAGED LINE. LINE STOPPERS WERE DROPPED AND THE BLOWING GAS WAS FINALLY STOPPED AT APPROXIMATELY 1:00PM ON FEBRUARY 5, 2002. THE PROXIMITY OF THE DAMAGED SECTION TO THE TOWN BORDER STATION AND WETLAND AREA MADE IT DIFFICULT TO INSTALL THE REPAIR FITTINGS TO SEAL OFF THE BLOWING GAS SOONER. AT 3:15PM, A REPAIR CLAMP HAD BEEN INSTALLED AND RESTORATION OF SERVICE TO CURTAILED CUSTOMERS BEGAN AROUND 6:15PM. BY NOON ON FEBRUARY 6, 2002 SERVICE HAD BEEN RESTORED TO APPROXIMATELY 90% OF THE INTERRUPTED CUSTOMERS. IN TOTAL, SERVICE TO 190 COMMERICAL, 350 RESIDENTIAL, AND 4 INDUSTRIAL CUSTOMERS INSIDE THE NEW BERN DISTRIBUTION SYSTEM HAD BEEN SHUT OFF IN ORDER TO MAINTAIN THE OPERATION OF THE REMAINING DISTRIBUTION SYSTEM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020094 | 2002-03-04 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1550 | 2002-02-05 | 2002 | WYOMING | SWEETWATER | WY |  | LINE 5B/298.78 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 84900.9019 | 91315.06 | 75000 | 62439.3204 | 20000 | 28875.7396 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 593157 | 2002-02-05 | 750 | 850 | NO | NO | YES | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 12 |  | 5L | [5 empty] | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 10 | 19 | 1978 | WATER |  | 8 | 1460 | [12 empty] | APPROXIMATELY 6" OF A 12" OD GARLOCK (PAPER) GASKET FAILED, POSSIBLY DUE TO IMPROPER INSTALLATION AND CAUSED A LEAK. GASKET WAS IN A FLANGED CONNECTION BETWEEN A 12" PLUG VALVE AND A 12" CHECK VALVE/BECAUSE THE 12" VALVE COULD NOT BE COMPLETELY CLOSED. 14 MILES OF 24" TRANSMISSION PIPELINE HAD TO BE BLOWN DOWN TO ISOLATE THE LEAK.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20020095 | 2002-03-14 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | ONE WILLIAMS CENTER | TULSA | OSAGE | OK | 74121 | 1710 | 2002-02-15 | 2002 | PECAN ISLAND | VERMILION | LA |  |  |  | 29.17.52 | 92.22.21 | OFFSHORE |  | VERMILION | 67 |  | YES | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657641 | 427320.7237 | 949493.5148 | 0 | 0 | 0 | 0 | 657641 | 949493.5148 | NO | YES | NO | NO | 0 |  | 2 | 5 | 591303 | 2002-02-15 | 800 | 1168 | NO | NO | NO | NO | YES | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.31 | API 5LX | 52000 |  |  |  | 1959 | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1959 | NO | [57 empty] | PRELIMINARY CAUSE OF FAILURE- INTERNAL CORROSION, FAILURE STILL UNDER ONGOING INVESTIGATION. LINE IS CURRENTLY ISOLATED AND OUT OF SERVICE. ANY CHANGE IN STATUS SHALL BE REPORTED ON SUPPLEMENTALS REPORTS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20020096 | 2002-05-07 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 830 | 2002-04-08 | 2002 | COLUMBUS | BARTHOLOMEW | IN | 47521 | MLV 55+ | 6033+91 | 39.1786015 | -86.0573309 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854839 | 665086.6382 | 1017305.5712 | 354839 | 295412.0801 | 500000 | 721893.4911 | 0 | 0 | NO | NO | NO | YES | 6 | PRECAUTIONARY | 1 | 56 | 598805 | 2002-04-08 | 711 | 1037 | YES | NO | NO | NO | NO | NO | LOUIS A SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 30 | 0.36 |  | 60000 | DSAW |  | STEEL CO OF CANADA | 1955 | UNDER GROUND |  | 100 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | THERE WAS A LEAK ON THE 501 30 MAINLINE BETWEEN MLV 55 & 56. A CLOUD AND ROARING NOISE REPORTED BY BARTHOLOMEW COUNTY SHERIFF DEPT, SOUTH OF HWY 46, WEST OF COLUMBUS, IN. INITIAL DISCOVERY INDICATED A LEAK AND NO FIRE PRESENT. THE PIPELINE FAILURE APPEARS ATTRIBUTABLE TO EXTERNAL STRESSES INDUCED BY THE LATERAL FORCE OF SOIL MOVEMENT AND HYDRAULIC LOAD FROM THE UNSTABLE HILLSIDE, ALONG WHICH IT TRAVERSES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020097 | 2002-06-04 | ORIGINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1745 | 2002-01-06 | 2002 | SCHUTENBURG | LAVACA | TX |  | MP 82+3696 |  | N 29 37' 14" | W 96 54' 21" | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 |  |  | 300 | 355 | NO | NO | NO | NO | YES | NO | KEVIN P SEHY | 2105284206 | KEVIN.SEHY@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 4 | 0.19 |  | 24000 |  |  |  |  | UNDER GROUND |  | 84 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | EXTERNAL LOADING | [51 empty] | A LOG DRIFT CREATED BY HEAVY RAINS HIT THE PIPELINE CREATING LONGITUDINAL STRAIN WHICH STRESSED A DRESSER COUPLING CAUSING IT TO SEPARATE. THE COUPLING WAS LOCATED APPROXIMATELY 15' LANDWARD FROM THE RIVERBANK. THE PIPE DEPTH AT THE LOCATION OF THE LEAK WAS 84 INCHES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20020098 | 2002-08-20 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1250 | 2002-07-24 | 2002 | ROANOKE | RANDOLPH | AL | 36274 | 976.327 | 10453+76 |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50500 | 32968.2743 | 72605.6112 | 500 | 416.2621 | 50000 | 72189.3491 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 40 | 617723 | 2002-07-24 | 250 | 800 | NO | NO | NO | NO | YES | NO | B R LANDES | 7132152001 | BILL.R.LANDES@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1951 | 4.5 | 0.15 | API 5L | 35000 | SMLS | 2022-01-02 | NATIONAL TUBE | 1951 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | DAMAGE CAUSE BY VEHICLE WHEN IT STRUCK THE 4" HEADER AND KNOCKED OFF A 1/2" VENT VALVE AND PRODUCED A 1 1/2" LONGITUDINAL CRACK IN A 2" PIPE. AS A RESULT GAS AND ODORANT LEAKED FROM THE M&R PIPING. THERE WAS NO INTERRUPTION OF SERVICE TO ROANOKE OR WEDOWEE AS BY-PASS LINE WAS TEMPORAILY INSTALLED UNTIL REPAIRS WERE COMPLETE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030001 | 2002-12-27 | ORIGINAL | 8116 |  | INDUSTRIAL GAS SUPPLY CORP | 1301 TRAVIS ST 7TH FLOOR | HOUSTON | HARRIS | TX | 77002 | 207 | 2002-11-30 | 2002 | HOUSTON | HARRIS | TX | 77045 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149338 | 143102.4627 | 124472.9902 | 149100 | 124129.3689 | 238 | 343.6213 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 33 | 630480 | 2002-11-30 | 344 | 375 | NO | NO | NO | NO | NO | NO | JERY V GANN | 7139678093 | JERRY.GANN@CENTERPOINTENERGY.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.25 |  | 30000 | LAP WELD |  |  |  | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | OTHER | LAP WELD | MATERIAL DEFECT |  | NO | NO
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030002 | 2002-12-30 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 525 MILAM STREET | SHREVEPORT | CADDO PARISH | LA | 71101 | 1015 | 2002-09-28 | 2002 | ROCKY BRANCH | UNION | LA | 71103 | 1 | 2+30 | 32.670403 | -92.199377 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57000 | 44761.346 | 67014.2902 | 25000 | 20813.1068 | 27000 | 38982.2485 | 5000 | 7218.9349 | NO | NO | NO | YES | 36 | PRECAUTIONARY | 0 | 30 | 624228 | 2002-09-28 | 350 | 500 | NO | NO | NO | YES | NO | NO | MITCHELL L REDDING | 4055562412 | MICKY.REDDING@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1927 | 10 | 0.32 | API5L |  | MACHINE ELEC FUSION ARC WELD |  |  |  | OTHER | OPEN DRAIN | 6 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | GALVANIC |  | NO |  | NO | [57 empty] | THE PIPE WAS EXPOSED IN ABOUT A 3FOOT AREA WHERE THE GROUND HAD WASHED AWAY. THE GENERAL CORROSION ALLOWED THE PIPE TO BLOW-OUT. A SECTION OF PIPE WAS INSTALLED TO CORRECT THE PROBLEM. 7-15-03 PIPE WAS EXPOSED AT TIMES AND NOT EXPOSED AT OTHER TIMES. THE PIPE WAS SCREW COLLAR PIPE INSTALLED IN 1927. THE SEGMENT WAS NOT CATHODICALLY PROTECTED AND HAD GENERAL CORROSION IN THIS AREA CAUSING WALL LOSS ALLOWING PIPE TO BLOW-OUT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030003 | 2002-12-30 | SUPPLEMENTAL FINAL | 20044 |  | PRAXAIR, INC | 39 OLD RIDGEBURY RD | DANBURY | FAIRFIELD | CT | 06810 | 1400 | 2002-12-03 | 2002 | DEER PARK | HARRIS | TX | 77536 |  |  | 29.72075 | -95.10743 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42000 | 27908.6 | 59416.5278 | 2000 | 1665.0485 | 20000 | 28875.7396 | 20000 | 28875.7396 | NO | NO | YES | NO | 0 |  | 7 | 30 | 630736 | 2002-12-03 | 1400 | 2160 | NO | NO | NO | YES | NO | NO | GREG COURSON | 2814787801 | GREG_COURSON@PRAXAIR.COM | TRANSMISSION | OTHER | HEAT AFFECTED ZONE OF WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 2.5 | 0.2 | UNKNOWN | 135000 | SEAMLESS | N/A | UNKNOWN |  | UNDER GROUND |  | 53 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | WELD | [12 empty] | NO | YES | 11 | 21 | 2002 | WATER |  | 8 | 3420 | [12 empty] | FAILURE OF STEEL 2 1/2 INCH HYDROGEN PIPELINE WITH AN MAOP OF 2160 PSIG OCCURRED 1400 HOURS DEC 3, 2002. THE FAILURE OCCURRED AFTER A LEAK HAD BEEN DETECTED AND THE LINE REPAIRED. THE LEAK WAS DISCOVERED DURING A ONE-CALL RESPONSE FOR PLANNED THIRD PARTY EXCAVATION IN EARLY NOVEMBER 2002. AT THAT TIME, THE LEAK WAS ISOLATED, A SECTION OF PIPE REMOVED AND REPLACED WITH NEW PIPE. FOLLOWING THE REPAIR, THE ENTIRE PIPELINE WAS SUCCESSFULLY HYDROSTATICALLY TESTED, CLEANED AND DRIED. THE LINE WAS RETURNED TO SERVICE ON NOVEMBER 23RD. THIRD PARTY EXCAVATION AROUND THE PIPELINE COMMENCED MONDAY, DECEMBER 2, 2002, BACKFILLED AND COMPLETED 1200 HOURS DECEMEBER 3, 2002.TWO HOURS AFTER BACKFILLING WAS COMPLETED, THE EVENT OCCURRED. IT IS SUSPECTED THAT FAILUE OF THE PIPELINE OCCURRED IN THE HEAT-AFFECTED ZONE OF A BUTT WELD ON THE ORIGINAL PIPE MATERIAL THAT HAD BECOME HARDENED AND SUSPECTIBLE TO SUDDEN STRESS RELIEF FAILURE. 10-28-03 A METALLURGICAL EXAMINATION OF THE FAILED WELD REVEALED THAT THIS PIPE MATERIAL HAD FAILED DUE TO THE APPLICATION OF HEAT, WHICH HARDENED AND MADE THE HIGH STRENGTH STEEL SUSCEPTIBLE TO FAILURE. THIS ENTIRE SEGMENT OF PIPELINE IN WHICH THE FAILURE OCCURRED HAS BEEN REMOVED FROM SERVICE AND WILL BE ABANDONED AND REPLACED WITH A NEW PIPELINE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20030004 | 2003-12-30 | ORIGINAL FINAL | 18646 |  | STINGRAY PIPELINE CO | 1301 MCKINNEY ST SUITE 700 | HOUSTON | HARRIS | TX | 77010 | 1040 | 2002-11-25 | 2002 | [6 empty] | 28 41 MIN NORTH | 92 35 MIN 23 SEC WES | OFFSHORE |  | VERMILLION | 221 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58019 | 40177.0243 | 78865.3612 | 8019 | 6676.0121 | 50000 | 72189.3491 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 750 | 1440 | YES | NO | NO | NO | NO | NO | RICHARD HARRINGTON | 3375692286 | RHARRINGTON@SHELL-GT.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.38 | 5LX52 | 52000 | SMLS |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED |  |  | OTHER | INTERNAL | YES | 1984 | NO | [57 empty] | THIS PIPELINE HAS BEEN REMOVED FROM SERVICE AND IS SCHEDULED FOR ABANDONMET IN 2003.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030005 | 2003-01-07 | ORIGINAL FINAL | 4900 |  | TEJAS GAS PIPELINE LP | 500 DALLAS STREET 1000 | HOUSTON | HARRIS | TX | 77002 | 833 | 2002-12-04 | 2002 | REFUGIO | REFUGIO | TX | 78377 | 83 |  | N 28 2.533' | W 97 08.963' | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565730 | 471264.2357 | 611696.6322 | 335530 | 279336.8689 | 225700 | 325862.7219 | 4500 | 6497.0414 | NO | NO | YES | NO | 0 |  | 2 | 0 | 630810 | 2002-12-04 | 840 | 844 | NO | YES | NO | NO | NO | NO | REBECCA VOSS FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 36 | 0.42 | GRADE X60 EFW | 60000 | FLASH WELDING |  | A O SMITH | 1964 | UNDER GROUND |  | 84 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER |  | YES | 1964 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030006 | 2003-01-09 | SUPPLEMENTAL FINAL | 6900 |  | GULF SOUTH PIPELINE CO | 20 EAST GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 900 | 2002-12-10 | 2002 |  | PERRY | MS |  | 137.9 | 848+12 TO 848 + 92 | N31 18' 39.18 | W88 55' 5.34 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | TO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130500 | 87051.4491 | 183951.9834 | 7300 | 6077.4272 | 123200 | 177874.5562 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 631320 | 2002-12-10 | 265 | 430 | NO | NO | NO | NO | YES | NO | JACK L ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | UNK | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 16 | 0.25 |  | 30000 | ERW |  | NATIONAL TUBE |  | UNDER WATER |  | 24 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | DUE TO THE LOCATION OF THE LEAK AND ITS LOCATION TO THE NEAREST ROAD (1 MILE IN EACH DIRECTION) AND THE (SWAMP) WETNESS OF THE GROUND, THE REPAIR COST OF THIS LEAK REPAIR WAS ELEVATED. UPDATE**** THIS PIPELINE SEGMENT WAS ABANDONED IN PLACE AND THERE ARE NO PLANS TO REMOVE IT FROM THE GROUND, THEREFORE THE ACTUAL CAUSE OF THE LEAK CANNOT BE DETERMINED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030007 | 2003-01-09 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1705 | 2002-12-12 | 2002 |  |  | LA |  | MP 1.695 |  | 29 DEG 10' 15.2 | 88 DEG 43' 11.1 | OFFSHORE |  | MAIN PASS | 311 |  | YES | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607326 | 395554.0176 | 875015.5846 | 3000 | 2497.5728 | 604326 | 872518.0118 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 631627 | 2002-12-12 | 1200 | 1729 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1985 | 6 | 0.43 |  | 35000 |  |  |  | 1985 | UNDER WATER |  | 24 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE LEAK OCCURRED ON THE 6" MAIN PASS 311A LINE, OPERATED BY SNG IN MAIN PASS BLK. 311, GULF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS CONFIRMED BY A DIVE BOAT INVESTIGATION ON 12/13, NEAR A SUB-SEA TIE-IN. SUSPECTED DAMAGE FROM A SHIP'S ANCHOR OR A FISHING VESSEL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030008 | 2003-01-09 | SUPPLEMENTAL FINAL | 6900 |  | GULF SOUTH PIPELINE CO | 20 E GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 2130 | 2002-12-13 | 2002 | THOMASTOWN | LEAKE | MS | 39171 | 286.19 | 15111+04 | 32 52.764' | 89 40.037' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LONGITUDINAL CRACK IN HARDSPOT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114000 | 93848.1286 | 125470.9025 | 64000 | 53281.5534 | 50000 | 72189.3491 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 631762 | 2002-12-13 | 625 | 936 | NO | YES | NO | NO | NO | NO | JACK L ADAMS DOT MANAGER & SECURITY OFFICER | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 30 | 0.38 | API 5LX | 52000 | ERW |  | A O SMITH | 1951 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | HARDSPOT | [10 empty] | MATERIAL DEFECT |  | NO | YES | 5 | 1 | 1974 | WATER |  | 8 | 1271 | [12 empty] | THE PIPELINE WAS INSTALLED IN 1952 WITH PIPE THAT WAS LATER FOUND TO BE DEFECTIVE AT THE TIME OF MANUFACTURE. AN ANOMALY WAS DISCOVERED IN THE PIPE IN 1988 AS THE RESULT OF AN INTERNAL INSPECTION PROGRAM. THE ANOMALY WAS IDENTIFIED AS A HARD SPOT IN THE METAL OF THE PIPE. A PROTECTIVE SLEEVE, DESIGNED TO PREVENT RUPTURE WAS INSTALLED ON THE PIPE AT THAT TIME. ALTHOUGH THE PIPE DEVELOPED A LEAK, IT DID NOT RUPTURE DUE TO THE INSTALLATION OF THE REINFORCEMENT SLEEVE. THE LEAK WAS REPAIRED BY REPLACING THE ENTIRE JOINT OF PIPE. [ THIS SUPPLEMENTAL/FINAL WAS ORIGINALLY ENTERED UNDER OPID 31728 AS SUBMITTED. AFTER FURTHER INVESTIGATION AND DISCUSSIONS WITH OPERATOR, IT WAS DECIDED TO ENTER UNDER ORIGINAL OPID ID 6900 TO CLOSE INCIDENT.]
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20030009 | 2003-01-09 | ORIGINAL | 18646 |  | STINGRAY PIPELINE CO | 4918 GULF BEACH HIGHWAY | CAMERON | CAMERON | LA | 70631 | 2150 | 2002-12-13 | 2002 | [6 empty] | 28.07.30 | 92.49.25 | OFFSHORE |  | EAST CAMERON | 338A |  | YES | NO | INTERSTATE | OTHER | BROKEN GREASE ZERK ON 16" VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40878 | 39114.0465 | 34184.7429 | 40628 | 33823.7961 | 250 | 360.9467 | 0 | 0 | NO | NO | NO | NO | 0 |  | 23 | 50 | 631763 | 2002-12-13 | 1077 | 1200 | YES | NO | NO | NO | NO | NO | RICHARD HARRINGTON | 3375692286 | RHARRINGTON@SHELL-GT.COM | GATHERING | OTHER | VALVE GREASE ZERK | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 16 |  |  |  |  | 16" CAMERON BALL VALVE | CAMERON | 1977 | OTHER | 60' ABOVE SEA LEVEL |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [11 empty] | NO | YES | 7 | 13 | 77 | WATER | [15 empty] | CONTRACTOR WAS INSTALLING PIPE SPOOL FOR SEA ROBIN PIPELINE COMPANY IN VICINITY OF 16-INCH VALVE. 12-INCH FLANGE ON SPOOL MADE CONTACT WITH THE VALVE GREASE FITTING, BREAKING FITTING IN THREADED PORTION. ALL GREASE ZERKS ON 16-INCH VALVE WERE REPLACED AND PIPELINE RETURNED TO SERVICE ON 12-15-02.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030010 | 2003-01-09 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1130 | 2002-12-31 | 2002 | EL DORADO | UNION | AR | 71730 | NA | 2960+16 | 33.26387712 | 92.68090498 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50001 | 32489.5551 | 72190.7929 | 0 | 0 | 50001 | 72190.7929 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 633096 | 2002-12-31 | 315 | 415 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 12 | 0.31 | UNKNOWN | 24000 | ERW | NA | UNKNOWN |  | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | LEAK AT A COUPLING, LINE WAS REMOVED FROM SERVICE, COUPLING REMOVED AND A 6 FOOT PIECE OF PIPE WAS INSTALLED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030011 | 2003-01-27 | SUPPLEMENTAL FINAL | 6900 |  | GULF SOUTH PIPELINE CO | 20 E GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1230 | 2003-01-10 | 2003 | LIVINGSTON | LIVINGSTON | LA | 70754-1060 | 103.72 | 5476+41 | N30 29.5' | W90 45.5' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | THREADS STRIPPED (SEE F6 AND PART G) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 52756.4392 | 75180.1411 | 46000 | 26970.9402 | 34000 | 48209.201 | 0 | 0 | NO | NO | NO | NO | 0 |  | 13 | 30 | 633805 | 2003-01-10 | 625 | 936 | YES | NO | NO | NO | NO | NO | AL JEANSONNE | 2257774300 | AL.JEANSONNE@GULFSOUTHPL.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1985 | 2 | 0.34 | ASTM 3-33 GRD 6 | 35000 | SEAMLESS |  | T D WILLIAMSON | 1965 | UNDER GROUND |  | 47 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | AT 3:30 ON JANUARY 9, 2003, A CREW WAS IN THE PROCESS OF ABANDONING METERING FACILITIES THAT WERE ATTACHED TO INDEX 130 WHEN A SMALL LEAK WAS DISCOVERED ON A T.D. WILLIAMSON THREAD - O RING FITTING. INITIAL INVESTIGATION IDENTIFIED THE CAUSE OF THE LEAK AS A POSSIBLE FAILED GASKET THAT COULD BE REPAIRED BY PLUGGING THE TAP USING A T.D. WILLIAMSON TOOL, REMOVING THE VALVE AND FLANGE, AND INSTALLING A CAP ON THE 2" NIPPLE. SINCE IT WAS LATE IN THE DAY AND THE LEAK WAS SMALL AND DID NOT POSE AN IMMEDIATE OR PROBABLE HAZARD TO THE PUBLIC, IT WAS DECIDED TO SECURE THE WORK SITE AND WAIT UNTIL THE NEXT DAY TO COMPLETE THE WORK. UPON RETURNING TO THE SITE AND WITH FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE THREADED NIPPLE TO FLANGE JOINT WAS ACTUALLY LEAKING BUT THAT THE REPAIR COULD BE ACCOMPLISHED USING THE SAME PROCEDURE AS ORIGINALLY PLANNED TO STOP THE LEAK. WHILE ATTEMPTING TO REMOVE THE DE-PRESSURZIED PIPING DOWNSTREAM OF THE TAP VALVE TO GAIN ACCESS TO THE VALVE FOR ATTACHMENT OF THE T.D. WILLIAMSON TOOL, A SLIGHT MOVEMENT OF THE PIPE CAUSED THE LEAK CHARACTERISTICS TO CHANGE (SOUND OF ESCAPING GAS INCREASED). UPON RE-EVALUATION IT WAS DECIDED THAT THE THREADS OF THE NIPPLE OR FLANGE MAY BE DAMAGED AND THAT IT WOULD BE UNSAFE FOR THE EMPLOYEES TO PROCEED WITH THE INITIAL REPAIR APPROACH. AT 12:30 PM JANUARY 10, 2003 A DECISION WAS MADE TO LOWER THE LINE PRESSURE TO ZERO BEFORE ATTEMPTING ANY FURTHER REPAIR THE LEAK. THE COST OF THE GAS LOST DURING THE BLOW DOWN OF THE PIPELINE WOULD MAKE THE REPAIR COST EXCEED $50,000 CLASSIFYING THE LEAK AS AN INCIDENT. AN INCIDENT REPORT WAS FILED WITH THE NATIONAL RESPONSE CENTER AT 1:14 PM JANUARY 10, 2003. SINCE THIS LINE PROVIDES SUPPLIES TO LOCAL DISTRIBUTIONS COMPANIES, ALTERNATE GAS SUPPLIES NEEDED TO BE ARRANGED BEFORE REPAIRS COULD BEGIN. THEREFORE, AS AN ADDITIONAL SAFETY MEASURE, A REQUEST TO GAS CONTROL TO LOWER PRESSURE TO <450PSIG AND NOT TO ALLOW FLUCTUATION WAS MADE AT 7:00 PM FRIDAY, JANUARY 10, 2003 AND THE SITE WAS ALSO BARRICADED AND TAPED OFF WITH WARNING TAPE. STABILITY OF 440 PSIG WAS ACCOMPLISHED AT 2:00 AM SATURDAY, JANUARY 11, 2003. THE LEAK AT THIS POINT WAS LIMITED TO APPROXIMATELY 1MCF/HR. AT 9:00 AM SUNDAY, JANUARY 12, 2003 ALTERNATE GAS FEEDS TO LOCAL DISTRIBUTION COMPANIES WERE INITIATED AND NOTIFICATIONS WERE ALSO MADE TO LOCAL, STATE AND FEDERAL AUTHORITIES AS WELL AS AFFECTED GULF SOUTH CUSTOMERS. AT 12:15 PM SUNDAY, JANUARY 12, 2003 THE PRESSURE IN THE PIPELINE WAS 313 PSIG AND THE BLOW DOWN OF THE PIPELINE WAS INITIATED. UPON COMPLETION OF BLOW DOWN, THE FITTINGS WERE REMOVED FROM THE PIPELINE AND INSPECTIONS WERE MADE PRIOR TO FINAL REPAIR. TWO THREADS OF THE NIPPLE APPEARED TO BE STRIPPED AND THE END OF THE NIPPLE WAS EGG SHAPED RESULTING IN IMPROPER SURFACE CONTACT BETWEEN THE THREADS OF THE TWO COUPLED FITTINGS. FINAL REPAIR CONSISTED OF CUTTING THE THREADED AREA FROM THE NIPPLE AND WELDING A 2" CAP TO THE NIPPLE OF THE TAP. THE WELD WAS X-RAYED AND THE PREVIOUSLY INSTALLED NIPPLE AND WELD SADDLE WERE ALSO DYE PENETRANT CHECKED FOR CRACKING. THE REPAIR WAS THEN COATED AND THE LINE PURGED AND RE-PRESSURIZED. THE LINE AND ALL CUSTOMERS WAS RESTORED TO NORMAL SERVICE AT 9:OO PM SUNDAY, JANUARY 12, 2003.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030012 | 2003-01-22 | ORIGINAL | 7605 |  | HOUSTON PIPELINE CO | 1201 LOUISIANA SUITE 1201 | HOUSTON | HARRIS | TX | 77002-5600 | 1155 | 2002-12-17 | 2002 | BAYTOWN | HARRIS | TX | [5 empty] | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | OLD THIRD PARTY HIT, UNREPORTED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67600 | 44728.2954 | 96010.717 | 2600 | 2164.5631 | 65000 | 93846.1538 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 632355 | 2002-12-19 | 440 | 525 | YES | NO | NO | NO | NO | NO | ELIZABETH S BUSH-IVIE | 8326681258 | ESBUSH-IVIE@AEP.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | 0.22 |  | 24000 |  |  |  |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | OTHER | UNKNOWN | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | 4286- J.M. HUBER 8" AN HPL CONTRACTOR WAS DIGGING OUT AS PART OF A CONSTRUCTION PROJECT. A HARD ENCAPSULATED AREA WAS ENCOUNTERED. EQUIPMENT OPERATIONS WERE SUSPENDED AND THE INVESTIGATION CONTINUED BY HAND. A GAS LEAK WAS DISCOVERED IN THE "CAPSULE" AT A NIPPLE ON A VALVE. THE INVESTIGATION INDICATES THE LEAK WAS THE RESULT OF AN UNREPORTED THIRD PARTY HIT AT SOME UNKNOWN PRIOR TIME. LINE PRESSURE WAS REDUCED TO DETERMINE THE REPAIR NEEDS. THIS SECTION OF LINE WAS ISOLATED, AND 40' OF PIPE REPLACED. THE LINE WAS RETURNED TO SERVICE ON 12/18/02 AT APPROXIMATELY 3:30 PM. BAYTOWN POLICE AND FIRE DEPARTMENTS WERE ON THE SCENE, SECURED THE SITE AND MANAGED TRAFFIC CONTROL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030013 | 2003-02-03 | SUPPLEMENTAL FINAL | 3 |  | ACADIAN GAS PIPELINE SYSTEM | 338 WAVERLY ROAD | THIBODAUX | LAFOURCHE | LA | 70302 | 1500 | 2003-01-22 | 2003 | INTERCOASTAL CITY | VERMILLION | LA |  | MP-19 | 2405+63 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413000 | 263550 | 585600 | 0 | 0 | 413000 | 585600 | 0 | 0 | YES | NO | NO | NO | 0 |  | 3 | 0 | 634804 | 2003-01-22 | 900 | 1000 | YES | NO | NO | NO | NO | NO | JOEL E KOHLER | 2256752507 | JKOHLER@EPROD.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1945 | 14 | 0.41 | X-46 | 46000 | ERW |  | UKNOWN |  | UNDER WATER |  | 120 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A BARGE RAN AGROUND AND STRUCK THE 14" UNDERGROUND NATURAL GAS PIPELINE IN THE INTERCOASTAL WATERWAY, CAUSING A PINHOLE LEAK IN THE PIPELINE AND A RELEASE OF NATURAL GAS. A SPECIAL LEAK CLAMP WAS FABRICATED AND INSTALLED ON THE PIPELINE, THE CLAMP WOULD NOT SEAL. A NEW UNDER WATER CROSSING WAS DRILLED TO ACCOMMODATE 800 FEET OF NEW 14 INCH PIPELINE. THE NEW CROSSING WAS CONNECTED TO EXISTING PIPELINE ON EACH SIDE OF INTECOASTAL WATERWAY. PIPELINE WAS RETURNED BACK TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030014 | 2003-02-06 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 910 | 2003-01-07 | 2003 | ANAHEIM | ORANGE | CA | 92806-1312 | 368' E/E PROPERTY LINE |  | 33.8182 | -117.9055 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311000 | 198497.2476 | 440140.8042 | 1000 | 586.3248 | 300000 | 425375.3027 | 10000 | 14179.1768 | YES | NO | NO | NO | 0 |  | 15 | 20 | 633577 | 2003-01-07 | 180 | 196 | NO | NO | YES | NO | NO | NO | W JEFF KOSKIE | 2132443283 | WKOSIE@SEMPRAUTILITIES.COM | TRANSMISSION | OTHER | UNKNOWN, DAMAGED PIPING ABANDONED AND REPLACED | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 12 | 0.22 | UKNOWN | 24000 | UKNOWN |  | UNKNOWN | 1947 | UNDER PAVEMENT |  | 100 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ELECTRICAL ARC BURN FROM DOWNED POWER LINE COMING IN CONTACT WITH CASING VENT PIPING. |  | DOWNED POWER LINE STRUCK GAS CASING VENT. ELECTRICITY TRAVELLED ALONG CASING AND ARCED ONTO TRANSMISSION LINE INSIDE CASING, CAUSING LEAK. TWO OTHER LEAKS WERE DISCOVERED AT LOCATIONS WHERE ELECTRICITY LEFT TRANSMISSION LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030015 | 2003-02-06 | ORIGINAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1800 | 2003-01-10 | 2003 | PORT SULPHUR | PLAQUEMINES | LA | 70083 | DISCHARGE HDR-AD-3 |  | N 29D 30' 57.46" | W 89D 43' 46.87" | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111000 | 70870.1289 | 156557.2691 | 1000 | 586.3248 | 110000 | 155970.9443 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 45 | 633829 | 2003-01-10 | 790 | 1000 | NO | NO | YES | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | 6' WELD CAP ON BOTTOM OF SUMP ASSEMBLY | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1969 | 36 | 0.63 |  | 60000 | DSAW |  | UKNOWN | 1969 | UNDER GROUND |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1969 | NO | [57 empty] | THERE WAS A LEAK LOCATED ON 527A-100 LINE ON THE DISCHARGE HEADER AD-3, IN THE PORT SULPHUR COMPRESSOR STATION. INTERNAL CORROSION AT A SUMP ON THE 36" HEADER IS THE APPARENT CAUSE. A PIN HOLE LEAK ON THE 6" CAP ON THE BOTTOM OF THE SUMP WAS FOUND.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030016 | 2003-02-17 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 542 | 2003-01-30 | 2003 | COMER | MADISON | GA |  | M.P. 1124.71 | 59384+85 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | GAS IGNITION & EXPLOSION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1318900 | 841637.0339 | 1870091.6223 | 0 | 0 | 1318900 | 1870091.6223 | 0 | 0 | NO | NO | YES | NO | 0 |  | 0 | 2 | 635453 | 2003-01-30 | 773 | 800 | NO | NO | NO | NO | YES | NO | B.R. LANDES | 7132152001 | BILL.R.LANDES@WILLIAMS.COM | TRANSMISSION | OTHER | COMPRESSOR | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2000 | [7 empty] | 2000 | INSIDE/UNDER BUILDING |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | SEE PART G |  | INVESTIGATION OF THE INCIDENT FOUND HIGH PRESSURE GAS HAD ENTERED THE LUBE OIL SYSTEM DUE TO A FAILURE OF THE HIGH PRESSURE GAS SEAL. ONCE THE GAS ENTERED THE LUBE OIL SYSTEM, IT VENTED INTO THE BUILDING AND IGNITED. IT APPEARS THE EXPLOSION OCCURRED IN THE ROOF AREA OF THE BUILDING AND BLEW OUT SECTIONS OF WALL ON THREE SIDES. INSPECTION OF THE COMPRESSOR WHEEL REVEALED THE CAUSE OF THE INCIDENT. AT THE BOTTOM OF THE ROTOR, THERE WAS A PIECE OF METAL LODGED IN THE ROTOR. THE METAL WAS 6 TO 8 INCHES LONG AND APPROXIMATELY 1 INCH IN DIAMETER. IT APPEARS IT WAS LARGE ENOUGH TO HAVE JAMMED THE COMPRESSOR WHEEL CAUSING A CATASTROPHIC FAILURE OF THE GAS SEAL. COMPUTER PRINT OUT SHOWED ALL THE ALARMS FUNCTIONED AND INDICATED THE CHAIN OF EVENTS. BOTH ESD AND ESD II FUNCTIONED IMMEDIATELY, THUS ISOLATING THE COMPRESSOR UNIT FROM THE REST OF THE STATION. THE STATION CONTINUED TO RUN WITHOUT INTERRUPTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030017 | 2003-03-03 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 2100 | 2003-02-02 | 2003 | VIOLA | MERCER | IL | 61486 | MP 689.58 |  | 41.222416 | -90.539819 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962000 | 647887.0419 | 601466.1245 | 917000 | 537659.8291 | 45000 | 63806.2954 | 0 | 0 | NO | YES | NO | YES | 30 | PRECAUTIONARY | 3 | 0 | 635767 | 2003-02-02 | 816 | 975 | NO | NO | YES | NO | NO | NO | KEN CROWL | 8323205462 | KEN_CROWL@TRANSCANADA.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1949 | 24 | 0.31 |  | 52000 | DSAW |  | REPUBLIC | 1949 | UNDER GROUND |  | 96 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 9 | 14 | 1976 | WATER |  | 24 | 1392 | [12 empty] | A LEAK AND SUBSEQUENT RUPTURE AND FIRE OCCURRED ON THE ANR SOUTHWEST MAINLINE (100-0), APPROXIMATELY 5 MILES UPSTREAM OF THE NEW WINDSOR COMPRESSOR STATION, BETWEEN VALVES 44 & 45 APPROXIMATE MP 689.58. INITIAL OBSERVATIONS OF FAILURE HAVE NOT INDICATED ANY SIGNS OF CORROSION, INTERNAL OR EXTERNAL. A DETAILED METALLURGICAL INVESTIGATION IS UNDERWAY. 4-29-03 THE FAILURE OCCURRED DUE TO THE CUMULATIVE EFFECTS OF THE NORMAL OPERATING CONDITIONS IN COMBINATION WITH THE COLD ENVIRONMENT ACTING ON A MAJOR SAG BEND PASSING UNDER A CREEK BED. THE FAILURE INITIATED DUE TO STRESSES CONCENTRATED IN THE PIPE'S DSAW LONGITUDINAL SEAM WHICH COINCIDED WITH THE APEX OF A WRINKLE BEND. THE AMBIENT TEMPERATURES AFFECTED THE PIPE'S MECHANICAL PROPERTIES AS WELL AS CONTRIBUTED TO PIPE CONTRACTION. SATURATED OVERBURDEN ALSO CONTRIBUTED TO THE POTENTIAL FOR FROST HEAVE AND UPWARD BUOYANCY OF THE PIPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030018 | 2003-03-12 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1245 | 2003-02-12 | 2003 |  |  | LA |  | MP 1.54 |  | N 28 DEG 19.2' | W 91 DEG 35.330' | OFFSHORE |  | EUGENE ISLAND | 306 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208500 | 133514.7472 | 285240.9242 | 12500 | 7329.0598 | 196000 | 277911.8644 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 636636 | 2003-02-12 | 844 | 1300 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 16 | 0.38 |  | 52000 |  |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1978 | NO | [57 empty] | THE LEAK OCCURRED ON ANR 16" LINE 607, IN EUGENE ISLAND BLK 306, GULF OF MEXICO, OFFSHORE LOUISIANA, AND WAS DISCOVERED NEAR A FIELD JOINT. IT WAS APPARENTLY DUE TO DAMAGE FROM INTERNAL CORROSION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030019 | 2003-02-26 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35203 | 1500 | 2003-01-28 | 2003 | MCADAMS | ATTALA | MS |  | 140.396 |  | 32 DEG. 56' 36.1 | 89 DEG. 41' 15.5 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56000 | 36866.4747 | 54039.8067 | 30500 | 17882.906 | 25500 | 36156.9007 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 635310 | 2003-01-28 | 354 | 500 | NO | NO | YES | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | MECHANICAL (DRESSER) COUPLING | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 22 | 0.25 |  | 35000 | FUSION WELD |  |  |  | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | LEAKING MECHANICAL | [6 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | LEAK DISCOVERED ON SOUTHERN NATURAL GAS' NORTH MAIN LOOP LINE, APPROXIMATE MP 140.396. HUNTER OBSERVED SWIRLING WATER IN SWAMPY AREA, IN VICINITY OF SOUTHERN'S PIPELINE. LEAK WAS FOUND TO BE LOCATED AT A MECHANICAL COUPLING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030020 | 2003-02-28 | ORIGINAL | 7605 |  | HOUSTON PIPELINE CO | 1201 LOUISIANA SUITE 1201 | HOUSTON | HARRIS | TX | 77002-5600 | 2045 | 2003-01-18 | 2003 | HOUSTON | HARRIS | TX |  | 4069+76 |  | 29.980383702 | 95.565841206 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173900 | 111338.8527 | 238343.1142 | 9900 | 5804.6154 | 14000 | 19850.8475 | 150000 | 212687.6513 | NO | NO | NO | NO | 0 |  | 0 | 45 | 634461 | 2003-01-18 | 900 | 1080 | NO | YES | NO | NO | NO | NO | ELIZABETH S. BUSH-IVIE | 8326681258 | ESBUSH-IVIE@AEP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 6 | 0.22 | 460000 |  | ERW |  |  |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | SEWER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | A CALL WAS RECEIVED IN HPL GAS CONTROL AT APPROXIMATELY 8:45 PM THAT A PIPELINE RUPTURE HAD OCCURRED. THE NOTICE WAS MADE BY A PERSON FAMILIAR WITH THE PIPELINE INDUSTRY THAT HAPPENED TO BE IN A NEARBY BUSINESS AND CALLED THE EMERGENCY NUMBER ON THE NEAREST PIPELINE MARKER. MORE THAN ONE COMPANY'S PIPELINE RUNS IN THE AREA. HPL PERSONNEL WERE NOTIFIED AND HEADED TOWARD THE SITE. AT ABOUT 9:00, PER GAS CONTROL, A PRESSURE DROP ON OUR PIPELINE WAS OBSERVED. HPL PERSONNEL ARRIVED IN THE AREA ABOUT 9:15 PM AND BASED ON VISUAL OBSERVATIONS AND THE INFORMATION FROM GAS CONTROL TOOK IMMEDIATE ACTION TO SHUT THE VALVES AND ISOLATE THE LEAK. ISOLATION OCCURRED AT APPROXIMATELY 9:30 PM. NO FIRE OCCURRED AND THE GAS QUICKLY DISSIPATED. THE SITE WAS SECURED, EXCAVATED AND 16' OF PIPE WAS REPLACED. REPAIRS WERE COMPLETED AT APPROXIMATELY 8:45 AM THE NEXT MORNING, JANUARY 19, AND SERVICE WAS RESTORED TO THE DISTRIBUTION COMPANY. UPON EXCAVATION OF THE SITE IT BECAME APPARENT THAT THE CAUSE OF THE RUPTURE WAS THIRD PARTY DAMAGE THAT OCCURRED AT SOME INDETERMINATE TIME IN THE PAST. THERE ARE VISUAL, OLD NOT FRESH, TEETH MARKS AND DENTS ON THE PIPE AND DAMAGE TO THE PROTECTIVE COATING. SEVERAL 4" PVC LINES WERE ENCOUNTERED WHEN EXCAVATING THE SITE. ONE WAS A GRAY WATER/SEWAGE LINE FROM A NEARBY RESTAURANT THAT CROSSED OVER AND WAS ONLY A FEW INCHES ABOVE THE HPL NATURAL GAS PIPELINE. A SUBSEQUENT REVIEW OF THE RECORDS DURING THE TIME OF CONSTRUCTION OF THE RESTAURANT SHOWS THAT NO ONE-CALLS WERE RECEIVED. THE RUPTURE OCCURRED IN A CLASS 3 AREA NEAR COMMERCIAL ESTABLISHMENTS. SEVERAL VEHICLES WERE DAMAGED. NO INJURIES WERE REPORTED OR OBSERVED AT THE TIME OF THE INCIDENT. SERVICE TO LOCAL DISTRIBUTION COMPANY CUSTOMERS WAS DISRUPTED. SITE CLEAN-UP WAS COMPLETED THE NEXT DAY, JANUARY 19, AND NEARBY BUSINESSES WERE ABLE TO RE-OPEN.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030021 | 2003-03-04 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 1503 | 2003-02-14 | 2003 | LAMONT | GRANT | OK |  |  | 1443+10 | W097-63675 | N36.62803 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74000 | 48556.8449 | 74988.564 | 36000 | 21107.6923 | 37000 | 52462.954 | 1000 | 1417.9177 | NO | NO | YES | NO | 0 |  | 2 | 27 | 636878 | 2003-02-14 | 720 | 800 | NO | YES | NO | NO | NO | NO | MITCHELL L. REDDING | 4055562412 | MICKY.REDDING@CENTERPOINTENERGY.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 12 | 0.19 | X-52 | 66000 | ERW |  | YOUNGS TOWN STEEL AND TUBE COMPANY | 1961 | UNDER GROUND |  | 33 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1963 | NO | [57 empty] | LAB ANALYSIS PERFORMED BY BATETELLE INDICATED THAT THE CONTRIBUTING FACTOR WHICH LEAD TO THE INCIDENT, WAS SELECTIVE SEAM CORROSION. THE FINAL REPORT AND A SUMMARY OF THE EVALUATIONS PERFORMED TO SATISFY THE COMPLIANCE ORDER, HAVE BEEN SENT TO YOUR OFFICE FOR REVIEW, IN A SEPARATE MAILING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030022 | 2003-03-12 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1137 | 2003-02-10 | 2003 | SILVER BAY | LAKE | MN | 55641 | MP 62.4 ON MNB72701 |  | 47 DEG 16.51' | 91 DEG 16.66' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1416222 | 927146.1672 | 1483166.4796 | 631222 | 370101.1043 | 750000 | 1063438.2567 | 35000 | 49627.1186 | NO | YES | NO | NO | 0 |  | 0 | 45 | 636496 | 2003-02-11 | 813 | 832 | NO | NO | NO | NO | YES | NO | PATRICK L. VAUGHAN | 4023987185 | PAT.VAUGHAN@NNGCO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 16 | 0.22 | API 5LX | 52000 | ERW |  | REPUBLIC STEEL | 1961 | UNDER GROUND |  | 58 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | DISCOLORATION | GALVANIC |  | YES | 1961 | NO | [57 empty] | FAILURE OCCURRED DUE TO STRESS CORROSION CRACKING IN THE HEAT AFFECTED ZONE OF THE LONGITUDINAL WELD. COATING DAMAGE ALLOWED CONDITIONS FOR SCC TO DEVELOP. NO SCC WAS FOUND IN THE PIPE BODY. LACK OF SNOW COVER ALLOWED VERY COLD SOIL TEMPERATURE AT PIPE DEPTH CONTRIBUTING TO PROPOGATION OF BRITTLE FRACTURE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030023 | 2003-03-18 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1800 | 2003-02-20 | 2003 | CAPE GIRARDEAU | SCOTT | MO |  | 448.07 | 23657+48 | N 37.2496057 | W 89.4636912 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3263000 | 2082236.4407 | 4626665.3753 | 0 | 0 | 3263000 | 4626665.3753 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 637392 | 2003-02-20 | 795 | 800 | NO | NO | YES | NO | NO | NO | DWAYNE E. TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1943 | 24 | 500 | API-5L | 37000 | SEAMLESS |  | NATIONAL TUBE | 1943 | UNDER WATER |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1951 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030024 | 2003-03-19 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1330 | 2003-02-19 | 2003 | HENDERSON | MASON | WV | 25550 |  | 1861+92 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475000 | 303587.2265 | 662906.4234 | 12752 | 7476.8137 | 462248 | 655429.6097 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 637230 | 2003-02-19 | 125 | 150 | NO | YES | NO | NO | NO | NO | CHRIS LEGG, ENGINEER, PIPELINE SAFETY/SYSTEM INTEGRITY | 3043573227 | CLEGG@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | 0.38 | API-5L-GRADE B | 35000 | ERW | N/A | UNKNOWN |  | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | AT APPROXIMATELY 1:30 P.M. ON FEBRUARY 19, 2003, COLUMBIA GAS TRANSMISSION CORPORATION'S (COLUMBIA) PIPELINE SM-90 (8") WAS DISCOVERED TO BE RELEASING GAS INTO THE KANAWHA RIVER. THE GAS RELEASE WAS DISCOVERED BY A RIVER BOAT EMPLOYEE. HE WAS TRAVELING IN A TUG-BOAT THAT WAS APPROACHING SEVERAL NEAR-BY, LOADED COAL BARGES PARKED NEAR AND OVER THE SM-90 PIPELINE. DURING THIS APPROACH, HE NOTICED THE WATER "BOILING", AS WELL AS COLUMBIA'S RIVER CROSSING SIGN ON THE ADJANCENT RIVER BANK. HE THEN BACKED THE TUG UP AND NOTIFIED COLUMBIA. THE PIPELINE WAS OPERATING AT 125 PSIG AT THE TIME OF THE RUPTURE. THE RUPTURE OCCURRED APPROXIMATELY 25 FEET INTO THE KANAWHA RIVER BETWEEN THE CITY OF POINT PLEASANT, WV AND THE COMMUNITY OF HENDERSON, WEST VIRGINIA, BOTH IN MASON COUNTY. SM-90 CROSSES THE KANAWHA RIVER AT THE 1.1 MILE MARK, DECENDING. NO DEATHS OR INJURIES RESULTED FROM THE INCIDENT. A COLUMBIA FIELD EMPLOYEE WAS WORKING AT A NEAR-BY PIPELINE FACILITY WHEN HE NOTICED THE PRESSURE DROP AND ACTED PROMPTLY TO ISOLATE THE RUPTURED PIPELINE SECTION. THE RIVER BOAT COMPANY NOTIFIED THE U.S. COAST GUARD, WHO CLOSED THE RIVER TO BOAT-TRAVEL FROM THE ZERO MILE MARKER TO THE THREE MILE MARKER. THEY ALSO ISSUED A "PROCEED WITH CAUTION" ORDER FOR THE OHIO RIVER. BY 3:15 P.M., THE LINE WAS ISOLATED AND THE RIVER WAS RE-OPENED FOR TRAVEL. THE CAUSE OF THE RUPTURE IS STILL UNDER INVESTIGATION AND IS STILL UNKNOWN. COLUMBIA CUT AND CAPPED SM-90 NEAR THE RIVER CROSSING ON ONE SIDE SEVERAL DAYS AFTER THE INCIDENT. THE OPPOSITE SIDE IS ISOLATED BY A VALVE, WHICH IS CHAINED AND LOCKED. THE PIPELINE WILL REMAIN OUT OF SERVICE UNTIL ARRANGEMENT ARE MADE TO INVESTIGATE THE CAUSE OF THE INCIDENT AND REPAIR OR REPLACE THE DAMAGED PIPELINE SECTION.6-14-04 FAILURE ANALYSIS COLUMBIA UTILIZED THE SERVICES OF CROFTON DIVING CORPORATION (CROFTON) TO PROVIDE PROFESSIONAL ASSISTANCE DURING THE PIPELINE RUPTURE INVESTIGATION. ON APRIL 29, 2003, CROFTON CONDUCTED AND UNDERWATER INVESTIGATION. IN THEIR MAY 6, 2003 UNDERWATER ASSESSMENT REPORT, CROFTON RECORDED THEIR OBSERVATIONS OF THE PIPELINE AND RIVER BOTTOM CONDITION. (SEE ATTACHMENTS A, B, AND C FROM THIS REPORT). THEY FOUND THE PIPELINE TO BE EXPOSED FROM 2.5' TO 24.5' FROM THE EDGE OF WATER (22'IN TOTAL LENGTH). IN ADDITION, THE PIPELINE HAD BEEN COMPLETELY SERVERED AND HAD SUFFERED OTHER EXTENSIVE DAMAGE. THEY NOTED THE TOP OF THE PIPE HAD BEEN DISTORTED OR FLATTENED TO VARIED DEGREES WITH THE MAXIMUM DEPTH OF DEPRESSION APPROXIMATELY 4". THEY ALSO REPORTED NUMEROUS FRESH SCRAPE MARKS TO THE PIPELINE AND IT'S COATING (COAL TAR) IN THIS SECTION INDICATING RECENT BARGE-RELATED DAMAGE DUE TO THEIR BARGE GROUNDING ACTIVITIES. THE RIVER BOTTOM TOPOGRAPHY HAD REPORTEDLY BEEN ALTERED DUE TO OUTSIDE FORCES RESULTING IN THE 22' OF EXPOSED PIPELINE. THIS SECTION WAS NOT EXPOSED ON OCTOBER 8, 2202, WHEN CROFTON PERFORMED THEIR ROUTINELY SCHEDULED PIPELINE RIVER CROSSING SURVEY. BASED ON THE EVIDENCE AND SUPPORTED BY CROFTON'S UNDERWATER CONDITION ASSESSMENT, COLUMBIA HAS CONCLUDED THE CAUSE OF INCIDENT WAS OBIVIOUSLY A STRIKE FROM A RIVER BARGE THAT HAD BEEN GROUNDED INTO RIVER BOTTOM SLOPE AND OUR PIPELINE. FURTHERMORE, SCOURING OF THE RIVER BOTTOM HAD OCCURRED EITHER PRIOR TO OR DURING THE MOST RECENT GROUNDING EVENT. THE PIPELINE WAS REPAIRED BY REPLACING THE DAMAGED PIPE SECTION, BACKFILLING WITH SELECT MATERIAL AND THEN PLACING A FLEXIBLE CONCRETE ARTICULATING MAT OVER THE REPAIR AREA. THIS MAT IS INTENDED PROTECT THE PIPELINE FORM FUTURE UNDERMINING AND DAMAGE. (SEE ATTACHMENT D AND E FROM THIS REPORT) COLUMBIA HAS CONTACTED THE US COAST GUARD ABOUT THE UNSAFE GROUNDING PRACTICES THAT HAVE OCCURRED AT OUR PIPELINE CROSSING LOCATION. COLUMBIA IS ALSO IN THE PROCESS OF CONTACTING THE TUGBOAT COMPANY(S) TO INFORM THEM OF THE DANGERS AND LIABILITIES OF THESE GROUNDING ACTIVITIES IN CLOSE PROXIMITY TO GAS PIPELINE FACILITIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030025 | 2003-03-24 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 9 GREENWAY PLAZA | HOUSTON | HOUSTON | TX | 77046 | 1330 | 2003-02-20 | 2003 | DEMING | LUNA | NM | 88030 | LINE 2000 MP 736+4269.4 |  | N 32 DEG 14' 10" | W 107 DEG 39' 4.7" | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE |  |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129400 | 86912.8814 | 86182.1792 | 117000 | 68600 | 12400 | 17582.1792 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 637361 | 2003-02-20 | 700 | 944 | YES | NO | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 30 | 0.28 | API 5LX | 70000 | SPIRAL WELD SEAM |  | BERG-RUHR | 1986 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 8 | 17 | 2002 | WATER |  | 8 | 1245 | [12 empty] | AT APPROXIMATELY 1:30 P.M. MST, A NON-HAZARDOUS LEAK ON LINE 2000 WAS FOUND IN LUNA COUNTY, NEW MEXICO, FIVE MILES EAST OF DEMING, DURING A SCHEDULED LEAK SURVEY. AFTER FURTHER INVESTIGATION, LACK OF FUSION IN THE GIRTH WELD WAS IDENTIFIED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030026 | 2003-03-21 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 9 GREENWAY PLAZA | HOUSTON | HOUSTON | TX | 77046 | 1300 | 2003-02-20 | 2003 | DEMING | LUNA | NM | 88030 | LINE 1103 MP 284+1745 |  | N 32 DEG 14' 10" | W 107 DEG 39' 47.6" | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123230 | 82827.2724 | 80759.9987 | 113000 | 66254.7009 | 10230 | 14505.2978 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 637356 | 2003-02-20 | 700 | 809 | YES | NO | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 30 | 0.32 |  | 52000 | DSAW |  | REPUBLIC | 1950 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | NO | [19 empty] | AT APPROXIMATELY 1:00 P.M. MST. A NON-HAZARDOUS LEAK ON LINE 1103 WAS FOUND IN LUNA COUNTY, NEW MEXICO, FIVE MILES EAST OF DEMING, DURING A SCHEDULED LEAK SURVEY. FOLLOWING A METALLURGICAL INVESTIGATION, A CLUSTER OF POROSITY WAS FOUND IN THE LONG SEAM. THE LEAK RESULTED FROM THE INTERSECTION OF A WORM-HOLE PORE WITH THE FINISH PASS CRACK.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030027 | 2003-02-28 | ORIGINAL FINAL | 11680 |  | TXU LONE STAR PIPELINE | 301 SOUTH HARWOOD STREET | DALLAS | DALLAS | TX | 75201-5696 | 1439 | 2003-02-02 | 2003 | MCKINNEY | COLLIN | TX | 75070 |  | 289+97 ON LINE D9-2-1 | N 33 12 245 | W 096 42 944 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 37372 | 24228.4537 | 44466.5923 | 10250 | 6009.8291 | 27122 | 38456.7632 | 0 | 0 | NO | YES | NO | NO | 0 |  | 2 | 45 | 635764 | 2003-02-02 | 390 | 500 | NO | NO | NO | NO | YES | NO | GARY WOOLSEY | 2148752706 | GWOOLSY1@ONCORGROUP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 12 | 0.28 | GR A | 30000 | LAP WELD |  | UNKNOWN |  | UNDER GROUND |  | 54 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DEVELOPER | NO |  |  |  |  | YES | STAKES | YES | ACCURATE | YES | [36 empty] | DURING THE EXCAVATION OF A DRAINAGE DITCH FOR A RETENTION POND BELONGING TO A DEVELOPER, THE DEVELOPER'S CONTRACTOR BACKHOE OPERATOR TRUCK THE PIPELINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030028 | 2003-04-09 14:23 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION INC | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 2220 | 2003-03-09 | 2003 | MARIANNA | WYOMING | WV | 24818 |  | 2495+63 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 26 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62800 | 40816.4769 | 72413.3722 | 20000 | 11726.4957 | 22800 | 32328.523 | 20000 | 28358.3535 | NO | YES | NO | NO | 0 |  | 0 | 25 | 638957 | 2003-03-10 | 636 | 680 | NO | NO | NO | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C_SCHWOEBLE@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 12 | 0.31 |  |  | ERW | N/A |  |  | UNDER GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | GALVANIC |  | NO |  | NO | [57 empty] | RURAL AREA. INITIALLY INSTALLED IN 1946. ROCKY SOIL AND WET WEATHER UNDERGROUND SPRING RUNNING ON/NEAR PIPE. HOT SPOT ANODE PROTECTED.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20030029 | 2003-03-27 | ORIGINAL | 3469 |  | DOMINION PIPELINE CO | 1301 TRAVIS SUITE 1210 | HOUSTON | HARRIS | TX | 77002 |  | 2002-12-18 | 2002 |  | NUECES | TX | [5 empty] | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 | [5 empty] | 100 | 989 | NO | NO | NO | NO | NO |  | JOE H. HAVELKA | 3618842901 |  | GATHERING | BODY OF PIPE |  |  |  | NO | NO | NO | PIPELINE |  |  | 2.84 | 0.16 | 5LX42 | [5 empty] | OPEN DITCH |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | PHONE/CABLE |  | NO |  |  |  |  | NO | [40 empty] | CONTRACTOR HIT PIPELINE WHILE RIPPING IN A TELEPHONE CABLE ALONG COUNTY ROAD 46 IN NUECES COUNTY. CONTRACTOR SAID THEY SENT ONE CALL. DOMINION DID NOT RECIEVE A ONE=CALL ON FAX.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030030 | 2003-03-28 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO (ENRON) | PO BOX 1188 | HOUSTON | HARRIS | TX | 77251 | 1730 | 2003-03-05 | 2003 | DICKINSON | GALVESTON | TX |  | 297.76 | 2742+37 | 29.25434N | 95.06807W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99970 | 65722.4755 | 98506.3998 | 52000 | 30488.8889 | 46410 | 65805.5593 | 1560 | 2211.9516 | NO | NO | NO | NO | 0 |  | 0 | 0 | 638615 | 2003-03-05 | 798 | 975 | NO | NO | NO | NO | YES | NO | MERLIN MOSEMAN, PIPELINE INTEGRITY ENGINEER | 7133451625 | MERLIN.MOSEMAN@ENRON.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 22 | 0.28 | API5LX | 52000 | DSA |  | KANE |  | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | YES | 5 | 17 | 1959 | WATER |  | 2 | 1150 | [12 empty] | THIS PIPELINE SEGMENT WAS INSPECTED IN 1999 USING A HIGH RESOLUTION MAGNETIC FLUX LEAKAGE TOOL AND IN NOVEMBER 2002, WITH A HIGH RESOLUTION CIRCUMFERENTIALLY ORIENTED MAGNETIC FLUX (TFI) TOOL WITH NO INDICATION BY EITHER DEVICE OF AN ANOMALY AT THE LEAK LOCATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030031 | 2003-03-23 | ORIGINAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET #1000 | HOUSTON | HARRIS | TX | 77002 | 2050 | 2003-03-10 | 2003 | RATLIFF CITY | CARTER | OK | 73481 | OE 256 |  | N 34 27' 51 | W 97 31' 53 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71148 | 48040.1026 | 41715.8359 | 71148 | 41715.8359 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 5 | 639161 | 2003-03-11 | 968 | 1050 | YES | NO | NO | NO | NO | NO | REBECCA VOSS FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1990 |  |  |  | 0 |  |  |  |  | OTHER | PSV IN COMP. STATION YARD |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030032 | 2003-03-31 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | ONE WILLIAMS CENTER | TULSA | TULSA | OK | 74101 | 1400 | 2003-03-03 | 2003 | TERREBONNE |  | LA |  | 125.824 | 6643+51 | 29.1949 | 91.8173 | OFFSHORE |  | N/A | N/A | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299000 | 191321.6355 | 412315.0845 | 14000 | 8208.547 | 285000 | 404106.5375 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 10 | 638348 | 2003-03-03 | 659 | 1169 | NO | NO | NO | NO | YES | NO | JOSEPH F. FREISBERG SR. | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 30 | 0.41 |  | 60000 | DSAW |  | US STEEL | 1964 | UNDER WATER |  | 120 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER |  | YES | 1964 | NO | [57 empty] | BUBBLING ACTIVITY WAS NOTICED BY EMPLOYEES IN THE PIPELINE GENERAL LOCATION. UPON INVESTIGATION A PINHOLE LEAK WAS DISCOVERED IN THE 30-INCH SELA "B" LINE. THE PINHOLE WAS LOCATED AT THE SIX O'CLOCK POSITION, A REPAIR CLAMP WAS INSTALLED.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030033 | 2003-04-01 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET #1000 | HOUSTON | HARRIS | TX | 77002 | 2100 | 2003-03-11 | 2003 | COLUMBUS JUNCTION | LOUISA | IA | 52638 |  |  | N 41 12' 44 | W 91 20' 34 | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 10 | 639182 | 2003-03-21 | 14 | 1050 | NO | YES | YES | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | TANK | STEEL |  | NO | NO | NO | OTHER | WASTE WATER TANK |  |  |  |  | 0 |  |  |  |  | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 8 |  |  | ON TUESDAY NIGHT AT APPROXIMATELY 9:00 PM, A DRIVER FOR THE WATER-HAULING CONTRACTOR (EMS, INC) WAS BURNED BY A FIELD TANK, WHILE WORKING AT A KINDER MORGAN STORAGE FACILITY LOCATE IN COLUMBUS JCT, 1A (STATION 204). THE CONTRACTOR WAS DRAINING ON TANK AND WHILE THAT TANK WAS DRAINING HE ATTEMPTED TO USE A PROPANE TORCH TO THAW A VALVE IN PREPARATION FOR DRAINING ANOTHER TANK. THE CONTRACTOR HAD NOT HOOKED HIS DRAIN HOSE TO THE SECOND TANK AS IT WAS BEING USED AT THE OTHER TANK. A KINDER MORGAN EMPLOYEE WITNESSED FLAMES ERUPT FROM A 3" DRAIN VALVE DURING THE THAWING PROCESS. THE FIRE OCCURRED AS A RESULT OF THE CONTRACTOR OPENING THE VALVE ON THE TANK WHILE USING THE TORCH. THIS ALLOWED A PATH FOR AN IGNITION SOURCE TO ENTER THE TANK AND ALSO CAUSED A SMALL RELEASE OF LIQUID WHICH WAS IGNITED BY THE TORCH. FAILING TO HOOK UP THE HOSE TO THE SECOND TANK BEFORE ATTEMPTING TO THAW THE VALVE IS AGAINST ACCEPTED PRACTICE. AND OPENING UP THE VALVE WHILE USING THE TORCH IS A VIOLATION AGAINST THE PROCEDURE SET OUT IN OM 103 - HOT WORK AND AGAINST PROCEDURES REVIEWED IN THE KINDER MORGAN CONTRACTOR SAFETY PROGRAM. UPON EXTINGUISHING THE FIRE AT THE VALVE, THE CONTRACTOR CLAIMS THAT HE HEARD A RUMBLING INSIDE THE TANK, AND HE CLIMBED THE LADDER AND OPENED THE THIEF HATCH TO INVESTIGATE. THE CONTRACTOR WAS BURNED AFTER HE OPENED THE THEIF HATCH AND WAS EXPOSED TO THE INTENSE HEAT BUILT UP FROM PROBABLE TANK FIRE. THIS HEAT ESCAPED FROM THE HATCH AND CAUSED 1ST AND 2ND DEGREE BURNS ON HIS FACE AND LEFT HAND. THE DRIVER WAS ADMITTED TO A LOCAL HOSPITAL FOR OBSERVANCE AND MEDICATED FOR PAIN.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030034 | 2003-04-02 | SUPPLEMENTAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1105 | 2003-03-02 | 2003 |  |  |  |  | MILE POST 49.2 |  | 27.59 N | 94.40 W | OFFSHORE |  | HIGH ISLAND | 555 |  | YES | NO | INTERSTATE | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 675.2137 | 586.3248 | 1000 | 586.3248 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 28 | 8 | 638250 | 2003-03-02 | 890 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 8326765459 | JIM.MCDONALD@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE | [10 empty] | UNDER WATER |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | ON MARCH 2, 2003, AT 11:52 AM, A LEAK REPORT WAS CALLED INTO THE NRC IN BLOCK HIA 555. DURING A ROUTINE FLYOVER, OUR HELICOPTER PILOT HAD NOTICED BUBBLING AT THE OCEAN SURGACE OVER OUR HIOS PIPELINE. EL PASO FIELD SERVICES OPERATES SEVERAL PIPELINES IN THE AREA OF THE LEAK. FURTHER INVESTIGATION IDENTIFIED THE AREA AS A LOCATION WHERE OUR HIA 531 LATERAL AND OUR HIA 557 LATERAL INTERCONNECT WITH OUR HIA 20" PIPELINE. WE PROCEEDED TO SHUT IN PRODUCTION ON THE HIA 557 LATERAL TO DETERMINE IF PRESSURE ON THE LATERAL SYSTEM WOULD DROP. IT DID NOT. ON MARCH 3, 2003 WE PROCEEDED TO SHUT IN ALL OTHER PRODUCTION IN THE AREA TO PREVENT THE CONTINUANCE OF GAS LOSS. THIS WAS COMPLETED BY 4:00 PM. A DIVE VESSEL WITH AN ROV WAS MADE AVAILABLE ON MARCH 5, 2003. THE DIVE TEAM IDENTIFIED TWO LEAKS AT THE SUBSEA TIE IN. ONE WAS A STEM LEAK ON THE HIOS 20" CHECK VALVE WHICH WE REPAIRED AND THE OTHER WAS A GASKET LEAK ON 20" RTJ 900 SERIES SWIVEL FLANGE ON THE HIA 531 INTERCONNECT WHERE WE FOUND THAT THE FLANGE HAD BEEN IMPROPERLY TORQUED. WE MADE THE NECESSARY REPAIRS AND RETURNED THE PIPELINES TO SERVICE ON MARCH 5, 2003 AT 10:00 PM. THE GAS LOSS AND THE DAMAGE TO MATERIAL WAS MINIMAL. HOWEVER, THE COST TO MAKE THE SUBSEA REPAIR WAS $208.000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030035 | 2003-04-21 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1937 | 2003-03-23 | 2003 | MITCHELL | LAWRENCE | IN | 47446 | MP676.7/BETWEEN MLV 53 AN | 6 | 38.7338 | -86.5127 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174000 | 117487.1795 | 102020.5128 | 174000 | 102020.5128 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 640296 | 2003-03-23 | 680 | 858 | NO | YES | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1999 | 36 | 0.4 |  | 65000 | DSAW |  | ITALSIDER | 1973 | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 12 | 31 | 1999 | WATER |  | 8 | 1390 | [12 empty] | THERE WAS A LEAK ON THE 2-501 36" MAINLINE BETWEEN MLV 53 & 54, FOLLOWING THE DISCOVERY OF AN ICE FORMATION ON THE SURFACE OF THE RIGHT-OF-WAY. INITIAL DISCOVERY INDICATED A LEAK AND NO FIRE PRESENT. A PARTIAL THROUGH-WALL WELD CRACK, INTRODUCED IN THE IC AREA AT THE TIME OF THE WELD WAS MADE, WAS NOT DETECTED DURING RADIOGRAPHIC INSPECTION IN THE FIELD. A COMBINATION OF AXIAL STRESS AND APPLIED MOMENT, DUE TO MISALIGNMENT OF THE PIPE SECTIONS, OVERLOADED THE GIRTH WELD AND PROPAGATED THE PRE-EXISTING CRACK THROUGH WALL, CAUSING THE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030036 | 2003-04-21 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1935 | 2003-03-23 | 2003 | GREELEY | WELD | CO |  | LINE 5B | 50-242+45 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850000 | 555392.5829 | 914172.513 | 350000 | 205213.6752 | 300000 | 425375.3027 | 200000 | 283583.5351 | NO | YES | NO | YES | 13 | PRECAUTIONARY | 3 | 0 | 640297 | 2003-03-23 | 814 | 850 | NO | YES | NO | NO | NO | NO | LOUIS A. SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 24 | 0.25 | 5LX | 60000 | ERW HIGH FREQ. |  | STUPP, BATON ROUGE, LA | 1978 | UNDER GROUND |  | 120 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | BRANCH |  |  |  | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 4 | 23 | 1978 | WATER |  | 8 | 1124 | [12 empty] | THE 24" 5B PIPELINE, NEAR GREELEY, CO RUPTURED. ESCAPING GAS WAS IGNITED AND CONTINUED TO BURN UNTIL THE PIPELINE SEGMENTS ON BOTH 5A AND 5B WERE ISOLATED AND THE RESIDUAL GAS WAS EXHAUSTED. A COMPANY OWNED METER STATION WAS DESTROYED. APPARENTLY, A 4-IN BRANCH LINE FAILED AT A SADDLE CONNECTION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030037 | 2003-04-15 | SUPPLEMENTAL FINAL | 792 |  | ATLANTA GAS LIGHT CO | 2695 OLD PEACHTREE ROAD | DULUTH | GWINNETT | GA | 30097 | 1025 | 2003-03-12 | 2003 | BUFORD | GWINNETT | GA | 30518 | BET MM #2 & #3 | N/A |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE |  |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55556 | 36412.2867 | 57242.2313 | 25892 | 15181.1214 | 29664 | 42061.1099 | 0 | 0 | NO | NO | NO | YES | 2 | PRECAUTIONARY | 7 | 50 | 639220 | 2003-03-12 | 235 | 720 | YES | NO | NO | NO | NO | NO | CHARLES CLEMENT, OPERATIONS SUPERVISOR | 7704182260 | CCLEMENT@AGLRESOURCES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 16 | 0.25 | API 5L-X52 | 52000 | UNKNOWN | N/A | UNKNOWN |  | UNDER GROUND |  | 56 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | HOME BUILDER | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | A CONTRACTOR EXCAVATING FOR A NEW BASEMENT PUNCTURED THE PIPELINE WITH A FRONT END LOADER.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20030038 | 2003-02-28 | ORIGINAL | 30691 |  | COPANO GATHERING SYSTEM, INC | 1300 POST OAK BLVD SUITE 1750 | HOUSTON | HARRIS | TX | 77056 | 1655 | 2003-01-17 | 2003 | HOUSTON | HARRIS | TX |  | MILEPOST 8.5 |  | 30.1227646 | -95.5542145 | ONSHORE | 2 |  |  |  |  | NO | INTRASTATE | LEAK |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 29327.89 | 50085.0127 | 16500 | 9674.359 | 28500 | 40410.6538 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 15 |  | 2003-01-17 | 850 | 1000 | NO | NO | NO | NO | NO | NO | K S DEYOUNG | 7136219547 |  | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 6 | 0.22 | GRB | 2314 | SEAMLESS | N/A | UNKNOWN |  | UNDER GROUND |  | 24 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | YES | 11 | 6 | 2002 | CONTRACTOR | YES | FLAGS | NO | ACCURATE | YES | [36 empty] | N/A
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030039 | 2003-04-30 17:11 | ORIGINAL | 844 |  | KERN RIVER GAS TRANSMISSION CO (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1710 | 2003-04-03 | 2003 |  | LINCOLN | WY | 83101 | MP 0/MUDDY CREEKC/S | SERIES 100, STA NO 0+00 | 41.6902955255 | -110.3610579208 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | NONE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123000 | 78490.678 | 174403.8741 | 0 | 0 | 123000 | 174403.8741 | 0 | 0 | NO | YES | NO | NO | 0 |  |  | 15 | 641289 | 2003-04-03 | 1100 | 1200 | NO | YES | NO | NO | NO | NO | VON MCALLISTER | 8015846851 | VON.MCALLISTER@KERNRIVERGAS.COM | TRANSMISSION | OTHER | NONE |  |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | STATIC ELECTRICITY. STATION WAS STILL UNDER CONSTRUCTION. VENT STACK GROUNDING WAS NOT COMPLETE. |  | ON APRIL 3, 2003 AT 1710 HRS, AN INTENTIONAL EMERGENCY SHUT DOWN (ESD) WAS INITIATED AT THE MUDDY CREEK COMPRESSOR STATION "B" PLANT, DURRING THE COMMISSIONING PROCESS. THIS IS A NEW STATION, CURRENTLY UNDER CONSTRUCTION, WHICH IS NOT YET IN SERVICE. THE ESD SYSTEM WAS USED TO BLOW DOWN THE STATION PIPING AT THE END OF THE WORK DAY. THE GAS DISCHARGING FROM THE VENT STACK IGNITED APPROXIMATLY 5 SECONDS INTO THE BLOW DOWN. THE FLAME WAS OBSERVED TO EMERGE FROM WITHIN THE STACK. THE GAS CONTINUED TO VENT AND BURN FOR APPROXIMATELY 15 MINUTES. THE WIND WAS VERY STRONG, AND KEPT THE GAS FIRE CLOSE TO THE GROUND, AND DIRECTED TO THE EAST. THE FIRE CONSUMED OR DAMAGED A MAN-LIFT CRANE, TWO TRASH DUMPSTERS, AND SOME VALVES AND OTHER MATERIALS STORED ON PALLETS. A SMALL GRASS AND BRUSH FIRE WAS ALSO STARTED. THE IGNITION IS BELIEVED TO HAVE BEEN CAUSED BY STATIC ELECTRICITY. THE STATIC BUILD UP MIGHT HAVE BEEN PREVENTED IF THE GROUNDING OF THE BLOW DOWN STACK HAD BEEN COMPLETED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030040 | 2003-04-28 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1540 | 2003-04-02 | 2003 | GULF MEXICO |  | LA |  | MP 509A-401+1.00 |  | Y=67,758 | X=1,583,192 | OFFSHORE |  | EAST CAMERON | 271 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187311 | 119615.5035 | 263669.7666 | 2311 | 1354.9966 | 185000 | 262314.77 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 641156 | 2003-04-02 | 740 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 16 | 0.38 |  | 52000 | SMLS |  | USS | 1973 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDETERMINED | YES | 1973 | NO | [57 empty] | THE LEAK OCCURRED ON TGP LINE 509A-400, NEAR MP 509A-401 + 1.00, IN EAST CAMERON BLOCK 271, GULF OF MEXICO. THE LEAK WAS DUE TO INTERNAL CORROSION. THE LEAK WAS REPAIRED BY INSTALLING A 16" PLIDCO REPAIR CLAMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030041 | 2003-04-25 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA, | HOUSTON | HARRIS | TX | 77046-2002 | 1600 | 2002-09-01 | 2002 | FARMERVILLE | UNION | LA | 71241 | 278.25 | 1729+47 | 32 41.829' | 92 23.057' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE | [5 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99141 | 79431.079 | 113439.0639 | 48587 | 40449.8568 | 50554 | 72989.2071 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 20 | 621690 | 2002-09-01 | 330 | 470 | NO | NO | NO | NO | YES | NO | SCOTT TOWNSEND | 3186652125 | SCOTT.TOWNSEND@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1928 | 18 | 0.28 |  | 33000 | ELECTRIC FLASH WELD |  | UNKNOWN | 1928 | UNDER GROUND |  | 12 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | EROSION | YES |  | NO | [57 empty] | ALTHOUGH WE FOUND NO INTERNAL CORROSION OR EXTERNAL PITTING OR CORROSION, THE WALL OF THE PIPE HAD BEEN GREATLY REDUCED. WE SENT THE PIPE TO A METALLURGIST TO DETERMINE WHY THIS THINNING OF THE PIPE OCCURRED. 7-29-03 THE INITIAL REPORT ON THIS INCIDENT WAS SENT ON 9/27/02. A SUBSEQUENT REPORT WAS SENT ON 1/3/03 FOLLOWING A METALLURGICAL STUDY. WE THEN RESENT THE REPORT ON 4/23/03 USING THE NEW FORM. THIS REPORT IS SENT TO ADD REQUESTED DATA THAT WAS LEFT OFF OF THE EARILER REPORTS. PLEASE NOTE THAT WE HAVE UPDATED A COUPLE OF ITEMS INCLUDING THE FINAL COST OF THE INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030042 | 2003-05-01 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 610 | 2003-04-02 | 2003 | PLAYA DEL REY | LOS ANGELES | CA | 90293 |  |  | 33.9619560 | -118.4375839 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500000 | 1596451.3255 | 3519846.4022 | 30000 | 17589.7436 | 75000 | 106343.8257 | 2395000 | 3395912.8329 | YES | NO | NO | NO | 0 |  | 0 | 25 | 641136 | 2003-04-02 | 20 | 60 | YES | NO | NO | NO | NO | NO | JEFF KOSKIE | 2132443283 | WKOSIE@SEMPRAUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1970 | 0.75 | [7 empty] | ABOVE GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | OTHER | ATMOSPHERIC | NO |  | NO | [57 empty] | ATMOSPHERIC CORROSION LEAK LOCATED ON INSTRUMENT GAS SUPPLY LINE RESULTED IN UNPLANNED EMERGENCY SHUT DOWN (ESD). DURING THE ESD PROCESS, ONE OF THE INVOLVED VALVES WAS NOT CLOSING FULLY DURING AUTOMATIC SHUTDOWN, AND HAD TO BE CLOSED MANUALLY. COMPLETE CLOSURE AND EVACUATION OF LINES OCCURRED WITHIN 25 MINUTES. BLOWDOWN RELEASED NATURAL GAS AND LIQUIDS (CRUDE OIL AND WATER) INTO THE ATOMOSPHERE, CAUSING MIST DAMAGE TO NEIGHORING HOMES, LANDSCAPING AND VEHICLES. DAMAGE ESTIMATE EXCEEDED 50K AT 10:30AM. INVOLVED SECTION OF INSTRUMENT GAS SUPPLY LINE HAD BEEN REPLACED AND IS READILY VISIBLE FOR INSPECTION. AUTOMATIC VALVE ACTUATOR HAS BEEN REFURBISHED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030043 | 2003-04-25 | SUPPLEMENTAL FINAL | 4511 |  | EQUITRANS INC | 100 ALLEGHENY CENTER MALL | PITTSBURGH | ALLEGHENY | PA | 15212 | 10 | 2003-03-30 | 2003 | MOBLEY | WETZEL | WV | 26437 |  |  | 538778.36 | 4378681.88 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 95720.339 | 212687.6513 | 0 | 0 | 150000 | 212687.6513 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 35 | 640971 | 2003-03-31 | 510 | 1000 | NO | NO | YES | NO | NO | NO | JOE LOMBARDO, PIPELINE SAFETY ENGINEER | 4123953135 | JLOMBARDO@EQT.COM | TRANSMISSION | OTHER | HEAT EXCHANGER TUBE IN DEHY UNIT | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1957 | 1 | [7 empty] | ABOVE GROUND |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | A SECTION OF 1" STEEL TUBING A DRY BED DEHYDRATION UNIT FAILED, CAUSING GAS TO IGNITE AND FORCING THE SHUTDOWN OF THE DEHYDRATION UNIT. 11-4-04 THE HEAT EXCHANGER FAILED DUE TO RAPID OVERHEATING, HOWEVER THE EXACT CAUSE OF OVERHEATING COULD NOT BE DETERMINED BY THE LAB (MODERN INDUSTRIES). ORIGINAL REPORT DATE WAS APRIL 25, 2003/ DOT REPORT NUMBER 20030043-577
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030044 | 2003-05-01 | SUPPLEMENTAL FINAL | 4900 |  | TEJAS GAS PIPELINE LP | 500 DALLAS STREET 1000 | HOUSTON | HARRIS | TX | 77002 | 1510 | 2003-04-09 | 2003 | REFUGIO | REFUGIO | TX | 77905 | 75 |  | N 28 16' 520 | W 97 14' 623 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 10 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140510 | 93825.3346 | 105910.2586 | 112220 | 65797.3675 | 28290 | 40112.891 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 20 | 641741 | 2003-04-09 | 780 | 844 | NO | YES | NO | NO | NO | NO | REBECCA VOSS FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 36 | 0.42 | 5LX | 60000 | EFW |  | A O SMITH | 1964 | OPEN DITCH |  |  | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030045 | 2003-05-08 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 715 | 2003-04-01 | 2003 | LORRRAINE | RICE | KS | 67427 | N/A | N/A | 38.51787 DEG W | 98.35320 DEG N | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BROKEN PIPE NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1557000 | 995690.5693 | 2160297.0261 | 57000 | 33420.5128 | 1500000 | 2126876.5133 | 0 | 0 | NO | NO | YES | NO | 0 |  | 8 | 30 | 641013 | 2003-04-01 | 829 | 1000 | YES | NO | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1963 | 1 | [5 empty] | UNKNOWN |  | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | A THREADED ONE-INCH PIPE NIPPLE IN A COMPRESSOR UNIT DISCHARGE PULSATION BOTTLE DRAIN BROKE, PROBABLY DUE TO HIGH CYCLE FATIGUE. NATURAL GAS WAS IGNITED BY UNKNOWN SOURCE. GAS FIRE CAUSED A LUBRICATING OIL FILTER ON ADJACENT COMPRESSOR UNIT TO LEAK RESULTING IN A LUBRICATING OIL FIRE. NATURAL GAS FIRE WAS VERY SHORT DURATION DUE TO RAPID SHUT IN AND VENTING OF GAS BY STATION ESD SYSTEM. 3-30-04 DURING REPAIRS NORTHERN TOOK ADVANTAGE OF THE OPPORTUNITY TO REPLACE AND UPGRADE THE FIRE AND GAS DETECTION SYSTEMS. THREE UNITS WERE REPAIRED AND RETURNED TO SERVICE AND ONE UNIT WAS NOT RETURNED TO SERVICE. ALL OF THE MODIFICATIONS AND REPAIRS COST ABOUT $3.2 MILLION. THERE IS ALSO AN ON-GOING INITIATIVE TO LOCATE OTHER SMALL DIAMETER PIPING THAT MIGHT BE SUBJECT TO VIBRATION AND CYCLIC FATIGUE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030046 | 2003-05-13 14:50 | SUPPLEMENTAL FINAL | 31556 |  | TEXACO PIPELINES, LLC | 2811 HAYES ROAD | HOUSTON | HARRIS | TX | 77082 | 600 | 2003-04-15 | 2003 | BELLE CHASSE | PLAQUEMINES | LA | 70037 | ALLIANCE METER STATION | END OF LINE | N2940396 | W8958699 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE ACTIVATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56715 | 37012.9914 | 62000.7448 | 22146 | 12984.7487 | 0 | 0 | 34569 | 49015.9961 | NO | NO | NO | NO | 0 |  | 0 | 55 | 642244 | 2003-04-15 | 232 | 720 | NO | YES | NO | NO | NO | NO | HENRY L. LEGER | 2815962523 | HENRYLEGER@CHEVRONTEXACO.COM | TRANSMISSION | OTHER | RELIEF VALVE ACTIVATED | STEEL |  | NO | NO | NO | REGULATOR/METERING | [7 empty] | RELIEF VALVE |  |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | THE INCIDENT OCCURRED AT A METER STATION. THE METER STATION RECEIVED A SLUG OF NATURAL GAS CONDENSATE. THE CONDENSATE CARRIED OVER OUT OF THE UPSTREAM SEPERATOR INTO THE STATION PIPING AND INTO THE RELIEF VALVE PILOT CAUSING THE RELIEF VALVE TO OPEN PREMATURELY AT 232PSIG WHICH IS FAR BELOW THE STATION MAOP. WHEN THE RELIEF VALVE ACTIVATED, ATOMIZED CONDENSATE WAS EXPELLED TO THE ATMOSPHERE (LESS THAN ONE BARREL) AND FELL ON NEARBY 3RD PARTY EQUIPMENT. THE GAS LOSS AND THE CLEAN-UP COST EXCEEDED $50,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030047 | 2003-05-14 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA, | HOUSTON | HARRIS | TX | 77046 | 1500 | 2003-04-15 | 2003 | MENDENHALL | SIMPSON | MS | 39114 | MP 63.75 | STN 212+40 | N32 01.113 | W89 49.987 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | SEE COMMENTS PART G | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227456 | 145333.1599 | 318355.9184 | 5000 | 2931.6239 | 222456 | 315424.2944 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 642291 | 2003-04-15 | 340 | 430 | NO | NO | NO | NO | YES | NO | MICHAEL JARRETT | 6019680322 | MICHAEL.JARRETT@GULFSOUTHPL.COM | TRANSMISSION | OTHER | SEE COMMENTS PART G | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 16 | 0.25 |  | 33000 | EFW | N/A | A O SMITH | 1930 | UNDER WATER |  | 36 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | THE PIPELINE LEAK WAS A FOUND IN THE MIDDLE OF A SWAMP. THE AREA IS SECURE AND AWAY FROM THE PUBLIC. THIS PIPE IS SCHEDULED FOR REPLACEMENT.10-28-03 THE LEAK WAS LOCATED IN A SWAMP AND A DECISION WAS MADE TO MAKE THE REPAIR BY REPLACING 1000 FEET OF PIPE USING THE DIRECTIONAL DRILL METHOD AND 664 FEET USING THE CONVENTIONALLY LAYING METHOD. THE EXISTING PIPE IS BEING ABANDONED IN PLACE AND AN ACTUAL DETERMINATION OF CAUSE CANNOT BE DETERMINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030048 | 2003-05-08 | ORIGINAL FINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1505 | 2003-04-16 | 2003 | ESCOBAS | ZAPATA | TX | 78361 | 80 | 4224+00 | 27 06.100 | 98 58.051 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | 2" TAP VALVE BROKEN OFF | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91500 | 61578.1218 | 58222.4788 | 86000 | 50423.9316 | 5500 | 7798.5472 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 642441 | 2003-04-16 | 938 | 1045 | NO | YES | NO | NO | NO | NO | KEVIN P SEHY | 2105284206 | KEVIN.SEHY@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.28 | X52 | 52000 | UNKNOWN |  | UNKNOWN |  | UNDER GROUND |  | 6 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 4 | 16 | 2003 | ONE-CALL SYSTEM | YES | FLAGS |  | ACCURATE | YES | [36 empty] | A 2" TAP VALVE CONNECTED TO EL PASO FIELD SERVICES 20" LINE WAS STRUCK BY A CONTRACTOR CONSTRUCTING A FOREIGN LINE CROSSING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030049 | 2003-05-14 | SUPPLEMENTAL FINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1418 | 2003-04-23 | 2003 | WICKETT | WARD | TX | 79788 |  |  | 31 34.296'N | 102 58.965' W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | ROAD CASING VENT LEAKING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 72095.9085 | 113335.1769 | 51270 | 30060.8718 | 58730 | 83274.3051 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 53 | 643026 | 2003-04-23 | 892 | 1025 | NO | YES | NO | NO | NO | NO | JAMES MCDONALD | 7138032494 | JMCDONALD@EPROD.COM | TRANSMISSION | OTHER | UNKNOWN | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 12 | 0.22 | API5L | 52000 | DSA |  | KAISER |  | UNDER PAVEMENT |  | 96 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ROAD/RAILROAD CASING VENT LEAK. PIPE ABANDONED IN PLACE. NEW PIPE INSTALEED WITH ROAD BORE. |  | ON APRIL 23, 2003, CASING VENT WAS FOUND LEAKING GAS TO THE ATMOSPHERE FROM PIPELINE. LOCATION WAS APPROXIMATELY 1 MILE EAST OF WICKETT, TX, AT HIGHWAY SPUR 57 AND RAILROAD CROSSING. SHORTED PIPE CASING IS SUSPECTED FACTOR OF CONTRIBUTING TO THE LEAK. PIPELINE CROSSING WAS ABANDONED IN PLACE. NEW PIPELINE CROSSING WAS BORED UNDER HIGHWAY AND RAILROAD CROSSING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030050 | 2003-05-29 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY - PO BOX 58900 | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1434 | 2003-05-01 | 2003 | SUMNER | PIERCE | WA |  | MP 1352.56 | 15223+40 | 47.2 N | 122.2 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 7 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101500 | 66161.1908 | 112733.9107 | 37500 | 21987.1795 | 64000 | 90746.7312 | 0 | 0 | NO | NO | NO | YES | 120 | PRECAUTIONARY | 2 | 16 | 643785 | 2003-05-01 | 630 | 674 | NO | YES | NO | NO | NO | NO | PETER C THOMAS SR | 8015846663 | PETER.C.THOMAS@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 26 | 0.28 | API5L | 52000 | SAW |  | KAISER | 1956 | UNDER GROUND |  | 54 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | TEST LAB | OTHER | UNKNOWN | YES | 1958 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030051 | 2003-05-30 | SUPPLEMENTAL FINAL | 1217 |  | BEAR CREEK STORAGE CO | 1900 5TH AVENUE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 852 | 2003-05-11 | 2003 | BIENVILLE | BIENVILLE | LA | 71008 | 0.00 |  | 32 DEG 22' 48 | 92 DEG 56'56 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308400 | 197112.4728 | 430300.4309 | 8400 | 4925.1282 | 300000 | 425375.3027 | 0 | 0 | NO | NO | YES | NO | 0 |  |  | 30 | 644634 | 2003-05-11 | 1398 | 3100 | NO | YES | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | FLEXITALLIC GASKET (STAINLESS STEEL) | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1981 | 10 | 0.5 |  | 35000 | SEAMLESS |  | USS | 1981 | INSIDE/UNDER BUILDING |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [9 empty] | NO | NO | [19 empty] | A FIRE AND EXPLOSION OCCURRED IN THE BUILDING FOR COMPRESSOR UNIT 1A AT THE BEAR CREEK STORAGE FACILITY. UPON INVESTIGATION, IT WAS DISCOVERED THAT THE GASKET HAD FAILED ON THE DISCHARGE BOTTLE, FOR UNIT 1A, COMPRESSOR NO.7, RESULTING IN THE INCIDENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030052 | 2003-06-03 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1805 | 2003-05-04 | 2003 | CHESTERTON | PORTER | IN | 46304 | 881 |  | 41.57507 | 87.04550 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | STRUCTURAL MEMBER DAMAGED NIPPLE AND VALVE ASSY. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64050 | 43245.582 | 37595.6822 | 64000 | 37524.7863 | 50 | 70.8959 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 644005 | 2003-05-04 | 620 | 850 | YES | NO | NO | NO | NO | NO | LOUIS A SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | 1/2 NIPPLE CONNECTED TO 6 | STEEL |  | NO | NO | NO | PIPELINE |  | 2003 | [8 empty] | OPEN DITCH |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | OTHER | EXCAVATED EARTH SETTLING | [53 empty] | DURING CONSTRUCTION,A TEMPORARY HEADER ASSEMBLY WAS ATTACHED TO THE 1-100 30" MAINLINE NEAR MILEPOST 881, IN INDIANA. ATTACHED TO THE HEADER ASSEMBLY WAS A 1/2" NIPPLE AND VALVE ASSEMBLY, WHICH WAS CONNECTED TO A 6" VERTICAL RISER PIECE AND VALVE. AFTER EXCAVATION AND INCLEMENT WEATHER CONDITIONS, THE SHORING/TRENCH BOX SETTLED OR SANK, CAUSING A STRUCTURAL MEMEBER (CROSS SUPPORT BEAM) TO COME INTO CONTACT WITH THE 1/2" VALVE AND NIPPLE ASSEMBLY. THE WEIGHT OF THE TRENCH BOX RESTING ON THE 1/2" VALVE AND NIPPLE ASSEMBLY CAUSED THE NIPPLE TO BE DAMAGED AND NEEDED TO BE REPLACED. THE ONLY WAY TO REPLACE THE DAMAGED NIPPLE WAS TO BLOW DOWN A SECTION OF PIPELINE. THEREFORE, THE COST OF GAS LOST MET THE REQUIREMENT PRESCRIBED IN 49CFR 191, WHICH NECESITATED THE REPORTING OF THIS EVENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030053 | 2003-06-03 | ORIGINAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1710 | 2003-05-08 | 2003 | LAFITTE | JEFFERSON | LA | 70036 | 34.13 | 519+36 | W90 09.314 | N29 44.521 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268428 | 176829.1445 | 256453.6506 | 149298 | 87537.1179 | 119130 | 168916.5327 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 644432 | 2003-05-08 | 778 | 938 | YES | NO | NO | NO | NO | NO | FRANK MARAIA | 5044695903 | FRANK.MARAIA@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 20 | 0.31 | 5LX | 50000 | SEAMLESS |  | NATIONAL | 1953 | UNDER WATER |  | 24 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE DAMAGE TO THE PIPELINE AND THE RESULTING LEAK WAS CAUSED BY A 3RD PARTY. IT IS UNKNOWN WHAT SPECIFIC PIECE OF EQUIPMENT CAUSED THIS INCIDENT TO OCCUR.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20030054 | 2003-05-28 | ORIGINAL | 31130 |  | DUKE ENERGY FIELD SERVICES INC | 7202 COUNTY ROAD 16 | BISHOP | NUECES | TX | 78434 | 2340 | 2003-05-01 | 2003 | NUECES |  | TX | 78380 |  |  | 274211.557N | 974144.15026W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127000 | 83972.3888 | 114379.7065 | 79000 | 46319.6581 | 8000 | 11343.3414 | 40000 | 56716.707 | NO | NO | NO | NO | 0 |  | 1 | 50 | 643813 | 2003-05-02 | 935 | 1050 | NO | NO | YES | NO | NO | NO | RHONDA KAPELLER | 3615226493 | RKAPELLER@DUKE-ENERGY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 20 | 0.28 | X-60 | 1686 |  |  | KAISER | 1952 | UNDER GROUND |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | LACK OF INTERNAL CORROSION CNTRL | YES | 1959 | NO | [57 empty] | SINCE 8/99, THE 1.1 MILE SECTION OF PIPE INVOLVED IN THE INCIDENT HAS BEEN UNDER STATIC CONDITIONS. AS A RESULT, THE OPERATOR WAS UNABLE TO MAINTAIN AN INTERNAL CORROSION PROGRAM ON THE 1.1 MILE SECTION OF PIPE. ADDITIONALLY, DUE TO THE CONFIGURATION OF THE PIPE, IT IS UNABLE TO BE PIGGED. THE ROOT CAUSE OF THE INCIDENT AS DETERMINED BY THE INVESTIGATION TEAM WAS SEVERE INTERNAL CORROSION ON THE BOTTOM SIDE OF THE 20 INCH LINE. THE 20 INCH LINE WAS SUPPLYING GAS TO A 12 INCH LINE THAT WAS BEING PIGGED AS REQUIRED BY THE PIPELINE INTERGRITY PROGRAM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030055 | 2003-05-19 | ORIGINAL | 31651 |  | OSPREY PETROLEUM CO INC | 15995 N BARKERS LANDING #350 | HOUSTON | HOUSTON | TX | 77079 | 400 | 2003-04-20 | 2003 | CORPUS CHRISTI | NUECES | TX |  |  |  | N27 39.245' | W97 12.996' | OFFSHORE |  | LAGUNA MADRE |  | TX | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 41849.5944 | 83848.72 | 10000 | 5863.2479 | 0 | 0 | 55000 | 77985.4722 | NO | NO | NO | NO | 0 |  | 4 | 30 |  |  | 550 | 892 | NO | YES | NO | NO | NO |  | SHARON H. KOUDELKA | 2815823120 | SKOUDELKA@OSPREPYPETROLEUM.COM | TRANSMISSION | BODY OF PIPE |  | OTHER | ALUMINUM | NO | NO | NO | PIPELINE |  | 1963 | 5.55 | 0.22 |  | 40000 |  |  |  |  | UNDER WATER |  | 8 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1963 | NO | [57 empty] | THE FAILURE OCCURRED BECAUSE OF IMPROPER COATING. THE PIPE WAS EXTERNALLY COATED EXCEPT FOR A BARE AREA 6" IN DIAMETER. THIS BARE AREA WAS EXPOSED TO EXTERNAL CONDITIONS WHICH, OVER TIME, REACTED WITH THE ALUMINUM. THE WALL THINNED, THEN EVENTUALLY FAILED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030056 | 2003-06-05 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 745 | 2003-05-08 | 2003 | NAPOLEONVILLE | ASSUMPTION | LA | 70390 | 56.7 | 2993+76 | N29 54.408' | W91 03.750' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78520 | 50167.5856 | 109962.7676 | 1650 | 967.4359 | 76870 | 108995.3317 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 10 | 644516 | 2003-05-09 | 760 | 925 | NO | NO | YES | NO | NO | NO | AL JEANSONNE | 2257774300 | ALL.JEANSONNE@GULFSOUTHPL.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | CONDENSATE DRIP VESSEL | 1952 | 20 | 0.5 | X-46 | 46000 | ERW | N/A | NATIONAL | 1951 | UNDER GROUND |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1952 | NO | [57 empty] | ON 5/8/03 AT 7:45A.M. GULF SOUTH PIPELINE CO., LP EMPLOYEE DISCOVERED A SMALL NATURAL GAS LEAK NEAR A PIG TRAP RECEIVER BARREL ON INDEX I30 AT NAPOLEONVILLE COMPRESSOR STATION SITE. TELEPHONIC REPORTS WERE MADE TO THE LA STATE HAZMAT. THE PIG TRAP WAS ISOLATED AND BLOWN DOWN. DURING THE EXCAVATION PROCESS NATURAL GAS CONDENSATE WAS DISCOVERED. THE SPILL WAS REPORTED (REPORT 644-426) WITH THE NATIONAL RESPONSE CENTER. A LEAK IN A DRIP COLLECTION BARREL ASSEMBLY ATTACHED TO THE BOTTOM OF THE 30" PIPELINE PIG TRAP WAS THE SOURCE OF THE CONDENSATE SPILL. AT THAT TIME THE COST OF REPAIR WAS DETERMINED TO BE GREATER THAN $50,000 A TELEPHONIC INCIDENT REPORT (REPORT #644-516) WAS MADE TO THE NATIONAL RESPONSE CENTER. THE DRIP ASSEMBLY WAS REMOVED AND REPLACED WITH A 12 FT SECTION OF 30" MAIN LINE PIPE. ALL CONTAMINATED SOIL WAS REMOVED FROM THE EXCAVATION SITE AND PROPERLY DISPOSED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030057 | 2003-06-23 10:44 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | PO BOX 770000 | SAN FRANCISCO | SAN FRANCISCO | CA | 94177-0001 | 1345 | 2003-04-01 | 2003 | TEMPLETON | SAN LUIS OBISPO | CA | 93465-8549 | 49.81 |  | 35.57189 | 120.6422472 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77000 | 49952.1585 | 90884.6175 | 22000 | 12899.1453 | 55000 | 77985.4722 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 644491 | 2003-05-09 | 515 | 650 | NO | NO | YES | NO | NO | NO | JEFF BORDERS | 4159735568 | JPB0@PGE.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 24 | 0.25 | API 5L-X52 | 52000 | DSAW |  | KAISER MILL, NAPA | 1962 | UNDER GROUND |  | 6 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES | FLAGS | YES | ACCURATE | YES
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030058 | 2003-06-11 | SUPPLEMENTAL FINAL | 31790 |  | CENTERPOINT ENERGY PIPELINE SERVICES | PO BOX 54979 | OKLAHOMA CITY | OKLAHOMA | OK | 73154 | 1700 | 2003-05-13 | 2003 | DAMASCUS | FAULKNER | AR | 72039 | NA | 4289+74 | 35.34405644 | 92.37530846 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323744 | 207394.3459 | 441059.9753 | 21624 | 12678.6872 | 302120 | 428381.2881 | 0 | 0 | NO | YES | NO | NO | 0 |  |  |  | 644904 | 2003-05-13 | 840 | 1000 | YES | NO | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 24 | 0.28 | X60 | 60000 | DSAW | NA | US STEEL | 1964 | UNDER GROUND |  | 35 | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | IT IS BELIEVED THAT LIGHTNING STRUCK A TREE ADJACENT TO LINE 'J' AND FOLLOWED THE ROOT SYSTEM TO THE PIPE. THERE WAS AN ARC BURN OF APPROXIMATELY 3/4 IN DIAMETER WITH A 3/16" HOLE IN THE BOTTOM OF THE ARCH BURN CAVITY. THERE WAS AN AREA OF APPROXIMATELY 4 TO 5 INCHES IN DIAMETER THAT THE PIPE COATING WAS REMOVED BY THE LIGHTNING. THE SUBSEQUENT LEAKING GAS WAS IGNITED BY THE LIGHTNING AND WAS BURNING ABOVEGROUND. INITALLY IT WAS THOUGHT THAT THIS WAS NOT A REPORTABLE INCIDENT UNTIL THE COMPANY DECIDED TO INSTALL STOPPLES TO KEEP THE FLOW OF GAS GOING TO THE CUSTOMER DOWNSTREAM. ONCE THE STOPPLES WERE IN PLACE, A 40" JOINT OF PIPE WAS INSTALLED TO REPAIR THE DAMAGED PIPE. THE TOTAL EXPENSE OF THE GAS LOSS AND WORK PERFORMED ON THE PIPE IS ESTIMATED TO BE $323744.00.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030060 | 2003-06-19 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 533 | 2003-05-29 | 2003 |  | SKAMANIA | WA |  | MP 1181.5 | 6192+29 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180872 | 116194.7547 | 239104.599 | 20872 | 12237.7709 | 160000 | 226866.8281 | 0 | 0 | NO | NO | NO | NO | 0 |  | 36 | 18 | 646378 | 2003-05-29 | 612 | 809 | NO | NO | NO | NO | YES | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.28 | API 5L | 52000 | DSAW | N/A | CONSOLIDATED WEST | 1956 | UNDER GROUND |  | 38 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [42 empty] | CONSTRUCTION DEFECT |  | NO | YES |  |  | 1956 | INERT GAS |  |  | 880 | [12 empty] | WHILE CONDUCTING A FLAME PACK SURVEY ALONG THE 26" PIPELINE A SUSPECTED LEAK WAS FOUND. AFTER EXCAVATION AND INSPECTION THE LEAK WAS FOUND TO BE A PIN HOLE LEAK IN THE TOP OF THE GIRTH WELD AT 12:00 POSITION. PIPELINE WAS TAKEN OUT OF SERVICE AND REPAIRED. REPAIR WAS MADE BY INSTALLING 95" PUP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030061 | 2003-06-25 | SUPPLEMENTAL FINAL | 7605 |  | HOUSTON PIPELINE CO | 1201 LOUISIANA SUITE 1201 | HOUSTON | HARRIS | TX | 77002-5600 | 2130 | 2003-05-20 | 2003 | NEDERLAND | JEFFERSON | TX |  | 321 |  | 29.9977W | 93.9871W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5737100 | 3664273.505 | 8062386.915 | 87000 | 51010.2564 | 480100 | 680742.276 | 5170000 | 7330634.3826 | NO | NO | YES | NO | 0 |  | 2 | 0 | 645555 | 2003-05-21 | 733 | 811 | NO | YES | NO | NO | NO | NO | ELIZABETH S BUSH-IVIE | 8326681258 | ESBUSH-IVIE@AEP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 30 | 0.31 | API 5LX | 65000 | ERW |  |  |  | UNDER GROUND |  | 72 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1976 | NO | [57 empty] | AT APPROXIMATELY 11:15 PM ON THE EVENING OF MAY 20 A PIPELINE RUPTURE OCCURRED INSIDE THE SUNOCO MARINE TERMINAL AT NEDERLAND, TEXAS. AT APPROXIMATELY, 1:50 AM MAY 21, 2003, CONFIRMATION WAS MADE THAT THE RUPTURE HAD OCCURRED ON THE HOUSTON PIPE LINE TEXOMA 30" LINE. IDENTIFICATION OF THE RUPTURED LINE WAS NOT POSSIBLE EARLIER DUE TO SITE LOGISTICS AND BECAUSE OF SEVERAL PIPELINES IN THE VICINITY OF THE RUPTURE SITE. AN UPSTREAM RAPID FLOW DROP DEVICE CLOSED AND OTHER VALVES ON THE SYSTEM WERE MANUALLY CLOSED. THE FIRE BURNED ITSELF OUT ABOUT 3 AM. THE RUPTURE AND FIRE DAMAGED NEARBY ELECTRIC LINES AND SEVERAL UNOCCUPIED BUILDINGS THAT WERE PART OF THE SUNOCO TERMINAL FACILITY. NO INJURIES OR DEATHS WERE REPORTED. INVESTIGATION AS TO THE CAUSE AND ORIGIN OF THE INCIDENT IS ONGOING; HOWEVER, IT APPEARS THAT INTERNAL CORROSION MAY HAVE PLAYED A PART. AFTER THE INVESTIGATION IS COMPLETED, HPL WILL FILE A SUPPLEMENTAL REPORT. THE RUPTURE OF THE LINE OCCURRED AT A LATERAL AT THE FARTHEST END OF THE LINE, WHICH CONTAINED CUSHION GAS. THAT LATERAL SECTION WILL NOT BE REPLACED. THE LINE WILL NOW TERMINATE AT STATION 765, THE PIPE WAS INSPECTED AT ALL POST-RUPTURE CUTS OF THE PIPE FOR INTERNAL CORROSION. NO CORROSION WAS IDENTIFIED IN ANY OF THE PIPE THAT HAD BEEN IN CONTINUOUS SERVICE. AN IN-LINE INSPECTION TOOL ("SMART" PIG) WAS RUN FROM THE NEW TERMINUS OF THE 30" PIPE (STATION 765), THROUGH THE RIVER CROSSING AND UPSTREAM TO A TEMPORARY RECEIVER AT STATION 9794, A TOTAL OF 9029' - OR 1.71 MILES. THE FOCUS OF THE RUN WAS THE RIVER CROSSING UNDER THE NECHES RIVER. NO CORROSION OR OTHER ANOMALIES WERE IDENTIFIED. THE NECHES RIVER CROSSING IS TYPICAL OF OTHER RIVER CROSSING ON THE TEXOMA PIPELINE. IN FACT, THE ELEVATION AND SLOPE CHANGE IS MOST SIGNIFICANT AT THIS SITE DUE TO THE DEPTH OF THE CHANNEL FOR SHIPPING. THERE, HPL, IS CONFIDENT THAT OTHER RIVER CROSSINGS ARE IN SIMILARLY GOOD SHAPE. THE PIPELINE WAS RETURNED TO SERVICE ON JUNE 6, 2003. 10-15-04 - CORROSION APPEARED TO HAVE OCCURRED DUE TO STANDING WATER IN LOW SPOT OF A DEAD LEG. THE PIPE HAD BEEN CLEANED AND PIGGED DURING CONVERSION FROM LIQUID TO GAS TRANSMISSION IN THE LATE 1980'S. IT IS BELIEVE THE WATER REMAINED FROM THAT OPERATION. NO OTHER CORROSION MECHANISM WAS IDENTIFIED. PUBLIC/PRIVATE PROPERTY DAMAGE INCLUDES INTERRUPTION OF BUSINESS AT THE SUNOCO MARINE TERMINAL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030062 | 2003-06-25 | SUPPLEMENTAL FINAL | 7605 |  | HOUSTON PIPELINE CO | 1201 LOUISIANA, SUITE 1201 | HOUSTON | HARRIS | TX | 77002 | 1705 | 2003-05-24 | 2003 | WOODVILLE | TYLER | TX | 75979 | 3357+73 | N/A | 30.8326 N | 94.3535 W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745000 | 479118.8251 | 973189.3794 | 100000 | 58632.4786 | 0 | 0 | 645000 | 914556.9007 | NO | YES | NO | YES | 10 | PRECAUTIONARY | 0 | 30 | 645951 | 2003-05-24 | 50 | 811 | NO | YES | NO | NO | NO | NO | DANNY NICHOLS, DIRECTOR OF REGULATORY COMPLIANCE | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | TEMPORARY EQUIPMENT | STEEL |  | NO | NO | NO | OTHER | TEMPORARY WORK SPACE | [7 empty] | STEEL, WELDED, TEMPORARY PIPING |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | MALFUNCTION OF THE SAFETY SHUT DOWN SWITCH ON THE DIESEL ENGINE POWERING THE TRANSPORT TRUCK, LOCATED ON THE SCENE |  | HOUSTON PIPELINE WAS CONDUCTING PIGGING OPERATIONS ON A SECTION OF THE TEXOMA 30" GAS TRANSMISSION LINE. LIQUIDS WERE BEING REMOVED FROM THE SYSTEM AND TRANSFERRED TO TEMPORARY STORAGE TANKS ON THE RIGHT-OF-WAY.VACUUM / TRANSPORT TRUCKS WERE REMOVING LIQUIDS FROM THE TANKS WHEN A APPARENT MALFUNCTION ON ONE OF THE TRUCKS SPARKED CAUSING A FLASH FIRE. THE ACTUAL CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION. LOCAL EMERGENCY PERSONNEL IN CONJUNCTION WITH HPL DECIDED TO LET THE FIRE BURN UNTIL IT COULD BE MORE EASILY EXTINGUISHED. NO INJURIES WERE REPORTED IN THE FIRE AND NO DEATHS OCCURRED. A VOLUNTEER FIREMAN WAS TREATED FOR HEAT EXHAUSTION. BELL HOLES WERE EXCAVATED TO EXAMINE THE PIPELINE FOR POSSIBLE HEAT EFFECTS. NONE WERE DETECTED. NO PIPELINE VALVES OR OTHER SURFACE EQUIPMENT WAS DAMAGED. FOLLOWING EXTINGUISHMENT OF THE FIRE, THE PIGGING OPERATION WAS FINISHED AND THE PIPELINE WAS RETURNED TO SERVICE. NO GAS WAS LOST OR VENTED DUE TO THE FIRE. FINAL UPDATE...AUGUST 07, 2009 THIS INCIDENT OCCURRED DURING A PIGGING OPERATION OF AN INTRASTATE PIPELINE. PIPELINE PRESSURE WAS EVACUATED DURING THIS LIQUID REMOVAL PROCESS, WITH THE EXCEPTION OF 50 PSIG OF NATURAL GAS, USED TO PUSH THE MAINTENANCE PIG. FINAL INVESTIGATION CONCLUDED THAT A TRANSPORT TRUCK, USED TO HAUL THE CONDENSATE FROM THIS SITE, EXPERIENCED A MALFUNCTION OF A SAFETY SWITCH ON THE DIESEL ENGINE, RESULTING IN IGNITION OF THE VAPORS OFF THE FRAC TANKS. THE ONLY PRODUCT LOSS DURING THIS INCIDENT WAS THE LIQUID CONDENSATE DURING THE FIRE. PROPERTY DAMAGES WERE LIMITED TO THE FRAC TANKS AND DIESEL TRUCKS OWNED BY THE THIRD PARTY CONTRACTOR. THERE WERE NO ADDITIONAL DAMAGES TO COMPANY FACILITIES OR PROPERTY.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030063 | 2003-07-09 11:55 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1250 | 2003-06-17 | 2003 |  | COCONINO | AZ |  | L1201/VALVE 32 | 254 +3265 | N 35 DEG. 15' 56.2 | W 111 DEG. 49' 51.3 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | PIPE NIPPLE (ON GAS OPERATOR PIPING) WAS DAMAGED. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54200 | 36559.5031 | 32610.3963 | 53200 | 31192.4786 | 1000 | 1417.9177 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 |  | 648157 | 2003-06-17 | 597 | 845 | NO | YES | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | PIPE NIPPLE | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | [8 empty] | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | A CONTRACTOR SHIFTED THE STRUCTURAL BRACING FOR THE MAINLINE VALVE, WHICH DAMAGED THE POWER GAS OPERATOR PIPING TO VALVE 32 ON THE 1201 LINE, WHILE EXCAVATING UNDERNEATH THE VALVE. A NIPPLE ON THE POWER GAS PIPING WAS DAMAGED, REQUIRING THE VALVE SECTION TO BE BLOWN DOWN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030064 | 2003-07-09 15:12 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1330 | 2003-06-19 | 2003 |  |  |  |  | LN.526A-2400/526A-2401+4 |  | 28 DEG. 56'14.9 | 89 DEG. 18'48.0 | OFFSHORE |  | SOUTH PASS | 38 |  | YES | NO | INTERSTATE | OTHER | PIPE DENTED TO APPROX. 1/3 OF PIPE OD. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505000 | 322443.865 | 711890.4617 | 5000 | 2931.6239 | 500000 | 708958.8378 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 648392 | 2003-06-19 | 900 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 12.75 | 0.5 | API 5L | 42000 | SEAMLESS |  | USS | 1972 | UNDER WATER |  | 132 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | OTHER | THE PIPELINE WAS DAMAGED AFTER A MUDSLIDE. | [53 empty] | STONE ENERGY CONTACTED TENNESSEE GAS PIPELINE TO REPORT BUBBLES IN THE AREA OF SOUTH PASS BLOCK 38, NEAR THEIR TIE-IN. THE PIPELINES ARE LOCATED IN A KNOWN MUDSLIDE AREA. THE TWO PIPELINES APPARENTLY CAME INTO CONTACT WITH ONE ANOTHER AFTER A MUDSLIDE OCCURRED. THE TENNESSEE LINE WAS FOUND WITH APPROXIMATELY 11 FEET OF SOIL OVERBURDEN, FOLLOWING DAMAGE INSPECTION. APPARENTLY, THE 8" STONE ENERGY LINE CAME INTO CONTACT WITH THE 12" TENNESSEE 526A-2400 LINE, WHERE THE LINES CROSSED, CAUSING SOME DAMAGE TO THE TOP OF THE 12" LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030065 | 2003-07-03 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 454 | 2003-06-05 | 2003 | KERMIT | WINKLER | TX | 79745 | 0.000 | 00+00 | 31.81100 N | 103.07416 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7252000 | 4684192.1628 | 9017054.6057 | 1522000 | 892386.3248 | 5730000 | 8124668.2809 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 6 | 646954 | 2003-06-05 | 925 | 1000 | YES | NO | NO | NO | NO | NO | PAT VAUGHAN | 4023987185 | PAT.VAUGHAN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1967 | 30 | 0.56 | API 5L | 60000 |  | N/A |  |  | UNDER GROUND |  | 84 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1967 | NO | [57 empty] | THE INITIAL INVESTIGATION INDICATES THAT A BURIED 30 INCH SCRUBBER INLET HEADER RUPTURED DUE TO INTERNAL PITTING. ESCAPING GAS IGNITED AND CAUSED EXTENSIVE DAMAGE TO THE COMPRESSOR STATION FACILITIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030066 | 2003-07-25 11:32 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1415 | 2003-07-04 | 2003 | LAMAR | BACA | CO |  | MAIN LINE 3A/ | 7406 + 126 | N 37-36-00 | W 102-40-20 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FLANGE GASKET AT 2 IN. TAP VALVE. | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220000 | 142985.2962 | 253730.3864 | 70000 | 41042.735 | 150000 | 212687.6513 | 0 | 0 | NO | YES | NO | NO | 0 |  | 6 |  | 649934 | 2003-07-04 | 750 | 943 | NO | NO | YES | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | OTHER | INSULATING GASKET | NO | NO | NO | REGULATOR/METERING |  | 1964 | [8 empty] | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | INSULATING GASKET ON A FLANGE BY FLANGE 2 IN. TAP VALVE ASSEMBLY AT THE BACA MATER STATION, NEAR LAMAR, CO, FAILED, RESULTING IN A NATURAL GAS RELEASE, AND SUBSEQUENT IGNITION(NO EXPLOSION) DUE TO AN UNKNOWN SOURCE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030067 | 2003-07-17 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 852 | 2003-06-17 | 2003 | WEST SALEM | LACROSSE | WI | 54669 | MP 0.388 | 20+51 | 43.90871 N | 91.09804 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236797 | 151111.0783 | 335702.9351 | 67 | 39.2838 | 236730 | 335663.6513 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 648170 | 2003-06-17 | 360 | 800 | NO | NO | NO | NO | YES | NO | PAT VAUGAHN | 4023987185 | PAT.VAUGHAN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 3 | 0.16 | API 5L | 35000 | ERW | N/A | LONE STAR | 1963 | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | GOUGE | [12 empty] | POOR WORKMANSHIP | NO | NO | [19 empty] | A CANOEIST REPORTED SEEING BUBBLES IN THE LACROSSE RIVER AND NOTED THE PIPELINE SIGNS. WEST SALEM BRANCH LINE PIPE FOUND EXPOSED IN RIVER BOTTOM. THE LEAK WAS FROM A CIRCUMFERENTIAL CRACK THAT APPEARS TO HAVE STARTED TO CREASE IN THE PIPE MADE DURING ORIGINAL INSTALLATION IN 1963. THE CREASE APPEARS TO HAVE BEEN CAUSED BY A 4-WHEEL CUTTER BEING USED TO TRIM THE XTRUECOAT COATING FOR THE GIRTH WELD. 3-30-04 NO FURTHER INFORMATION AVAILABLE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030068 | 2003-07-17 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1100 | 2003-06-11 | 2003 | BUSHTON | RICE | KS | 67427 | 0.00 | 0+00 | 38.51896 N | 98.35243 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88700 | 59891.453 | 52007.0085 | 88700 | 52007.0085 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 3 | 647579 | 2003-06-11 |  |  | NO | NO | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | OTHER | NO FAILURE WAS INVOLVED | STEEL |  | NO | NO | NO | COMPRESSOR | [10 empty] | OTHER | COMPRESSOR STATION |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 1 |  |  | A FOREMAN FOR A 3RD PARTY CONTRACTOR INSTALLING ELECTRICAL EQUIPMENT AT THE BUSHTON COMPRESSOR STATION WAS SIMULATING TO ANOTHER 3RD PARTY PERSON HOW THE EMERGENCY SHUT DOWN (ESD) SYSTEM COULD BE ACTIVATED BY A PUSHBUTTON SWITCH. WHEN THE FOREMAN TOUCHED THE SWITCH, THE ESD SYSTEM ACTIVATED SHUTTING IN AND BLOWING DOWN THE COMPRESSOR STATION. THE FOREMAN DID NOT EXPECT THE PUSHBUTTON TO BE SET TO BE SO SENSITIVE. THE INCIDENT WAS REPORTED BECAUSE MORE THAN $50,000 WORTH OF GAS WAS VENTED FROM THE COMPRESSOR STATION YARD BY THE ESD SYSTEM. NO FAILURE OR MALFUNCTION OF EQUIPMENT OCCURRED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030069 | 2003-07-23 | SUPPLEMENTAL | 792 |  | ATLANTA GAS LIGHT CO | 660 RALPH MCGILL BLVD | ATLANTA | FULTON | GA | 30312 | 1520 | 2003-06-23 | 2003 | ATLANTA | FULTON | GA | 30318 | BET HABERSHAL DR & MCCALL | N/A |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689071 | 441022.4316 | 947851.219 | 35107 | 20584.1043 | 63964 | 90695.6862 | 590000 | 836571.4286 | NO | YES | NO | NO | 0 |  | 4 | 45 | 648782 | 2003-06-23 | 190 | 300 | NO | NO | NO | YES | NO | NO | SCOTT CRIDER,DESIGN ENGINEER | 4045844697 | SCRIDER@AGLRESOURCES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 24 | 0.28 | API 5LX X42 | 42000 | WELDED LONGITUDINAL | N/A | UNKNOWN |  | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | HOME BUILDER | YES | 2 | 20 | 2003 | ONE-CALL SYSTEM | YES |  | YES | ACCURATE | [37 empty] | GRADING CONTRACTOR MOVING DIRT FOR A NEW HOUSING DEVELOPMENT RUPTURED A 24" STEEL NATURAL GAS PIPELINE WITH A BULLDOZER. ESCAPING GAS TRAVELED THROUGH HIGH VOLTAGE POWER LINES OVERHEAD THUS GIVING GAS AND DESTROYING THE BULLDOZER AND DAMAGING A NEARBY TRUCK. OPERATOR OF BULLDOZER ESCAPED UNHARMED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030070 | 2003-07-30 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1110 | 2003-07-02 | 2003 | LINDEN | UNION | NJ |  | 84.91 | 4483+44 | N 40.605415 | W 74.254633 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | SMALL AIRPLANE COLLIDED WITH PIPELINE FACILITIES | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54900 | 36494.5205 | 45078.9206 | 39400 | 23101.1966 | 15500 | 21977.724 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 1 | 649735 | 2003-07-02 | 747 | 795 | NO | NO | YES | NO | NO | NO | DWAYNE E TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | OTHER | OPERATOR POWER GAS & ESD PIPING | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1960 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A SMALL SINGLE ENGINE AIRCRAFT HAD MECHANICAL FAILURE SHORTLY AFTER TAKE OFF FROM THE LINDEN, NEW JERSEY AIRPORT AND WAS FORCED TO ATTEMPT AN EMERGENCY LANDING AT THE TEXAS EASTERN LINDEN COMPRESSOR STATION. THE AIRCRAFT COLLIDED WITH SOME PIPELINE FACILITIES RESULTING IN DAMAGE TO OPERATOR POWER GAS PIPING, ESD PIPING, AND TEMPERATURE AND PRESSURE TRANSMITTERS. THE FAA AND FBI IMMEDIATELY BEGAN AN INVESTIGATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030071 | 2003-08-06 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1508 | 2003-07-05 | 2003 | ST FRANCIS | CHEYENNE | KS | 67756 |  | 4599+61 | 39.9268901 | -101.9384019 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | ESD SYSTEM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141912 | 95820.9231 | 83206.5231 | 141912 | 83206.5231 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 649997 | 2003-07-05 | 911 | 960 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR-PIPELINE SAFETY SPECIALIST | 2708524424 | DAVID.L.SINCLAIR@SSGCP.COM | TRANSMISSION | OTHER | SUCTION GATE DID NOT CLOSE DURING ESD |  |  | NO | NO | NO | COMPRESSOR |  | 1981 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | ON SATURDAY, JULY 5, 2003 AT 3:08 PM CST, ST. FRANCIS COMPRESSOR STATION ON THE RAWLINS-HESSTON EXPERIENCED AN ESD "EMERGENCY SHUT-DOWN", WHICH SHUT THE STATION DOWN. DURING THE ESD, THAT STATION SUCTION VALVE DID NOT CLOSE WHICH ULTIMATELY VENTED GAS TO THE ATMOSPHERE FOR APPROXIMATELY 1 HOUR AND 45 MINUTES UNTIL FIELD OPERATIONS PERSONNEL ARRIVED AT THE SCENE AND RESPONDED TO THE SITUATION. THE STATION SUCTION VALVE WAS CLOSED AND THE EVENT WAS UNDER CONTROL AT 4:53 PM CST.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030072 | 2003-08-12 | ORIGINAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 2603 AUGUSTA | HOUSTON | HARRIS | TX | 77057 | 1215 | 2003-07-21 | 2003 |  |  | LA |  | WEST CAMERON 630 | X 1367792.89 Y -233432.04 | 28 00 67.9 | -93 17 44.3 | OFFSHORE |  | WEST CAMERON | 630 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275000 | 175487.2881 | 389927.3608 | 0 | 0 | 275000 | 389927.3608 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 651472 | 2003-07-21 | 850 | 1440 | YES | NO | NO | NO | NO | NO | HENRY WANG | 7132674784 | TWANG@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 20 | 0.5 | X-60 | 60000 | DSAW |  | US STEEL CORP | 1978 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1978 | NO | [57 empty] | PIN HOLE LEAK ON THE BOTTOM OF THE PIPE. POSSIBLY CAUSED BY INTERNAL MICROBIOLOGICAL CORROSION. A REPAIR CLAMP WAS INSTALLED TO REPAIR THE LEAK.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030073 | 2003-08-21 13:36 | SUPPLEMENTAL FINAL | 6141 |  | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 414 SILVER AVENUE, SW | ALBUQUERQUE | BERNALILLO | NM | 87102-1007 | 30 | 2003-07-24 | 2003 | MALJAMAR | LEA | NM | 88264 | MP 21 |  | 32.723461N | 103.646564W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | LIGHTNING STRIKE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72338 | 47721.9949 | 67569.2473 | 42088 | 24677.2376 | 30250 | 42892.0097 | 0 | 0 | NO | YES | NO | NO | 0 |  | 7 | 30 | 615775 | 2003-07-24 | 540 | 600 | NO | NO | NO | YES | NO | NO | JON W. JONES, P.E. | 5052414571 | JJONES@PNM.COM | TRANSMISSION | OTHER | GASKET | OTHER | GASKET | NO | NO | NO | OTHER | VALVE SET |  | 8 |  | ANSI 300 |  |  | PLUG | NORDSTROM |  | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | AN APPARANT LIGHTNING STRIKE HIT THE GROUND IN THE IMMEDIATE AREA OF AN 8 INCH ABOVE GROUND VALVE SET CAUSING GAS TO ESCAPE AND CATCH FIRE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030074 | 2003-08-25 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1440 | 2003-07-27 | 2003 |  | ST MARY | LA |  | 0.00/0+00 | 0+00 | 29-18'-64 | 091-32'-15 | OFFSHORE |  | EUGENE ISLAND | 32 |  | YES | NO | INTERSTATE | OTHER | MAINTENANCE SANDBLASTING CAUSED LEAK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52118 | 33421.791 | 70233.372 | 4408 | 2584.5197 | 47710 | 67648.8523 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 30 | 652088 | 2003-07-27 | 950 | 1200 | NO | NO | YES | NO | NO | NO | JACK ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | MAINTENANCE SANDBLASTING | OTHER | INSOLATING RING GASKET | NO | NO | NO | OTHER | INSOLATING RING GASKET | [5 empty] | N/A | N/A | N/A |  | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | INADEQUATE PROCEDURES |  | 0 | 0 | Y | 7 |  |  | WHILE CONDUCTING COATING MAINTENANCE A CONTRACT CREW WAS SANDBLASTING THE PLATFORM PIPING WHEN A 2" INSOLATING FLANGE GASKET WAS SANDBLASTED TO A POINT THAT THE GASKET FAILED. WHEN THE GAS STARTED ESCAPING IT BEGAN TO COVER THE AREA WITH A CONDENSATE MIST. THE CREW STOPPED ALL OPERATIONS AND BOARDED A UNOCAL STANDBY BOAT. THE PROJECT INSPECTOR CALLED GULF SOUTH PERSONNEL AND THE APPROPRIATE PERSONNEL RESPONDED TO THE INCIDENT. ONCE ON SCENE GULF SOUTH PERSONNEL CONTACTED ALL EFFECTED PRODUCERS AND ASKED THAT ALL PRODUCTION BE SHUT-IN. THIS ACTION STOPPED THE FLOW AND ELIMINATED THE CONDENSATE MIST AND ALLOWED PERSONNEL TO CLOSE 2" ISOLATION VALVE AND STOP THE LEAK. GULF SOUTH PERSONNEL RETURNED THE FOLLOWING MORNING AND REMOVED DAMAGED GASKET AND REPLACED WITH NEW ONE. GULF SOUTH ALSO ACTIVATED THE O'BRIENS GROUP TO HANDLE GULF SOUTH'S SPILL RESPONSE EFFORTS (THERE REPORT IS ATTACHED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030075 | 2003-08-25 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1300 | 2003-08-03 | 2003 | VENICE |  | LA |  | 17.00 | 898+06 | 148829.36 | 2574978.00 | OFFSHORE |  | WEST DELTA | 48 | LA | NO | NO | INTERSTATE | OTHER | LEAK THROUGH COMPONENT DUE TO 3RD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371000 | 236785.3832 | 525215.8647 | 1000 | 586.3248 | 370000 | 524629.54 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 652878 | 2003-08-04 | 1040 | 1440 | YES | NO | NO | NO | NO | NO | DWAYNE E TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | [5 empty] | BALL | GROVE B-5 | 1983 | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | NET AND CHAIN WRAPPED AROUND THE VALVE GEAR BOX ON TEXAS EASTERN LINE 40-G IN 40 FEET OF WATER DAMAGED THE PIPELINE COMPONENTS RESULTING IN A NATURAL GAS LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030076 | 2003-08-25 | ORIGINAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET #1000 | HOUSTON | HARRIS | TX | 77002 | 1238 | 2003-08-08 | 2003 | MOUNTAIN VIEW | KIOWA | OK | 73062 | OE 197 | 7931+29 | N 34 57' | W 98 17' 01 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378807 | 255441.9639 | 229588.2693 | 369807 | 216827.0103 | 9000 | 12761.2591 | 0 | 0 | NO | NO | NO | YES | 1 | THREAT TO THE PUBLIC | 1 | 53 | 653335 | 2003-08-08 | 680 | 720 | NO | NO | YES | NO | NO | NO | REBECCA VOSS FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 26 | 0.25 | 5LX52 | 52000 | ERW |  | A O SMITH | 1956 | UNDER GROUND |  | 60 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | GENERAL CORROSION |  | STRESS CORROSION CRACKING |  | YES | 1957 | NO
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20030077 | 2003-08-20 | ORIGINAL | 22175 |  | DYNEGY MIDSTREAM SERVICES, L.P. | 1000 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1000 | 2003-07-26 | 2003 | [6 empty] | 29.17'.16" | 93.42'.56.2" | OFFSHORE |  | WEST CAMERON | 296 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243000 | 159256.7724 | 250583.9987 | 113000 | 66254.7009 | 130000 | 184329.2978 | 0 | 0 | NO | NO | NO | NO | 0 |  | 81 |  | 652003 | 2003-07-26 | 980 | 1440 | YES | NO | NO | NO | NO | NO | TIM HUFFER | 3375834642 | TIM.HUFFER@DYNEGY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.31 | API 5L | 52000 | ERW |  | UNKNOWN |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1969 | NO | [57 empty] | THE TIME REPORTED FOR THE ELASPED TIME UNTIL AREA WAS MADE SAFE REFLECTS THE TIME REQUIRED TO DEPRESSURE PIPELINE IN ORDER TO SAFELY AFFECT REPAIR. THE DOLLAR VALUE FOR GAS LOSS INCLUDES $1,700 FOR GAS THAT LEAKED AND $111,300 FOR GAS THAT WAS FLARED TO DEPRESSURE THE PIPELINE FOR REPAIR.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030078 | 2003-08-27 12:13 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1044 | 2003-07-28 | 2003 |  |  |  |  | MP 0.50 |  | N 29^35' 91 | W 93^09'12 | OFFSHORE |  | WEST CAMERON | 71 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 41664.204 | 88006.6845 | 5000 | 2931.6239 | 60000 | 85075.0605 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 0 | 652144 | 2003-07-28 | 14 | 2000 | NO | YES | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 10.75 | 0.37 | API 5L | 42000 |  |  | USS | 1980 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDETERMINED | YES | 1980 | NO | [57 empty] | A LEAK WAS DISCOVERED ON THE 10 IN. ANR LINE, 653-32, IN WEST CAMERON BLOCK 71, GULF OF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS DUE TO INTERNAL CORROSION. THE LEAK WAS REPAIRED BY INSTALLING A 10 IN. PLIDCO SPLIT SLEEVE REPAIR CLAMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030080 | 2003-09-09 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 1655 | 2003-08-13 | 2003 | GRANITE CITY | MADISON | IL |  | 28.1 | 1498+96 | 38.69694 | 90.13194 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 9 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100410 | 65017.349 | 121242.3385 | 25410 | 14898.5128 | 75000 | 106343.8257 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 653867 | 2003-08-13 | 185 | 200 | NO | NO | NO | YES | NO | NO | JOHNNY L CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 16 | 0.31 | UNKNOWN | 24000 | ELCWELD | NA | UNKNOWN |  | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 8 | 13 | 1999 | EXCAVATOR | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | ON 8/13/03, AT APPROXIMATELY 10:45, THE STEIN STEEL MILL SERVICES CALLED ONE OF OUR COMPANY'S FIELD EMPLOYEES ABOUT A SMELL OF GAS. UPON ARRIVING AT THE LOCATION, HE WAS WAVED DOWN BY A CREW (3 MEN) WITH A BACKHOE. OUR EMPLOYEES ASKED THE EXCAVATION CREW ABOUT THE LEAK, BUT THEY SAID THEY DIDN'T KNOW ANYTHING ABOUT A LEAK. THE EXCAVATION CREW SAID THAT THEY JUST WANTED THE PIPELINE LOCATED SO THEY COULD DO SOME DIGGING TO LOCATE A WATER LEAK. OUR EMPLOYEE FLAGGED AND PAINTED THE LOCATION OF THE PIPELINE. THE EXCAVATION CREW ALSO WANTED TO KNOW THE DEPTH OF THE LINE. OUR EMPLOYEE INFORMED THE EXCAVATOR THAT DUE TO THE PRESENT OF A LAYER OF STEEL SLAG IN THE GROUND THEY WOULD HAVE TO REMOVE THE SLAG BEFORE AN ACCURATE DEPTH PROBE COULD BE CONDUCTED. AT THAT POINT THE EXCAVATION CREW SAID THEY COULD NOT BE WORKING TOWARD THE LINE, BUT WOULD BE DIGGING AWAY FROM THE PIPELINE AND THAT WOULD NOT BE NECESSARY. THE EMPLOYEE GAVE THE CREW LEADER A BUSINESS CARD AND TOLD HIM TO CALL IF ANY CHANGES WERE MADE IN THE PLANS THAT WOULD CAUSE THEM TO DIG BACK TOWARD THE PIPELINE. THE COMPANY'S EMPLOYEE RETURNED TO HIS REGULAR WORK DUTIES. AT ABOUT 16:30 THE SAME DAY OUR EMPLOYEE RECEIVED A CALL THE EXCAVATOR REPORTING THAT A PIPELINE HAD BLEW AND HE THOUGHT STREAM WAS COMING OUT OF THE PIPELINE. OUR COMPANY'S EMPLOYEE INFORMED THE EXCAVATOR TO EVACUATE THE WORKING AREA. WHEN OUR COMPANY'S EMPLOYEE WAS ON THE WAY TO THE WORK SITE HE RECEIVED A CALL FROM UNITED STATES STEEL COMPANY CONFIRMING THAT THE COMPANY'S PIPELINE WAS LEAKING. FIRE AND LOCAL POLICE HAD THE LOCATION SECURED WHEN THE COMPANY'S FIELD EMPLOYEE. THE PIPELINE HAD A GOUGE AT 9.5" X 4.0" THAT APPEARED TO MATCH THE TEETH ON THE BACKHOE. THE EXCAVATION CREW DID NOT ADMIT TO HITTING THE LINE. THE PIPELINE WAS REPAIRED WITH PRE-TESTED PIPE. ALL WELDS X-RAYED, AND THE PIPELINE SECTION WAS PRESSURE TESTED FOR 30 MINUTES PER DOT REQUEST. THE PIPELINE WAS PUT BACK INTO NORMAL SERVICE AT 11:35 ON 8/27/03.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030081 | 2003-09-23 15:25 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | PO BOX 770000 | SAN FRANCISCO | SAN FRANCISCO | CA | 94177-0001 | 1300 | 2003-08-22 | 2003 | MADERA | MADERA | CA | 93638 | 30.46 |  | 37.0193 | -120.1277 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | LEAK CAUSED BY LONGITUDINAL TEAR - 40 INCHES | [5 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 490000 | 313872.9393 | 668168.6886 | 32000 | 18762.3932 | 88000 | 124776.7554 | 370000 | 524629.54 | NO | YES | NO | YES | 50 | PRECAUTIONARY | 1 | 5 | 654758 | 2003-08-22 | 360 | 400 | NO | NO | YES | NO | NO | NO | JEFF P. BORDERS | 4159735568 | JPB0@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1931 | 8 | 0.25 | GRADE B | 35000 | SEAMLESS |  | UNKNOWN |  | UNDER GROUND |  | 9 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | AGRICULTURAL OPERATIONS | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | THE EXCAVATOR, TSB AG SERVICES, WORKING FOR GOLDEN WEST FARMING, WAS PREVIOUSLY EXCAVATING ON A SITE NEAR THE DIG-IN. GOLDEN WEST FARMING HAD RECEIVED A ONE-CALL NOTIFICATION TAG FOR WORK IN AN AREA APPROXIMATELY 1/4 MILE NORTH OF DIG-IN. THAT EXCAVATION SITE WAS ACCURATELY MARKED BY PG&E WITHIN THE PROPER TIME LIMITS, AND EXCAVATOR WAS FOLLOWING PROPER PROCEDURES AT THAT LOCATION. EXCAVATOR THEN MOVED 1/4 MILE SOUTH, IN AREA OUTSIDE OF DELINEATED EXCAVATION ZONE AND BEGAN "RIPPING UP" THE DIRT ACCESS ROAD AS PART OF A SECOND EXCAVATION OPERATION. HOWEVER, THE EXCAVATOR HAD NOT NOTIFIED THE ONE-CALL CENTER OF THIS EXCAVATION ACTIVITY. THERE WAS A PERMANENT PIPELINE MARKER WITHIN 40 FEET OF THE DIG-IN LOCATION. THE EXCAVATOR¿S INJURED EMPLOYEE, HOSPITALIZED SINCE THE INCIDENT, DIED ON 9/12/03.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030082 | 2003-09-15 | ORIGINAL | 11680 |  | TXU LONE STAR PIPELINE | 301 SOUTH HARWOOD STREET, SUITE 10 NORTH | DALLAS | DALLAS | TX | 75201-5696 | 1715 | 2003-07-16 | 2003 | HENRIETTA | CLAY | TX | 76365 | LAPAN STORAGE COMPRESSOR |  | 33 44' 10" | 98 11' 34" | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | COMPRESSOR FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 127627.1186 | 283583.5351 | 0 | 0 | 200000 | 283583.5351 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 10 | 651094 | 2003-07-17 | 2200 | 3000 | NO | YES | NO | NO | NO | NO | ELLEN WEAVER | 2144627053 | EWEAVER1@ONCORGROUP.COM | TRANSMISSION | OTHER | COMPRESSOR CYLINDER | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1977 | [8 empty] | INSIDE/UNDER BUILDING |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 10 |  |  | ONE OF THE TWO HIGH STAGE COMPRESSOR CYLINDERS SEPARATED FROM THE ENGINE AFTER THE COMPRESSOR CYLINDER VALVE WAS CHANGED AND AN ATTEMPT WAS MADE TO RESTART THE COMPRESSOR.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030083 | 2003-10-08 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 510 | 2003-09-10 | 2003 | CHESTER SPRINGS | CHESTER | PA | 19425 |  |  | 40.098156 | -75.681320 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | VALVE LEAK THROUGH | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 5 | 656440 | 2003-09-10 | 0 | 936 | YES | NO | NO | NO | NO | NO | STEVEN P BURNLEY | 6077210112 | SBURNLEY@NISOURCE.COM | TRANSMISSION | OTHER | DURING THE ACT OF WELDING ON 20X20X8 TEE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1967 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | OTHER | SEE PART G | 0 | 0 | Y | 19 |  |  | A FLASH FIRE RESULTED IN SECOND DEGREE BURNS TO THE FACE OF MR. DAN WILLIAMS AND POLING AND BACON CONSTRUCTION COMPANY. MR. WILLIAMS, WELDER'S HELPER, WAS HOLDING AND ALIGNING AN 8-INCH WELD END CAP TO AN EXISTING 20 X 8 INCH TEE. WHEN THE CONTRACT WELDER STRUCK AN ARC TO BEGIN THE WELDING OPERATION, A FLASH FIRE OCCURRED. AN UNANTICIPATED COMBUSTIBLE GAS MIXTURE HAD DEVELOPED WITHIN THE NORTHERN END OF THE ABOVE GRADE LINE 1278 HEADER WITHIN THE EAGLE COMPRESSOR STATION YARD. THIS COMBUSTIBLE MIXTURE WAS BELIEVED TO BE PRINCIPALLY ATTRIBUTED TO VALVE L-7208 LEAKING AND NOT BEING ABLE TO ACHIEVE ADEQUATE SHUT OFF AND THE REMOVAL OF THE PRIMARY FRESH AIR SOURCE. ALIGNING THE WELD CAP OVER THE LAST SIGNIFICANT SOURCE OF FRESH AIR CHANGE THE FLOW DYNAMICS THAT HAD MAINTAINED NON-COMBUSTIBLE LIMITS JUST MOMENTS BEFORE. TWO AIR MOVERS LOCATED AT BOTH ENDS OF THIS HEADER SYSTEM WERE EVACUATING THE PIPING AT THE TIME OF THE INCIDENT. COLUMBIA WILL FILE A SUPPLEMENTAL REPORT WITH A MORE DETAILED ACCOUNT AND PHOTOGRAPHS. 12-11-03 THE INVESTIGATION RESTRICTED ITSELF TO THE EVENTS DIRECTLY CONNECTED TO THE SINGLE SUBJECT WELD ON THE SOUTHERN END OF THE LINE 1278 ABOVE GRADE HEADER. ON TUESDAY NIGHT, SEPTEMBER 9, 2003, COLUMBIA PERSONNEL BEGAN AN OVERSIGHT PROCESS TO BLOW DOWN LINE 1278 FROM SHELMIRE VALVE SETTING TO EAGLE COMPRESSOR STATION (A DISTANCE OF 4.26), THE 20-INCH LINE 1278 DISCHARGE HEADER INSIDE THE COMPRESSOR STATION FIRE VALVES, THE ABOVE GRADE LINE 1278 HEADER FEEDING NORTH, AND PARTS OF LINE 1556. THE PURPOSE OF THIS BLOW DOWN WAS TO FACILITATE TIE-IN OF NEW LINE 1896 20-INCH PIPELINE AND MAKE MODIFICATIONS TO EXISTING PIPING. SPECIFICALLY, THESE MODIFICATIONS CONSISTED OF THE REMOVAL OF EXISTING PIPING AND REGULATORS FABRICATED BETWEEN THE BLOW OFFS ON LINES 1278, 1804, AND 1896 AND THE SOUTHERN END OF THE LINE 1278 HEADER. THESE BLOW OFFS ARE IMMEDIATELY WEST OF THE ABOVE GRADE LINE 1278 HEADER (SEE ATTAHCED PHOTOS) NIGHT WORK WAS UNDERTAKEN TO FACILITATE A SERIES OF OTHER CONSTRUCTION OUTAGES SCHEDULED FOR THE FOLLOWING DAY IN OTHER PARTS OF COLUMBIA'S PIPELINE SYSTEM. AFTER THE INITIAL BLOW DOWN WAS COMPLETED AND AFTER OTHER TIE IN WORK WAS PERFORMED, A SMALL ONSITE CREW SET OUT TO WELD ON 8-INCH WELD END CAP IN A LOCATION WHERE PREVIOUS 10-INCH PIPING HAD BEEN CONNECTED WITH A 10 X 8 INCH REDUCER ON THE SOUTHERN END OF THE LINE 1278 HEADER SEE PHOTO P1 AND FIGURE 1.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030084 | 2003-10-10 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 130 | 2003-09-15 | 2003 | PLAQUEMINE |  | LA |  | MILEPOST 137.54 | 7261+92 | 30.24 | 91.23 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2309300 | 1555933.9128 | 1428843.1891 | 2219300 | 1301230.5983 | 90000 | 127612.5908 | 0 | 0 | NO | YES | NO | NO | 0 |  | 2 | 19 | 656923 | 2003-09-15 | 882 | 1120 | NO | NO | YES | NO | NO | NO | DWAYNE E TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | OTHER | ALL ABOVEGROUND METER STATION | STEEL |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | A PIPELINE FAILURE OCCURRED ON GULF STATES' PIPELINE SYSTEM WHICH RESULTED IN A FIRE THAT DESTROYED THE ADJACENT TEXAS EASTERN METER STATION FACILITIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030085 | 2003-10-07 | ORIGINAL FINAL | 13580 |  | NORTH CAROLINA NATURAL GAS CORP | 5625 DILLARD DRIVE | CARY | WAKE | NC | 27511 | 1752 | 2003-09-03 | 2003 | JACKSONVILLE | ONSLOW | NC | 28540 | 41.39 | 2185+63 | 34.73909 | 77.46262 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372586 | 238080.2978 | 521121.2916 | 8628 | 5058.8103 | 363958 | 516062.4814 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 | 655873 | 2003-09-03 | 600 | 1133 | NO | YES | NO | NO | NO | NO | THEODORE R HODGES | 9192356004 | THEODORE.HODGES@PIEDMONTNG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1999 | 8 | 0.25 | API-5LX52 | 52000 | ERW | N/A | LTV | 1999 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 8 | 29 | 2003 | ONE-CALL SYSTEM | YES | PAINT | NO | INACCURATE | YES | [36 empty] | A SUBCONTRACTOR FOR A CONTRACTOR WORKING FOR THE HIGHWAY DEPARTMENT WAS INSTALLING SHEET PILINGS IN THE MEDIAN OF HIGHWAY 17 WHEN HE STRUCK THE 8-INCH PIPELINE AT A DEPTH OF APPROXIMATELY 23 FEET. THE PIPELINE WAS LOCATED AT THIS DEPTH BECAUSE IT HAD BEEN INSTALLED UNDER THE HIGHWAY USING THE HORIZONTAL DIRECTIONAL DRILLING METHOD. THE LINE HAD BEEN LOCATED AND PAINT MARKS PLACED IN THE AREA OF THE INCIDENT. HOWEVER, DUE TO THE DEPTH OF THE LINE AND OTHER METALLIC FACILITIES IN CLOSE PROXIMITY TO WHERE THE PIPELINE WAS HIT, THE LINE LOCATE MARKS MADE BY THE LOCATOR WERE OFF BY APPROXIMATELY 15 FEET WHICH WAS A CONTRIBUTING FACTOR TO THIS INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030086 | 2003-10-14 | SUPPLEMENTAL | 3029 |  | SABINE GAS TRANSMISSION CO | 6950 SULPHUR DRIVE | BEAUMONT | JEFFERSON | TX | 77705 | 145 | 2003-09-15 | 2003 | PLAQUEMINE | IBERVILLE | LA |  | UNKNOWN | UNKNOWN | 30 15' 23 | 91 15' 40 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 30 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3400000 | 2251232.7973 | 2991415.7406 | 2200000 | 1289914.5299 | 0 | 0 | 1200000 | 1701501.2107 | NO | NO | YES | NO | 0 |  | 6 | 0 | 656898 | 2003-09-15 | 903 | 997 | NO | YES | NO | NO | NO | NO | PAUL LANHAM | 4098394602 | SGTRANS@RURALCOMM.COM | TRANSMISSION | OTHER | FORGED ELBOWS | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1991 | 16 | 0.38 | ASTM A-234-77-WPB | 1625 | SEAMLESS | FORGED ELBOWS | UNKNOWN |  | ABOVE GROUND |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | STILL UNDER INVESTIGATION
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030087 | 2003-10-27 14:06 | SUPPLEMENTAL | 2714 |  | DOMINION TRANSMISSION INC | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 1422 | 2003-10-10 | 2003 | HARRISON VALLEY | POTTER | PA | 16927 |  | +500 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | YES | 1 | THREAT TO THE PUBLIC | 0 | 38 | 702168 | 2003-10-10 | 2124 | 2200 | NO | NO | YES | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C._SCHWOEBLE@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 6 | 0.31 | X-42 |  | SEAMLESS |  |  |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | OTHER | UNDER INVESTIGATION | YES | 1970 | NO | [57 empty] | PRIOR TO THE INCIDENT THE HARRISON COMPRESSOR STATION WAS IN THE NORMAL INJECTION MODE STORING APP. 120 MILLION. FIELD PERSONNEL, WORKING AT HARRISON STATION INVESTIGATED INCIDENT THAT OCCURRED AT APPROXIMATELY 2:22 PM ON FRIDAY, OCTOBER 10, 2003. HP-20 RUPTURED AND IGNITED. DTI FIELD PERSONNEL ISOLATED THE HP-20 PIPELINE CAUSING THE FIRE TO BE EXTINGUISHED BY 3 PM THIS SAME DAY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030088 | 2003-10-17 | SUPPLEMENTAL FINAL | 6660 |  | GREAT LAKES GAS TRANSMISSION CO | 5250 CORPORATE DRIVE | TROY | OAKLAND | MI | 48098 | 1100 | 2003-09-18 | 2003 | MARENISCO | GOGEBIC | MI | 49947 | MILE POST 421.44 | 276+17 | 42 24' 28 | 89 43' 42 | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | OTHER | CAUSE IS CURRENTLY BEING INVESTIGATED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257000 | 169718.2877 | 236173.2191 | 154200 | 90411.2821 | 102800 | 145761.937 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 657269 | 2003-09-18 | 715 | 974 | YES | NO | NO | NO | NO | NO | ROBERT J CADORIN | 2482057669 | RCADORIN@GLGT.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 36 | 0.38 | API 5LX X-65 | 65000 | DSAW | N/A | FRANCO | 1981 | UNDER GROUND |  | 53 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | SEE PART G, BELOW FOR DESCRIPTION |  | UPON COMPLETION OF THE FAILURE INVESTIGATION, A FINAL REPORT WILL BE SUBMITTED. 3-12-04 A FAILURE ANALYSIS INDICATED THA THE LEAK OCCURRED AS A RESULT OF THE INITIATION AND PROPAGATION OF A CRACK AT THE APEX OF A DENT ON THE ID SURFACE OF THE PIPE. THE DENT, WHICH WAS LOCATED ON THE BODY OF THE PIPE AT APPROXIMATELY THE 6 O'CLOCK POSITION, WAS THEORIZED TO BE CAUSED OVER TIME BY A ROCK SITUATED UNDER THE PIPE. THE DENT DEPTH TO DIAMETER RATIO WAS 2.5% AND THE MAXIMUM AXIAL STRAIN IN THE DENT WAS APPROXIMATELY 22%. THE CRACK WAS ORIENTED AT AN ANGLE OF APPROXIMATELY 55 DEGREES WITH RESPECT TO THE AXIS OF THE PIPE AND HAD A LENGTH OF APPROXIMATELY 1.25 INCHES. IT WAS DETERMINED THAT THE CRACK INITIATED ON THE ID PIPE SURFACE. THE CRACK IS NOT A PUNCTURE FROM A ROCK SINCE A PUNCTURE WOULD INITIATE ON THE OD SURFACE. THE INITIATION OF CRACKING WAS LIKELY ASSOCIATED WITH DUCTILE TEARING, BASED ON THE HIGH TENSILE STRAINS AT THE DENT APEX ON THE ID SURFACE AND THE 45 DEGREE ANGLE OF THE CRACK WITH RESPECT TO THE PIPE WALL. THERE WAS NO EVIDENCE THAT THE CRACKING WAS ASSOCIATED WITH ANY METALLURGICAL DEFICIENCY IN THE PIPE. THE MECHANICAL PROPERTIES OF THE STEEL MEET THE SPECIFICATIONS FOR API 5L X-65 LINE PIPE AND THE MICROSTRUCTURE IS TYPICAL OF THIS VINTAGE AND GRADE OF PIPE STEEL. IN GENERAL, THE CHEMISTRY OF THE STEEL ALSO MEETS SPECIFICATIONS.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030089 | 2003-09-24 | ORIGINAL | 11808 |  | LOUISIANA INTRASTATE GAS CO, L.L.C. | 8090 HWY 3128 | PINEVILLE | RAPIDES | LA | 71360 | 2215 | 2003-08-30 | 2003 | MIRE | ACADIA | LA |  |  |  | N30 17.96' | W92 9.55' | ONSHORE | 2 |  |  |  | NO | YES | INTRASTATE | OTHER | LEAK DUE TO THIRD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 30000 | 19299.7957 | 39044.8401 | 4200 | 2462.5641 | 25800 | 36582.276 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 15 | 655528 | 2003-08-31 | 635 | 1032 | NO | YES | NO | NO | NO | NO | MICHAEL LEGER | 3372338945 | MLEGER@AEP.COM | TRANSMISSION | OTHER | FAILURE N/A INCIDENT CAUSED BY THIRD PARTY | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1966 | [8 empty] | ABOVE GROUND |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | PICK UP TRUCK FAILED TO STOP AND SPED THROUGH THE "T" SECTION OF HWY 98 (GRAND PRAIRIE HWY) AND CREDEUR ROAD ACROSS THE ROAD DITCH AND INTO THE LIGC 1" FARM TAP RISER & TRANS LA (ATMOS ENERGY) REGULATOR STATION. THE VEHICLE CAME TO REST ON THE 1" RISER AND REGULATOR STATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030090 | 2003-11-10 | SUPPLEMENTAL | 22365 |  | WESTAR TRANSMISSION CO | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103-4298 | 800 | 2003-10-10 | 2003 | COLORADO | MITCHELL | TX |  | BLOCK 27 SECTION 68 | LINE # 4100-000 | N32.18.04 | W100.56.18 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129137 | 87195.0684 | 75716.2239 | 129137 | 75716.2239 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 |  | 2003-10-10 | 900 | 960 | NO | YES | NO | NO | NO | NO | RONALD BARBER | 4323432672 | RBARBER@ONEOK.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | [5 empty] | RELIEF VALVE | CONSOLIDATED | 1980 | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | OTHER | INADEQUATE COMMUNICATIONS | 0 | 0 | Y | 2 |  |  | RELIEF VALVE THAT IS PROTECTING PIGGING VESSEL IS SET 900 PSI AND THE LINE MAOP IS 960 PSI. LINE PRESSURE GOT ABOVE 900 PSI AND CAUSED RELIEF VALVE TO RELIEVE TO ATMOSPHERE. THERE WAS A MISCOMMUNICATION BETWEEN FIELD OPERATIONS AND GAS CONTROL REGARDING THE APPROPRIATE PRESSURE TO OPERATE THE PIPELINE. FIELD OPERATIONS HAD INSTALLED AND SET THE RELIEF VALVE AT A CONSERVATIVE LEVEL BASED UPON HISTORICAL MOP AND THE CENTRAL GAS CONTROL DID NOT HAVE THIS INFORMATION. THIS RESULTED IN THEIR DECISION TO INCREASE THE LINE PRESSURE TO A LEVEL THAT WAS STILL BELOW THE MAOP BUT ABOVE THE SET PRESSURE OF THE RELIEF VALVE, CAUSING IT TO TRIGGER AND RELIEVE GAS TO THE ATMOSPHERE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030091 | 2003-11-12 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1330 | 2003-10-14 | 2003 | FRENCH LICK | ORANGE | IN | 47432 | 629.80 | 33253+74 | 38.5220 | 86.6662 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  | PUNCTURE |  | LONGITUDINAL-TEAR/CRACK | 27 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550000 | 359020.5201 | 599399.0646 | 217000 | 127232.4786 | 333000 | 472166.586 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 702478 | 2003-10-14 | 794 | 800 | NO | NO | YES | NO | NO | NO | DWAYNE E TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1943 | 24 | 0.38 | API 5L X-37 | 37000 | SEAMLESS |  | NATIONAL TUBE | 1943 | UNDER GROUND |  | 30 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | INTERMITTENT ATMOSPHERIC AND GALVANIC | YES | 1949 | NO | [57 empty] | A PIPELINE FAILURE WITH NO FIRE OCCURRED ON THE 24-1NCH LINE IN A RURAL AREA ABOUT 1000 FEET DOWNSTREAM OF THE FRENCH LICK, INDIANA COMPRESSOR STATION. THE CAUSE OF THE FAILURE WAS GENERAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030092 | 2003-11-18 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 456 | 2003-10-25 | 2003 | SODA SPRINGS | CARIBOU | ID | 83276 | MP 546.75 | ES 8176+71 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105400 | 69536.0858 | 98388.7196 | 61400 | 36000.3419 | 44000 | 62388.3777 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 50 | 703567 | 2003-10-25 | 670 | 850 | NO | YES | NO | NO | NO | NO | LARRY OLSEN | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 22 | 0.25 |  |  | DSAW | N/A | CONSOLIDATED WEST | 1956 | UNDER GROUND |  | 38 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | YES | 6 | 25 | 1975 | WATER |  | 8 | 1137 | [12 empty] | PIN HOLE LEAK IN LONG SEAM WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030093 | 2003-11-18 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 255 | 2003-11-08 | 2003 | KEMMERER | LINCOLN | WY | 83101 | MP 467.4 | ES 3987+03 |  |  | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86000 | 55769.535 | 101982.6908 | 24000 | 14071.7949 | 62000 | 87910.8959 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 10 |  | 2003-11-08 | 700 | 850 | NO | YES | NO | NO | NO | NO | LARRY OLSEN | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 22 | 0.25 |  |  | DSAW | N/A | CONSOLIDATED WESTERN | 1955 | UNDER GROUND |  | 38 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | YES | 6 | 29 | 1956 | NATURAL GAS |  | 3 | 861 | [12 empty] | FIRST TEST ON 6-27-1956 RESULTED IN A RUPTURE WHICH WAS REPAIRED WITH 734 FEET OF 22" X .344X 5LX52 PIPE REPLACEMENT FROM ES 3992+42 TO ES 3999+76. SUCCESSFUL RETEST ON 6-29-1956 AT 861 PSIG FOR THREE HOURS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030094 | 2003-11-10 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056-5306 | 1105 | 2003-10-14 | 2003 | BRADENTON | MANATEE | FL | 34203 | MP 81.82 | 4320+11 | 27.43625 N | 82.51148 N | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  | PUNCTURE |  | LONGITUDINAL-TEAR/CRACK | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52549 | 34914.138 | 43542.4683 | 37239 | 21834.1487 | 15310 | 21708.3196 | 0 | 0 | YES | NO | NO | YES | 200 | PRECAUTIONARY | 1 | 40 | 702450 | 2003-10-14 | 690 | 763 | NO | NO | NO | NO | YES | NO | JOSE L.DE LA FUENTE | 7139892585 | JOSE.DELAFUENTE@PANHANDLEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 8 | 0.19 | API-5L | 35000 | SEAMLESS |  | REPUBLIC | 1959 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | EXCAVATOR INSTALLING A WATER LINE FAILED TO NOTIFY FLORIDA ONE CALL CENTER AND HIT THE BURIED NATURAL GAS PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030095 | 2003-11-24 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 425 | 2003-11-02 | 2003 | OWINGSVILLE | BATH | KY | 40360 | 501.76 | 26493+05 | 38.22514 | 83.71785 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  | PUNCTURE |  | LONGITUDINAL-TEAR/CRACK | 2 | 1350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3301500 | 2137783.3985 | 3986459.3469 | 835500 | 489874.359 | 2316000 | 3283897.3366 | 150000 | 212687.6513 | NO | NO | YES | NO | 0 |  | 0 | 55 | 704211 | 2003-11-02 | 906 | 1000 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF, PRINCIPAL ENGINEER | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 30 | 0.38 | API 5L X-52 | 52000 | EFW |  | A O SMITH | 1957 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | MANUFACTURE DEFECT | [10 empty] | MATERIAL DEFECT |  | NO | YES | 11 | 7 | 1957 | WATER |  | 24 | 1425 | [12 empty] | PIPELINE FAILURE RESULTED FROM A MANUFACTURE DEFECT IN THE PIPE AT THE POINT OF FAILURE. 5-20-04 THE ORIGIN OF THE FAILURE WAS DEFINED BY KIEFNER AND ASSOCIATES INC [FINAL REPORT NO 03-76 DATED DECEMBER 10, 2003] AFTER CONSIDERABLE EVALUATION TO BE THE VERY UNUSUAL COINCIDENCE AND INTERACTION OF TWO SEPARATE MANUFACTURING DEFECTS THAT EXISTED IMMEDIATELY ADJACENT TO ONE ANOTHER ON THE PIPE, NAMELY A SMALL 4.5 INCHES LONG LAMINATION AND A 1-INCH TO 1.5 INCH DIAMETER HARD SPOT. IT WAS PROJECTED THAT HYDROGEN RESULTING FROM THE CATHODIC PROTECTION SYSTEM ACTING AT A NEARBY COATING DISCONTINUITY PERMEATED THE MATERIALS AND CAUSING HYDROGEN-INDUCED CRACKING TO INITIATE AT THE OD SURFACE IN THE HARD SPOT. THE FAILURE APPARENTLY OCCURRED WHEN THE HYDROGEN-INDUCED CRACKING REACHED THE MID-WALL LAMINATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030096 | 2003-11-14 | SUPPLEMENTAL | 11272 |  | LAVACA PIPELINE CO | 103 FANIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 | 1100 | 2003-11-11 | 2003 | POINT COMFORT | JACKSON | TX | 77978 |  |  | 28.7054 | 96.5545 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 448.5488 | 950.9627 | 50 | 29.3162 | 650 | 921.6465 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 705006 | 2003-11-11 | 200 | 714 | NO | YES | NO | NO | NO | NO | ROBERT C SERRATA | 3169878914 | ROBERTS@FTPC.FPCUSA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 6 | 0.25 | B | 24000 | SMLS | N/A | N/A |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | IMPROPER CATHODIC PROTECTION |  | YES | 1953 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030097 | 2003-12-01 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 2130 | 2003-10-27 | 2003 | KIOWA | PITTSBURG | OK |  | 24.551 | 24.551 | 34.76502 | 95.86314 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR FUEL GAS LEAK AND FIRE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86455 | 55177.4283 | 122419.7541 | 200 | 117.265 | 86255 | 122302.4891 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 30 | 703780 | 2003-10-28 |  |  | NO | NO | NO | NO | NO | NO | JOHNNY L CAVITT | 3164293606 | JOHNNY.CAVITT@CENTERPOINT.ENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1981 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 0 |  |  | ON 10-27-03 SYSTEM CONTROL RECEIVED A FIRE ALARM FOR THE SHAWNEE COMPRESSOR STATION. AN O & M TECH WAS CALLED OUT THE STATION. UPON ARRIVING THE TECH NOTICED A SMALL FIRE LOCATED IN THE "V" OF THE ENGINE COMING FROM THE SPEED CONTROL ACTUATOR AND EXTINGUISHED THE FIRE. INSPECTION OF THE ENGINE SHOWED THAT A FAN SHAFT WAS BROKEN IN HALF. DUE TO INCORRECT WIRING FROM A PREVIOUS REPAIR, THE ENGINE DID NOT SHUT DOWN AND OVERHEATED. THE HEAT FROM THE ENGINE BLOCK MELTED THE INSULATION ON THE #10 IGNITION WIRE CAUSING THE SPARK WHICH IGNITED LEAKING CONTROL GAS TO THE ACTUATOR. IT COULD NOT BE DETERMINE WHETHER THE CONTROL GAS LEAK FROM THE ACTUATOR WAS LEAKING PREVIOUSLY OR THE HEAT FROM THE OVERHEATED ENGINE AFFECTED THE INTEGRITY OF THE DIAPHRAGM IN THE CONTROLLER CAUSING THE LEAK.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030098 | 2003-12-09 12:41 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1730 | 2003-11-23 | 2003 | GALLION | HALE | AL |  | 138.893 | 4719.5 | 32^29'30 | -87^42'43 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | VALVE OPERATOR PART FAILED. | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 706130 | 2003-11-23 | 950 | 1200 | NO | YES | NO | NO | NO | NO | LOUIS A. SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1982 | [5 empty] | 20 IN. PLUG | ROCKWELL | 1980 | ABOVE GROUND |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | CONTRACT EMPLOYEE WAS OPERATING SUCTION VALVE FROM THE 'CLOSED' TO 'OPEN'POSITION FOR ENGINE #8, AT THE GALLION COMPRESSOR STATION, WHEN GAS PRESSURE ENTERED THE VALVE OPERATOR AND CAUSED THE INDICATOR PLATE TO FRACTURE APART. A PIECE OF PLATE STRUCK THE EMPLOYEE'S HARDHAT, INJURING HIM. THE VALVE OPERATOR BODY IS NORMALLY A NON-PRESSURIZED AREA. APPARENTLY, THE SEAL BETWEEN THE VALVE STEM AND THE OPERATOR FAILED, CAUSING GAS TO ENTER THE OPERATOR BODY.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20030099 | 2003-12-05 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84118 | 150 | 2003-11-13 | 2003 | KEMMERER | LINCOLN | WY | 83101 | MP 448.8 | E S 3004+95 | 41 44 MIN | 110 33 MIN | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61282 | 41007.6636 | 44247.0844 | 51282 | 30067.9077 | 10000 | 14179.1768 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 10 | 705266 | 2003-11-13 | 638 | 850 | NO | YES | NO | NO | NO | NO | LARRY OLSEN | 8015846726 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 30 | 0.31 | X-70 |  | GIRTH WELD | N/A | IPSCO CORPORATION | 2003 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 9 | 19 | 2003 | WATER |  | 8 | 1235 | [12 empty] | SMALL CRACK IN GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030100 | 2003-12-23 | SUPPLEMENTAL FINAL | 11808 |  | LOUISIANA INTRASTATE GAS CO, L.L.C. | 8090 HWY 3128 | PINEVILLE | RAPIDES | LA | 71360 | 100 | 2002-09-05 | 2002 | [5 empty] | + - 35+38 | 29 03' 50.5 | 90 13' 57.3 | OFFSHORE |  | BAY MARCHAND | 5 | LA | NO | NO | INTRASTATE | OTHER | FOUND LARGE SEA ANCHOR ON 12" P/L | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 134960.7694 | 278854.9405 | 16200 | 13486.8932 | 183800 | 265368.0473 | 0 | 0 | NO | NO | YES | NO | 0 |  | 2 | 0 | 622012 | 2002-09-05 | 845 | 1250 | NO | YES | NO | NO | NO | NO | MIKE LEGER | 3372338945 | MLEGER@AEP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 12 | 0.25 | API 5LX | 52000 | ERW | N/A | REPUBLIC STEEL | 1976 | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | LARGE SEA ANCHOR FOUND ON 12" P/L WHICH STRESSED THE PIPE ANCHOR WAS ABANDON IN PLACE ON 12" P/L BY OTHER PARTY. OTHER PARTY UNKNOWN. |  | CAUSE OF INCIDENT AND TYPE IS UNKNOWN AS OF THIS INITIAL REPORT. INCIDENT OCCURRED IN 25 - 30 FEET OF WATER ON THE WEST SIDE OF BELLE PASS IN THE GULF OF MEXICO + - 1.8 MILES SOUTH OF THE BANK LINE ROCK JETTY. ON THE MORNING OF THE INCIDENT (9/5/02), THE 12" PIPELINE WAS ISOLATED FROM THE COMPANY'S PIPELINE SYSTEM AND FROM ALL PRODUCTION IN TO THE 12" PIPELINE. PIPELINE REMAINS DEPRESSURIZED AND ISOLATED AS OF 9/5/02. A FULL INVESTIGATION, VISUAL INSPECTION, EXAMINATION, TESTING, AND REPAIR OF THE PIPELINE SECTION HAS BEEN RESTRICTED DUE TO WATER DEPTH, WEATHER CIRCUMSTANCES, AND MARINE CONDITIONS. SCHEDULING OF REPAIRS REMAINS CONTINGENT UPON WEATHER AND MARINE CONDITIONS. UPON COMMENCEMENT OF FIELD REPAIRS ON LOCATION, ALL RETRIEVABLE EVIDENCE WILL BE COLLECTED AND THE INVESTIGATION WILL CONTINUE TO DETERMINE INCIDENT TYPE AND POSSIBLE CAUSE. A SUPPLEMENT REPORT WILL BE REQUIRED TO FORWARD INFORMATION NOT COMPLETED IN THE INITAL REPORT OF 10/3/04. 12-29-03 ON 9/11/02 A SIDE SCAN SONAR/SUB BOTTOM PROFILER SURVEY WAS PERFORMED AT THE PIPELINE INCIDENT BY T. BAKER SMITH & SONS INC. THE DATA CAPTURED BY THE SURVEY WAS PLOTTED AND REVIEWED ON 9/12/02. THE INTERPRETATION OF THE DATA BY THE SURVEY COMPANY PROJECT MANAGER WAS THAT THE INCIDENT OCCURRED AT THE APPROXIMATE LOCATION INDICATED ON THE ATTACHED MAP IN ABOUT 26 FEET OF WATER. THE CRATER DIMENSIONS MEASURED + - 117 FEET IN LENGTH, + - 1 - 2 FEET IN DEPTH, AND VARIED APPROXIMATELY 1 FOOT TO 15 FEET IN WIDTH. IT APPEARS THAT THERE IS A GAP BETWEEN THE TWO ENDS OF THE PIPE IN THE CRATER MEASURING + - 13.5 FEET. ON 10/7/-2, THREE DAYS AFTER HURRICAN LILI, ANOTHER SIDE SCAN SONAR/ SUB BOTTOM PROFILER SURVEY WAS PERFORMED AT THE PIPELINE INCIDENT BY T. BAKER SMITH & SONS INC. THE DATA CAPTURED BY THIS SURVEY WAS PLOTTED AND REVIEWED ON 10/9/02. THE INTERPRETATION OF THIS DATA BY THE SURVEY COMPANY PROJECT MANAGER INDICATED THAT THE WATER DEPTH OVER THE INCIDENT CHANGED BY ABOUT 2 FEET TO 28 FEET. THE + -13.5 FEET GAP BETWEEN TWO ENDS OF THE PIPE REMAINED THE SAME IN THE CRATER. IT DID APPEAR THAT THE STORM DID CAUSE A SIGNIFICANT CHANGE IN THE SUB-SEAN TERRAIN SURROUNDING THE PIPELINE AND THE CRATER. ON 11/16/2002, THE 12" PIPELINE WAS CUT AT THE LAND PORTION ON THE WEST SIDE OF THE BELLE PASS TO SEPARATE AND SEGMENT THE PIPELINE (SEE ATTACHED MAP). A 10 - 15 FOOT SECTION OF PIPE WAS REMOVED FROM THE LINE. A VISUAL INSPECTION OF THE PIPE SECTION REMOVED AND THE END OF THE NORTH SEGMENT PERFORMED AND THERE WERE NO APPARENT DEFECTS INTERNALLY OR EXTERNALLY ON THE STEEL PIPE OR ON THE COATING. ALSO, THERE WAS NO APPARENT WALL LOSS ON EACH PIECE INSPECTED. A 12" PIPELINE RISER WITH A LOR FLANGE AND BLIND WAS INSTALLED ON THE NORTH SECTION AND THEN WAS RETURNED TO SERVICE. THE SECTION HAD NOT BEEN IN SERVICE SINCE THE 9/5/02 INCIDENT. THE SOUTH SECTION WAS CAPPED AND REMAINED DEPRESSURIZED. DISCUSSIONS ARE ON GOING BETWEEN LIGC AS OPERATOR/OWNER OF THE LINE AND THE CUSTOMER ON A SOLUTION TO RESOLVE THE CURRENT STATUS AND CONDTION OF THE SOUTH SEGMENT OF THE PIPELINE THAT INCURRED THE INCIDENT. SCHEDULING OF RETRIEVING SUB-SEA PHYSICAL EVIDENCE FOR FURTHER INVESTIGATION IS CURRENTLY CONTINGENT UPON A RESOLUTION BETWEEN LIGC AND THE CUSTOMER AND ALSO UPON FAVORABLE WEATHER AND MARINE CONDITIONS. AN ADDITIONAL REPORT WILL BE REQUIRED TO FORWARD INFORMATION NOT COMPLETED IN THIS SUPPLEMENT REPORT OF 11/14/02 UPDATING STATUS AND INFORMATION AND AFTER EVIDENCE IS RECOVERED, EXAMINED, AND TESTED. 12-23-03(FINAL) FOUND AND RETRIEVED LARGE SEA ANCHOR ATTACHED TO PIPELINE AT INCIDENT LOCATION. ANCHOR PLACED THE PIPELINE IN STRESS CAUSING THE INCIDENT. ANCHOR WAS ABANDON IN PLACE ON 12" PIPELINE BY OTHER PARTY. OTHER PARTY IDENTIFICATION UNKNOWN WAS OF THE DATE OF THIS REPORT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20030101 | 2003-12-18 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA, | HOUSTON | HARRIS | TX | 77046 | 15 | 2003-12-02 | 2003 | MORGAN CITY | ST MARY | LA |  | 273+49 |  | 29-17'-13.663 | 91-27'-29.012 | OFFSHORE |  | EUGENE ISLAND | 39 | LA | NO | YES | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250000 | 816321.9915 | 1354055.9756 | 503060 | 294956.547 | 746940 | 1059099.4286 | 0 | 0 | NO | YES | NO | NO | 0 |  | 10 | 15 | 706823 | 2003-12-02 | 915 | 1440 | YES | NO | NO | NO | NO | NO | MIKE MARTIN | 3379887103 | MIKE.MARTIN@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 20 | 0.38 | API 5LX | 60000 | SUBMERGED ARC WELD | N/A | BETHLEHEM STEEL |  | UNDER WATER |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DREDGING OF SHIP CHANNEL | YES | 11 | 24 | 2003 | EXCAVATOR | YES | STAKES | NO | ACCURATE | YES | [36 empty] | ON TUESDAY DECEMBER 2ND AT APPROXIMATELY 12:15AM WEEKS MARINE ( A CONTRACTOR FOR THE ARMY CORP OF ENGINEERS) WAS DREDGING THE ATCHAFALAYA SHIP CHANNEL AND RUPTURED THE 20" PIPELINE. THE PIPELINE WAS TOTALLY SEVERED, CAUGHT FIRE AND BURNED FOR ALMOST AN HOUR. AT THE TIME OF THE RUPTURE THE PIPELINE WAS OPERATING AT 915 PSI AND HAD AND ESTIMATED 16,451 BBLS OF CONDENSATE AND 1,936 MCF OF NATURAL GAS IN THE 11 MILE SECTION. THE CHECK VALVE THAT IS AT THE EUGENE ISLAND BLOCK # 32 PLATFORM CLOSED AND THE LINE WAS SHUT-IN INSTANTANEOUSLY. GULF SOUTH NOTIFIED IT'S SPILL RESPONSE CONTRACTOR IMMEDIATELY TO RESPOND. BY DAYLIGHT WHEN THE FIRST FLY OVER WAS MADE WITH THE U.S. COAST GUARD ON BOARD THEIR WAS NO SIGNIFICANT ENVIRONMENTAL DAMAGE AND THE COAST GUARD REQUIRED NO FURTHER RESPONSE. IN THE MEANTIME WE HAD ALREADY SET CONTRACTORS (DIVERS, VESSELS AND EQUIPMENT) TO THE RUPTURE LOCATION. ON NOVEMBER 24TH GULF SOUTH WAS NOTIFIED BY TELEPHONE FROM THE CONTRACTOR (WEEKS MARINE) OF THE DREDGE CROSSING THE PIPELINE. ON NOVEMBER 26TH THE PIPELINE WAS SURVEYED AND MARKED BY A LICENSED SURVEYOR WERE IT CROSSED THE CHANNEL. THE SURVEY INFOMRMATION WAS FAXED TO THE DREDGE BARGE TOM JAMES AND ARRANGEMENTS WERE MADE WITH WEEKS MARINE FOR A GULF SOUTH EMPLOYEE TO PICKED UP AND BROUGHT TO THE DREDGE AT 6:00 AM ON DECEMBER 2ND TO MAKE THE CROSSING. APPROXIMATELY 12:15 AM ON DECEMBER 2ND THE DREDGE STRUCK AND RUPTURED THE PIPELINE. RISERS REMOVED AND 1,664 FEET OF PIPE REMOVED FROM SHIPPING CHANNEL. REMAINER ABANDONED IN PLACE ON MAY 31, 2009.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20030102 | 2003-12-24 | ORIGINAL FINAL | 30950 |  | EL PASO FIELD SERVICES | 402 3RD STREET SE | FAYETTE | FAYETTE | AL | 35555 | 1430 | 2003-12-10 | 2003 |  | TUSCALOOSA | AL | 35406 | MP 5.563 ON 10" MAIN |  | 33.458 | 87.723 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 26763 | 17570.1895 | 26918.3143 | 13263 | 7776.4256 | 13500 | 19141.8886 | 0 | 0 | NO | NO | NO | YES | 4 | THREAT TO THE PUBLIC | 2 | 15 | 707719 | 2003-12-10 | 420 | 856 | YES | NO | NO | NO | NO | NO | ALVIN W HUDSON | 2059323266 | ALVIN.HUDSON@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A 3RD PARTY LOGGING TRUCK, BELONGING TO KILGORE LOGGING OF JASPER, ALABAMA, VEERED OFF THE ROADWAY AND RAN OVER A STEEL 2 INCH VALVE ASSEMBLY ON A NATURAL GAS PIPELINE. THE VALVE ASSEMBLY WAS PROTECTED BY A 4 INCH GUARD RAIL. THE GUARD RAIL WAS DEMOLISHED AND THE 2 INCH VALVE ASSEMBLY WAS SEVERED COMPLETELY FROM A 4 INCH HEADER ALLOWING NATURAL GAS TO BE RELEASED FROM THE PIPELINE. THE PRESSURE IN THE PIPELINE AT THE TIME OF THE INCIDENT WAS APPROXIMATELY 420 PSIG. THE NATURAL GAS DID NOT IGNITE. THE DAMAGED FACILITY IS OPERATED BY EL PASO FIELD SERVICES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040001 | 2003-12-30 | ORIGINAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1535 | 2003-11-21 | 2003 | CYPRESS | HARRIS | TX | 77429 | 322/31 | 0+00 | 29-59-15N | 95-39-30W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR VALVE CAP SEPARATION DUE TO BOLT FAILUR | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 635000 | 405345.875 | 897467.1489 | 3500 | 2052.1368 | 631500 | 895415.0121 | 0 | 0 | NO | NO | YES | NO | 0 |  | 0 | 15 | 706034 | 2003-11-21 | 680 | 1000 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS | 7139897473 | MEHOVIS@PANHANDLEENERGY.COM | TRANSMISSION | OTHER | COMPRESSOR VALVE CAP STUD BOLTS | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1955 |  |  | N/A |  | N/A | N/A | N/A |  | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | STUD BOLTS | [8 empty] | UNIT #4303 COMPRESSOR WAS BEING PRESSURED UP, WHEN THE GAS PRESSURE ACTING ON THE SUCTION COMPRESSOR VALVE CAP CAUSED 3 BOLTS CONTAINING FATIGUE CRACKS TO FAIL. FAILURE OF THESE BOLTS PUT ADDITIONAL STRESS ON THE REMAINING BOLTS BEYOND THEIR CAPABILITY TO RESIST THAT STRESS, RESULTING IN THEIR EVENTUAL FAILURE AND FAILURE OF THE COMPRESSOR VALVE CAP THAT THEY WERE RESTRAINING. THE FAILURE OF THE COMPRESSOR VALVE CAP RESULTED IN A NATURAL GAS RELEASE FROM THE COMPRESSOR CYLINDER INTO THE COMPRESSOR BUILDING. THE NATURAL GAS FROM THE COMPRESSOR CYLINDER WAS IGNITED BY AN UNKNOWN IGNITION SOURCE, RESULTING IN AN EXPLOSION AND FIRE. THE COMPRESSOR STATION ESD WAS ACTIVATED, WHICH RESULTED IN DEPRIVATION OF A FUEL SOURCE TO THE FIRE AND THE FIRE QUICKLY BURNED ITSELF OUT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040002 | 2003-12-18 | ORIGINAL | 31870 |  | TGS RIO, L.L.C. | 1301 S. MOPAC EXPRESSWAY, SUITE 400 | AUSTIN | TRAVIS | TX | 78746 | 1112 | 2003-11-17 | 2003 | MCALLEN | HIDALGO | TX | 78550 | N/A | N/A |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73331 | 49291.8851 | 47979.5191 | 67338 | 39481.9385 | 5993 | 8497.5806 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 12 | 708377 | 2003-11-17 | 280 | 420 | NO | NO | YES | NO | NO | NO | AL M PAYTON | 5123708448 | APAYTON@TXGAS.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1945 | 4 | 0.19 |  |  |  |  | UKNOWN |  | UNDER GROUND |  | 42 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | NO | [40 empty] | A SUB-CONTRACTOR FOR H20 CONSTRUCTION WAS WORKING ON 2ND STREET AS PART OF A STREET WIDENING PROJECT. THEY WERE USING HEAVY EQUIPMENT TO GRADE THE NEW ROADWAY. APPARENTLY, THEY WENT BEYOND THE AREA OF CONSIDERATION AND HIT THE 4" STEEL GAS LINE. THERE WERE 10 HOLES OF VARIOUS SIZES IN THE BODY OF THE PIPE. THE CONTRACTOR DID NOT MAKE ANY REQUESTS FOR UTILITY LOCATES BEFORE WORKING. 4TH AND 2ND STREETS WERE TEMPORARILY CLOSED DURING THE INCIDENT. TWO RESIDENTS WERE TEMPORARILY EVACUATED WHILE THE SITUATION WAS BROUGHT UNDER CONTROL.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040003 | 2003-12-31 | SUPPLEMENTAL FINAL | 10035 |  | ENBRIDGE PIPELINES (KPC) | 1100 LOUISIANA SUITE 2900 | HOUSTON | HARRIS | TX | 77002 | 1530 | 2003-12-02 | 2003 | BARBER | BARBER | KS |  | MP 167 | 47+98 | 37.02961 | -98.61974 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 472.6496 | 410.4274 | 700 | 410.4274 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 511 | 930 | NO | YES | NO | NO | NO | NO | SCOTT PETERSON | 7138212176 | SCOTT.PETERSON@ENBRIDGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 8 | 0.28 | UNKNOWN |  | LAP WELD | N/A | REPUBLIC | 1930 | OTHER | EXPOSED IN GULLY |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1950 | NO | [57 empty] | S30 T348 R15W CASE #706879 WHITE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040004 | 2004-01-14 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 545 | 2003-12-13 | 2003 | TOLEDO | LEWIS | WA |  | 1281.8 | 11487+90 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 79542.5177 | 103622.6899 | 80000 | 46905.9829 | 40000 | 56716.707 | 0 | 0 | NO | NO | YES | YES | 6 | PRECAUTIONARY | 1 | 40 | 707973 | 2003-12-13 | 630 | 647 | NO | YES | NO | NO | NO | NO | LARRY D OLSEN, SR COMPLIANCE SPECIALIST | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.28 |  | 1124 | DSA LONG SEAM | N/A | KAISER | 1956 |  |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | SUSPECT SCC | [10 empty] | MATERIAL DEFECT |  | NO | YES | 9 | 9 | 1972 | WATER |  | 8 | 1078 | [12 empty] | SUSPECTED SCC; WAITING FOR METALLURIGICAL REPORTS. METTALLURIGICAL TESTING COMPLETED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040005 | 2004-01-12 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 1550 | 2003-12-11 | 2003 | LEMOORE | KINGS | CA |  | MILE POST 5.14 | 27065.576 | 120 2 36.08W | 365 12.59N | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375000 | 249497.32 | 303031.0838 | 275000 | 161239.3162 | 100000 | 141791.7676 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 8 | 707843 | 2003-12-11 | 375 | 400 | NO | NO | YES | NO | NO | NO | W JEFF KOSKIE, SAFETY SYSTEMS ADVISOR | 2132443283 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 20 | 0.28 | X-42 | [5 empty] | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | LANDOWNER |  | YES | 10 | 31 | 2004 | ONE-CALL SYSTEM | YES | STAKES | YES | ACCURATE | YES | [36 empty] | FARMER STRUCK TRANSMISSION LINE WHILE USING RIPPER ATTACHED TO BULLDOZER. DAMAGE LIMITED TO PIPELINE AND GAS LOST - NO PUBLIC PROPERTY DAMAGE. ESTIMATED DAMAGE WAS DETERMINED TO EXCEED $50,000 AT 19:15 ON DATE OF INCIDENT.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040006 | 2004-01-20 11:17 | SUPPLEMENTAL | 30716 |  | NEUMIN PRODUCTION CO. | 103 FANNIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 | 1530 | 2004-01-08 | 2004 | [6 empty] | 28-83-04 | 96-30-37 | OFFSHORE |  | STATE TRACK | 47 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 121.7182 | 190.0514 | 100 | 51.5789 | 100 | 138.4725 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 110025 | 2004-01-08 | 60 | 813 | NO | YES | NO | NO | NO | NO | ROBERT C. SERRATA | 3619878914 | ROBERTS@FTPC.FPCUSA.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 2.37 | 0.2 | N/A | 24000 | SMLS | N/A | N/A |  | OTHER | ABOVE THE WATER |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | OTHER | ATMOSPHERE | YES | 1952 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040007 | 2004-01-21 16:15 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1540 | 2003-12-26 | 2003 |  |  | LA |  | 766-32 + 0.0 | 3+26 | 1860796.81 | -74780.63 | OFFSHORE |  | EUGENE ISLAND | 266F |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 51236.2379 | 109275.4496 | 5000 | 2931.6239 | 75000 | 106343.8257 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 709025 | 2003-12-26 | 918 | 1250 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 12.75 | 0.38 | API | 46000 | SEAMLESS |  | AMERICAN STEEL | 1971 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1971 | NO | [57 empty] | AFTER A 2 FT. DIA. BUBBLE CIRCLE WAS SPOTTED, APPROXIMATELY 200 FT. NE OF EUGENE ISLAND BLOCK 266F, A PIN HOLE LEAK WAS DISCOVERED ON THE 12 IN. 766-32 LINE. INTERNAL CORROSION WAS DETERMINED TO BE THE CAUSE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040008 | 2004-01-22 | ORIGINAL | 25169 |  | SOUTH CAROLINA PIPELINE CORP | 105 NEW WAY ROAD (PO BOX 102407) | COLUMBIA | RICHLAND | SC | 29224-2407 | 1217 | 2003-12-17 | 2003 | GEORGETOWN | GEORGETOWN | SC | 29440 |  | 3139+00 | 33 22' 17" | 79 17' 16" | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE |  |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 51532.8625 | 102622.7065 | 13000 | 7622.2222 | 42000 | 59552.5424 | 25000 | 35447.9419 | YES | NO | NO | YES | 2 | PRECAUTIONARY | 0 | 58 | 708402 | 2003-12-17 | 150 | 275 | NO | NO | NO | YES | NO | NO | GLEN BOATWRIGHT | 8032171812 | GBOATWRIGHT@SCANA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 12 | 0.25 |  |  | ERW |  |  | 1970 |  |  | 72 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | SOIL BORE TESTS | YES | 12 | 10 | 2003 | ONE-CALL SYSTEM | NO | [40 empty] | AT 12:17 PM ON DECEMBER 17, 2003, SOUTH CAROLINA PIPELINE CORPORATION RECEIVED NOTIFICATION THAT A THIRD PARTY CONTRACTOR CONDUCTING SOIL BORE TESTS HAD STRUCK A NATURAL GAS TRANSMISSION PIPELINE ON FRONT STREET IN THE CITY OF GEORGETOWN NEAR METER & REGULATION STATION 27-200. THE PIPELINE WAS PUNCTURED BY THE SAMPLING APPARATUS AND GAS WAS ESCAPING. THE GEORGETOWN FIRE DEPARTMENT AND POLICE DEPARTMENT RESPONDED AND ISOLATED THE AREA. SOUTH CAROLINA PIPELINE CORPORATION PERSONNEL RESPONDED TO THE SCENE, EVALUATED THE SITUATION, AND ISOLATED THE IMPACTED SECTION OF LINE. THE LINE WAS SUBSEQUENTLY REPAIRED BY CUTTING OUT THE DAMAGED SECTION OF PIPE AND REPLACING IT WITH PRE-TESTED PIPE. THE INTERNAL INVESTIGATION OF THE INCIDENT DETERMINED THAT THE THIRD PARTY CONTRACTOR APPARENTLY DRILLED OUTSIDE OF THE AREA THAT HAD BEEN PREVIOUSLY CLEARED BY SOUTH CAROLINA PIPELINE CORPORATION RIGHT-OF-WAY DEPARTMENT PERSONNEL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040009 | 2004-01-29 16:40 | SUPPLEMENTAL FINAL | 2731 |  | CHEVRON PIPELINE CO | 4800 FOURNACE PLACE | BELLAIRE | HARRIS | TX | 77401 | 112 | 2004-01-09 | 2004 | [6 empty] | 29 57.815' | 88 43.284' | OFFSHORE |  | CHANDELEUR | 3 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4735000 | 2942424.6093 | 6306417.314 | 288000 | 148547.3684 | 4447000 | 6157869.9456 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 710044 | 2004-01-09 | 950 | 1440 | YES | NO | NO | NO | NO | NO | HENRY L. LEGER | 3376548915 | HENRYLEGER@CHEVRONTEXACO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 12.75 | 312 | GRADE API 5 LX-46 | 46000 | ERW | N/A | J&L STEEL CORP. | 1964 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE INCIDENT OCCURED IN THE GULF OF MEXICO IN OCS WATERS OFF THE COAST OF LOUISIANA IN THE NORTHEAST QUADRANT OF CHANUELEUR BLOCK 3. A 3RD PARTY LIFT-BARGE IN TRANSIT FROM A LOCATION FURTHER OFFSHORE, INADVERTENTLY LOWERED ITS JACK-UP LEGS ON TO THE PIPELINE CAUSING IT TO RUPTRUE. AT THE TIME OF THE INCIDENT, THE LIFT-BARGE WAS IN ROUTE, THE SEAS WERE ROUGH; IT WAS THE CAPTAIN'S INTENTION TO LOWER THE JACK-UP LEGS TO LIFT THE BARGE ABOVE THE WAVES AND WAIT IN THAT POSITION UNTIL THE ROUGH SEAS SETTLED BEFORE CONTINUING HIS JOURNEY. THE LIFT-BARGE WAS NOT CONTRACTED BY NOR WAS IT DOING WORK FOR CHEVRON PIPE LINE COMPANY. IN ADDITION, THE INCIDENT OCCURED IN OPEN WATERS; THERE WERE NO PLATFORMS IN THE AREA OF THE INCIDENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040010 | 2004-01-22 | ORIGINAL | 9011 |  | J - W GATHERING CO | 126 POST OAK ROAD | KILGORE | GREGG | TX | 75662 | 700 | 2003-12-23 | 2003 | FRIERSON | DESOTO | LA | 71027 | 300 YDS SW OF I-49 |  | 32 13' 05.3" | 93 42' 35.7" | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | TREE FELL ON PIPELINE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46041 | 29565.7913 | 61124.3833 | 5000 | 2931.6239 | 39829 | 56474.2431 | 1212 | 1718.5162 | NO | NO | NO | NO | 0 |  | 0 | 40 | 708826 | 2003-12-23 | 690 | 983 | NO | YES | NO | NO | NO | NO | GLENN P BESSINGER | 9039833409 | GBESSINGER@JWOPERATING.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 6 | 0.16 | API 5L | 42000 | ERW |  | UNKNOWN | 1974 | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | TREE ON BANK OF BAYOU FELL ACROSS PIPELINE |  | A DEAD TREE ON BANK OF RAMBIN BAYOU FELL INTO BAYOU AND STRUCK PIPELINE CAUSING LINE TO FAIL. AT 7:00 A.M. ON 12-23-03, OUR FIELD OPERATOR NOTICED CHANGES IN PIPELINE FLOWS AND PRESSURES. BY 7:40 A.M. ON 12-23-03 WE HAD LEAK SECURED BY CLOSING BLOCK VALVES ON EITHER SIDE OF LEAK THEREBY ISOLATING THE LEAK. INCIDENT WAS REPORTED TO THE LOUSIANA STATE POLICE AT 7:45 A.M. ON 12-23-03. CREWS WERE CALLED OUT AND CLEAN-UP/REMEDIATION AND REPAIRS WERE COMMENCED AROUND 11:00 A.M. ON 12-23-03.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040011 | 2004-01-24 | SUPPLEMENTAL FINAL | 31783 |  | CENTRAL NEW YORK OIL AND GAS CO LLC | 800 ROBINSON RD | OWEGO | TIOGA | NY | 13827 | 832 | 2004-01-22 | 2004 | NICHOLS | TIOGA | NY | 13827 | CNYOG WELL 13-2 |  | 6715' S OF 42 2' 30 | 4132' E OF 76 17'30 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | ROUTINE GAS BLOWDOWN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150150 | 93568.6437 | 207786.0466 | 150 | 77.3684 | 150000 | 207708.6782 | 0 | 0 | NO | NO | YES | NO | 0 |  |  | 25 | 711295 | 2004-01-22 | 2597 | 3250 | YES | NO | NO | NO | NO | NO | MAUREEN BALL | 6076890195 | MBALL@CNYOG.COM | TRANSMISSION | OTHER | NO KNOWN EQUIP FAILURE | STEEL |  | NO | NO | NO | OTHER | WELL SITE EQUIP | [9 empty] | INSIDE/UNDER BUILDING |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | UNKNOWN IGNITION SOURCE IN CLASS I DIVISION I ENVIRONMENT. |  | TWO CNYOG OPERATORS WERE PERFORMING A ROUTINE MAINTENANCE OPERATION TO CLEAN A STRAINER BASKET IN THE GAS LINE ON A STRAINER SKID WHICH IS INTEGRATED INTO THE SURFACE FACILITIES OF ONE OF THE COMPANY'S TEN NATURAL GAS STORAGE WELLS. THE SURFACE FACILITIES FOR THE WELL ARE LOCATED IN A PROTECTIVE METAL BUILDING SPACE WITH AN ELECTRICAL CLASSIFICATION OF CLASS I DIVISION I. THE OPERATORS CLOSED THE TWO ISOLATION VALVES AT THE PERIMETER OF THE BUILDING AND OPENED THE LARGE ROLL-UP DOOR AND PERSONNEL DOOR AT ONE END OF THE SPACE, THE DOUBLE PERSONNEL DOOR AT THE OTHER END OF THE SPACE, AND THE FOUR 4' X 4' VENTS ON THE SIDE OF THE BUILDING (TWO ON EACH SIDE) FOR VENTILATION DURING THE VENTING PROCESS. THEY STARTED THE VENTING PROCESS BY PARTIALLY OPENING TWO SMALL BALL VALVES AND THEN BOTH WALKED OUTSIDE THE BUILDING TO AWAIT COMPLETION OF THE VENTING PROCESS IN ACCORDING WITH THE ESTABLISHED PRACTICE. AN UNKNOWN IGNITION SOURCE IGNITED THE GAS IN THE SPACE. SMALL FIRES AT THE TWO VENTING VALVES BURNED FOR 10-15 MINUTES UNTIL THEY WERE EXTINGUISHED BY A FIRE EXTINGUISHER JUST BEFORE THEY BURNED OUT. THERE WAS NO APPARENT DAMAGE TO ANY OF THE SURFACE EQUIPMENT OR GAS PIPING EXCEPT FOR DAMAGE TO INSTRUMENTATION AND ELECTRICAL CONDUIT AND FOR SOME POSSIBLE HEAT RELATED DAMAGE TO ONE SECTION OF PIPING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040012 | 2004-01-27 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1940 | 2004-01-02 | 2004 | GRANGER | UINTA | WY |  | 413.7 | 1151+67 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108045 | 64863.5875 | 76148.4473 | 84545 | 43607.4211 | 23500 | 32541.0262 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 10 | 709620 | 2004-01-03 | 560 | 850 | NO | YES | NO | NO | NO | NO | LARRY D OLSEN | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 30 | 0.31 | X-70 | 1456 | GIRTH WELD | N/A | IPSCO CORPORATION | 2003 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 9 | 19 | 2003 | WATER |  | 8 | 1230 | [12 empty] | SMALL CRACK IN GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040013 | 2004-02-09 09:25 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | -7-7002 | 1640 | 2004-01-14 | 2004 |  |  | LA |  | 527A-301+17.25 |  | 29*04.08' | 89*34.86' | OFFSHORE |  | WEST DELTA | 46 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358564 | 218019.8196 | 334808.7645 | 186094 | 95985.3263 | 172470 | 238823.4382 | 0 | 0 | NO | NO | NO | NO | 0 |  | 8 |  | 710370 | 2004-01-12 | 820 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 30 | 0.5 | API | 60000 | DSAW |  |  | 1979 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1979 | NO | [57 empty] | FOLLOWING THE DISCOVERY OF A BUBBLE CIRCLE IN WEST DELTA BLK. 46, IN THE AREA OF THE TGP 30 IN. W.D. BLK. 61A LINE (527A-300), DIVERS LOCATED A PIN HOLE LEAK. A PLIDCO REPAIR CLAMP WAS INSTALLED TO REPAIR THE PIPE. INTERNAL CORROSION WAS IDENTIFIED AS THE PROBABLE CAUSE OF THE INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040014 | 2004-02-09 12:09 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1815 | 2004-01-13 | 2004 | PORT SULPHUR | PLAQUEMINES | LA | 70083 |  |  | 29^30'57 | 89^43'46 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR CAP LEAK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 52679.6226 | 109012.2338 | 10000 | 5157.8947 | 75000 | 103854.3391 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 710265 | 2004-01-11 | 915 | 1000 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | COMP. CAP ON ENGINE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1969 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 8 |  |  | COMPRESSOR CAP BLEW OFF NUMBER 6 COMPRESSOR ON UNIT 1A (INGERSOLL RAND KVT-616)ENGINE, WHICH WAS ON LINE AT FULL SPEED AND UNDER LOAD DURING THE INCIDENT. THERE WAS DAMAGE TO THE BUILDING, BUT NO IGNITION OCCURRED, AND THERE WAS NO FIRE OR INJURIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040015 | 2004-01-15 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1348 | 2003-12-17 | 2003 |  | SAINT MARY | LA |  |  | 3942+48 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230000 | 147438.5919 | 311152.3934 | 18000 | 10553.8462 | 212000 | 300598.5472 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 708370 | 2003-12-17 | 750 | 877 | NO | YES | NO | NO | NO | NO | MARY S FRIEND, SR ENGINEER | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 20 | 0.28 |  | 52000 | SQUARE SEAM |  | AO SMITH | 1953 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1954 | YES | 8 | 0 | [55 empty] | A SMART PIG WAS RUN ON THE LINE IN OCTOBER 2003. THE SMART PIG IDENTIFIED A CORROSION ANOMALY AT THIS SITE. COLUMBIA WAS IN THE PROCESS OF OBTAINING THE NECESSARY PERMITS WHEN THE LEAK WAS DISCOVERED BY THE SURVEY CREW. THE LINE WAS BLOWN DOWN AND REMOVED FROM SERVICE UNTIL THE BAYOU CROSSING COULD BE REPLACED. COLUMBIA REPAIRED THE LEAK BY REPLACING THE CROSSING WITH 530 FEET OF 20', X-52, .375 WALL PIPE WITH THIN FILM COATING. THE CROSSING UNIT WAS COVERED BY CONCRETE MATS AND ROCK SHIELD. A PREVIOUS LEAK ON THIS CROSSING IN 1985 HAD BEEN REPAIRED WITH A CLAMP. THE CLAMP AND PIPE WAS ALSO REPLACED DURING THE CROSSING REPLACEMENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040016 | 2004-02-09 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 413 | 2004-01-11 | 2004 | CAMARILLO | VENTURA | CA |  | 10.27 | 542+80.7 | 34.25713 | -119.109030 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9000 | 5579.5607 | 11593.5856 | 1000 | 515.7895 | 8000 | 11077.7962 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 58 | 710221 | 2004-01-11 | 435 | 562 | YES | NO | NO | NO | NO | NO | W JEFF KOSKIE | 2132443283 | WKOSIE@SEMPRAUTILITIES.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1979 | 0.6 | 0.47 | 50-15 | 5 |  |  |  | 1979 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | VEHICLE'S DRIVER LOST CONTROL, LEAVING ROADWAY AND FLIPPING OVER, LANDING UPSIDE DOWN ON REGULATOR STATION COMPONENTS,BREAKING A 1/2" HIGH PRESSURE NIPPLE. DRIVER WAS FOUND TO BE SEATBELTED IN PLACE, UPSIDE DOWN. CORNER REPORT STATES CAUSE OF DEATH POSITIONAL ASPHYXIA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040017 | 2004-02-19 10:07 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1146 | 2004-01-26 | 2004 | CLENDENIN | KANAWHA | WV | 25045 |  | 16+57 LINE WB | N38'29''20''' | W81'18''53''' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167677 | 99597.6165 | 86486.0316 | 167677 | 86486.0316 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 27 | 711612 | 2004-01-26 | 743 | 750 | NO | NO | YES | NO | NO | NO | MARK A. NEWMAN | 3043572869 | MNEWMAN@NISOURCE.COM | TRANSMISSION | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 2000 | [5 empty] | RELIEF, 8X10X10 | ANDERSON-GREENWOOD | 1979 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | MOISTURE IN THE CONTROL LINE TO THE RELIEF VALVE CAUSED THE VALVE TO MALFUNCTION. THE MOISTURE IN THE CONTROL FORM INTO ICE AND THEREFORE WOULD NOT ALLOW THE RELIEF VALVE TO CLOSE. THE RELIEF VALVE WAS ALLOWED TO VENT UNTIL A VALVE POSITIONED BELOW THE RELIEF VALVE WAS CLOSED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040018 | 2004-02-11 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1700 | 2004-01-13 | 2004 | IRVINGTON | MOBILE | AL | 36544 | 6 | 365+57 | 88.21300W | 30.47168N | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110375 | 66886.147 | 96345.1569 | 65015 | 33534.0526 | 45360 | 62811.1043 | 0 | 0 | NO | NO | NO | NO | 0 |  | 56 | 0 | 710482 | 2004-01-13 | 851 | 976 | YES | NO | NO | NO | NO | NO | F T WALDROP, AREA BUSINESS LEADER | 2288329351 | FORREST.WALDROP@GULFSOUTHPL.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1992 | 30 | 0.5 | X-65 | 65000 | ERW | N/A | BERG STEEL PIPE CORP | 1991 | UNDER GROUND |  | 56 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | PIPELINE WAS EXCAVATED AS A RESULT OF AN INTERNAL IN-LINE INSPECTION THAT INDICATED AN ANOMALY AT THE ABOVE LOCATION. DURING EXCAVATION GAS LEAKAGE WAS DETECTED AND AFTER THE PIPE WAS EXPOSED A DETERMINATION THE LEAKAGE WAS FROM A CRACK A BUTT WELD. REPAIR WAS MADE BY REPLACING A 10 FEET OF PIPE IN THE AREA OF THE BUTT WELD. THE SECTION OF PIPE CONTAINING THE WELD HAD BEEN SENT FOR METALLURGICAL ANALYSIS AND WE ARE WAITING FOR COMPLETION OF ANALYSIS TO CLASSIFY CAUSE. 3-23-04 THE METALLURGICAL CONSULTANTS, INC ON THE GIRTH WELD CRACK/WELD FROM THE 30" MOBILE BAY INDEX 880 LINE INDICATES. "THE EXACT CAUSE OF THE CRACK WAS NOT DETERMINED. THE CRACK WAS LIKELY DUE TO EITHER HYDROGEN-INDUCED COLD CRACKING, OR SOME UNUSUAL CONDITION THAT OCCURRED DURING PIPELINE CONSTRUCTION. THE CRACK WAS NOT ASSOCIATED WITH A WELDING DEFECT, FATIGUE, INTERNAL OR EXTERNAL CORROSION OR ANY OBVIOUS METALLURGICAL DEFECIENCY"
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040019 | 2004-02-09 | ORIGINAL | 31690 |  | HESCO UTILITY CO LLC | 500 N SHORELINE #608 | CORPUS CHRISTI | NUECES | TX | 78471 | 1100 | 2004-01-12 | 2004 | HARLINGEN | CAMERON | TX | [5 empty] | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE |  |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 3086.7729 | 6054.6876 | 1000 | 515.7895 | 4000 | 5538.8981 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 | 30 |  | 2004-01-12 | 120 | 1080 | NO | NO | NO | NO | NO | NO | GARY HOLT | 7138063648 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1996 | 4 | 0.19 | X-42 | 42000 | ERW | N/A |  |  | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR |  |  | YES | 1 | 12 | 2004 | ONE-CALL SYSTEM | YES | [40 empty] | CONTRACTOR (BALLENGER CONSTRUCTION) HIT LINE WHILE LAYING 60" STORM DRAIN LINES IN SAME TEX DOT R.O.W. CONTRACTOR VEERED OFF THEIR CONSTRUCTION LINE INTO OUR PIPE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040020 | 2004-02-23 11:51 | SUPPLEMENTAL FINAL | 1007 |  | K N INTERSTATE GAS TRANSMISSION CO | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1500 | 2004-02-13 | 2004 | TILDEN | MADISON | NE | 68781 | 790+97 |  | 42 01.940 | 97 46.91 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LINE HIT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16308 | 9788.6567 | 11444.0781 | 12818 | 6611.3895 | 3490 | 4832.6886 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 32 | 713290 | 2004-02-13 | 610 | 935 | NO | NO | YES | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 2.37 | 0.15 |  |  | ERW |  | YOUNGSTOWN | 1951 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | MADISON COUNTY ROAD MAINTENANCE CREW STRUCK AND PUNCTURED LINE WITH ROAD GRADING EQUIPMENT WHILE WHILE DOING ROAD MAINTENANCE ACTIVITY. GAS WAS RELEASED TO THE ATMOSPHERE AS A RESULT OF THE LINE HIT. THE COUNTY ROAD MAINTENANCE CREW HAD NOT MADE A LINE LOCATE NOTIFICATION. THE PIPELINE WAS REPAIRED AND PUT BACK IN SERVICE WITH THE COVER REQUIRED BY 192.327.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040021 | 2004-02-24 | ORIGINAL | 2704 |  | CONSOLIDATED EDISON CO OF NEW YORK | 1615 BRONXDALE AVE | BRONX | BRONX | NY | 10462 | 1000 | 2004-02-19 | 2004 | QUEENS |  | NY |  |  |  | -73.88 | 40.76 | ONSHORE | 4 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO | NO | NO | 0 |  | 46 | 36 | 713767 | 2004-02-19 | 274 | 350 | NO | NO | NO | NO | NO | NO | MARIO SELLITTU | 7183192310 | SELLITTIM@CONED.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.38 | ASTM A139 GRADE B | 35000 | SPIRAL WELD |  | UNKNOWN | 1949 | UNDER PAVEMENT |  | 60 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | SPIRAL |  | MATERIAL DEFECT |  |  |  | 11 | 20 | 1950 | OTHER | AIR | 48 | 425 | [12 empty] | GAS READINGS WERE DETECTED DURING A PREVENTATIVE LEAKAGE SURVEY OF THE TRANSMISSION MAIN. UPON EXCAVATION, A PINHOLE LEAK WAS FOUND ON THE MANUFACTURER'S SPIRAL WELD AND OCCURRED AT A POINT OF POROSITY IN THE WELD.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040022 | 2004-03-15 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1000 | 2004-02-05 | 2004 | EARLVILLE |  | IA | 52041-9743 | MP 57.36 |  | 42.4355 | -91.2319 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82526 | 49667.7096 | 61856.4002 | 60326 | 31115.5158 | 20200 | 27971.4353 | 2000 | 2769.449 | NO | NO | NO | NO | 0 |  | 2 | 45 | 712519 | 2004-02-05 | 894 | 960 | NO | NO | NO | NO | YES | NO | JACK GUINN, SENIOR PIPELINE SAFETY ENGINEER | 4023987396 | JACK.GUINN@NNGCO.COM | TRANSMISSION | OTHER | FARM TAP RISER | STEEL |  | NO | NO | NO | OTHER | FARM TAP RISER | 1962 | [5 empty] | 1" BALL VALVE | CRANE COMPANY |  | ABOVE GROUND |  | 0 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | AT APPROXIMATELY 10:00 AM ON THURSDAY, FEBRUARY 5, 2004, A PICKUP TRUCK PULLING A LIVESTOCK TRAILER SLID OFF THE ROAD AND STRUCK A FARM TAP ON NORTHERN NATURAL GAS COMPANY'S 26" LINE NEAR EARVILLE, IA. THE DRIVER OF THE PICKUP AND TRAILER INDICATED THE ETREME SLICK CONDITIONS ON THE GRAVEL ROAD, COMBINED WITH SHIFTING WEIGHT IN THE TRAILER DUE TO CATTLE MOVEMENT AS THE TRAILER MADE THE CURVE, CAUSED HIM TO LOSE CONTROL AND GO OFF THE ROAD STRIKING THE FARM TAP SETTING. THE FARM TAP BROKE AT THE ABOVE GROUND VALVE ON THE ONE-INCH PIPE RISER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040023 | 2004-03-29 12:11 | ORIGINAL FINAL | 10030 |  | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228 | 1523 | 2004-03-08 | 2004 | SNOWMASS VILLAGE | PITKIN | CO | 81615 |  |  | 106 55.87 | 39 13.106 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 31159.8487 | 69236.2261 | 0 | 0 | 50000 | 69236.2261 | 0 | 0 | NO | YES | NO | YES | 400 | PRECAUTIONARY | 1 | 30 | 715460 | 2004-03-08 | 180 | 40 | NO | NO | NO | YES | NO | YES | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1995 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20040024 | 2004-03-26 | ORIGINAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 820 | 2004-02-26 | 2004 | HEIDELBERG | JONES | MS | 39439 | 740.50 |  | 31.8154 | -89.0491 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | 1/2" NIPPLE OF 3 WAY VALVE BROKE | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 100 | 62.3197 | 138.4725 | 0 | 0 | 100 | 138.4725 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 714442 | 2004-02-26 | 514 | 800 | NO | NO | NO | NO | YES | NO | CHRISTINA YORK ENGINEER II | 7132152758 | CHRISTINA.L.YORK@WILLIAMS.COM | TRANSMISSION | OTHER | FITTING (REDUCER) / 1/2" NIPPLE | STEEL |  | NO | NO | NO | OTHER | YARD PIPING | [9 empty] | ABOVE GROUND |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | EMPLOYEES PROCEEDED TO BLOWOFF M18B TO SHORT CYCLE VALVE. THEY FIRST INSTALLED A YALE CAP ON THE BLOWOFF STACK OF THE VALVE AND CLOSED THE POWER GAS SUPPLY SO THAT WHEN IT OPERATED IT WOULD NOT ACTUALLY BLOW ANYTHING DOWN. THEY THEN ATTEMPTED TO OPERATE THE 3 WAY VALVE ON THE EMERGENCY BLOW DOWN SIGNAL LINE COMING INTO THE VALVE TO MAKE THE BLOW OFF VALVE OPERATE. THE 3 WAY VALVE WOULD NOT OPERATE SO THEY DECIDED TO VENT THE POWER GAS LINE OFF IN ORDER TO CHECK THE OIL LEVEL IN THE OILER. EMPLOYEES THEN AGAIN ATTEMPTED TO TURN THE HANDLE ON THE 3 WAY VALVE. AS THEY STARTED TO TURN THE HANDLE, THE 1/2" NIPPLE THAT IS ON THE UPSTREAM SIDE OF THE 3 WAY VALVE BROKE INTO RELEASING HIGH PRESSURE GAS. THE EMPLOYEE SUFFERED ABRASIONS, SWELLING AROUND THE EYES, AND FOREIGN MATERIAL IN HIS EYES AT THE TIME OF THE INCIDENT, RESULTING IN ONE OVERNIGHT STAY IN THE HOSPITAL.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040025 | 2004-04-05 14:07 | SUPPLEMENTAL | 2714 |  | DOMINION TRANSMISSION INC | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 1545 | 2004-03-12 | 2004 | BIG RUN | JEFFERSON | PA | 15715 | BIG RUN COMP. STATION |  | 4057-50.0 | 78-51-30.0 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53000 | 31481.203 | 27336.8421 | 53000 | 27336.8421 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 15 | 715802 | 2004-03-12 | 404 | 45 | YES | NO | NO | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C_SCHWOEBLE@DOM.COM | TRANSMISSION | OTHER | ESD SYSTEM |  |  | NO | NO | NO | OTHER | COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM | 1975 | [8 empty] | OTHER | COMPRESOR STATION EMERGENCY SHUTDOWN SYSTEM |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | DISCHARGE FIRE GATE / VALVE ACTUATOR | [10 empty] | ON 03/12/04 AT APPROXIMATELY 12 AM, BIG RUN COMPRESSOR STATION LOST PURCHASE POWER. AT APPROXIMATELY 2:45 AM, THE UPS BACKUP BATTERIES FOR COMPUTER CONTROLS LOST THEIR ELECTRIC CURRENT CHARGE. WITH NO BACKUP BATTERIES OPERATING AS THEY SHOULD, AN ESD OCCURRED ALTHOUGH THE DISCHARGE FIRE GATE DID NOT MOVE TO THE CLOSED POSITION. THEREFORE, THE COMPRESOR STATION WAS NOT ISOLATED FROM THE PIPELINE TL-280. THE SUCTION FIRE GATE DID OPERATE PROPERLY. NATURAL GAS PROCEEDED TO VENT OUT OF THE DISCHARGE HEADER FROM THE STATION AND PIPELINE TL-280. THE TUBING LINE FOR THE PILOT AIR TO THE OPERATOR WAS BELIEVED TO HAVE SOME MOISTURE / CONDENSATE THAT COULD HAVE POSSIBLY FROZEN DUE TO BELOW FREEZING TEMPERATURES PREVENTING THE VALVE TO OPERATE. A FULL ESD TEST WAS PERFORMED AFTER THE VALVE WAS INSPECTED. ALL COMPONENTS WORKED PROPERLY. TOTAL VALVE MOVEMENT WAS COMPLETED IN 15.4 SECONDS. THE ESD SYSTEM WAS RESET AND THE UNIT WAS PUT BACK ON LINE AT 17:00. STATION PERSONNEL MONITORED CONDITIONS UNTIL 20:00, WHEN CONDITIONS WERE BACK TO NORMAL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040026 | 2004-04-05 14:30 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION INC | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 1930 | 2004-03-21 | 2004 | NASHPORT | LICKING | OH | 43834 |  | 6242+75 | N40-04.269' | W82-11.723' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 178195.4887 | 154736.8421 | 300000 | 154736.8421 | 0 | 0 | 0 | 0 | NO | NO | NO | YES | 70 | PRECAUTIONARY | 1 | 30 | 716665 | 2004-03-21 | 820 | 850 | YES | NO | NO | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C_SCHWOEBLE@DOM.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1992 | [5 empty] | ROCKWELL 8" PLUG VALVE | SHAFER VALVE COMPANY (ACTUATOR) | 1992 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | VALVE ACTUATOR | [10 empty] | DISCHARGE VENT AT NEWARK STATION OPENED AT 7:30 PM ON 03/21/04. IT IS SUSPECTED THAT THE ACTUATOR CAUSED THE 8" DISCHARGE VENT VALVE TO OPEN DUE TO A LEAK AROUND THE SEAT / STEM AREA. NATURAL GAS VENTED FOR 1.5 HOURS. DTI GAS CONTROL WAS ABLE TO ISOLATE GAS VENTING VIA SCADA. APPROXIMATLEY 70 PEOPLE WERE EVACUATED BY THE LOCAL EMA DUE TO SMELL OF NATURAL GAS. THERE WAS NO PROPERTY DAMAGE, INJURIES OR FATALITIES.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040027 | 2004-04-05 15:50 | ORIGINAL | 30716 |  | NEUMIN PRODUCTION CO. | 103 FANNIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 | 715 | 2004-03-27 | 2004 | POINT COMFORT | CALHOUN | TX | 77978 | ST 38 |  | 28-37-44.200 | 96-31-53.28407 | OFFSHORE |  | LAVACA BAY | 38 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 96.4495 | 210.2876 | 5 | 2.5789 | 150 | 207.7087 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 20040812 | 2004-03-27 | 500 | 800 | NO | YES | NO | NO | NO | NO | ED VAVRA | 3619878914 | ROBERTS@FTPC.FPCUSA.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 2 | 0.2 | GRADE B | 24000 | SMLS | N/A | N/A |  | ABOVE GROUND |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | GENERAL CORROSION |  | OTHER | INTERNAL CORROSION | YES | 1986 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040028 | 2004-03-30 | ORIGINAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1430 | 2004-02-27 | 2004 | N/A | N/A |  | N/A | N/A | 5+00 | 28.137569 | 92.952933 | OFFSHORE |  | EAST CAMERON | 335 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 155739.6508 | 344408.5028 | 2040 | 1052.2105 | 247960 | 343356.2923 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 714574 | 2004-02-27 | 1050 | 1440 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS SR. ENGINEER | 7139897473 | MHOVIS@PANHANDLEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 10 | 0.5 | API5LX | 42000 | SEAMLESS | N/A | U.S. STEEL | 1980 | UNDER WATER |  | 38 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1980 | NO | [57 empty] | SUBJECT LEAK WAS DISCOVERED ON FEBRUARY 27, 2004 @ 2:30 P.M. THE PIPELINE WAS IMMEDIATELY SHUT IN AND INVESTIGATION AND REPAIR INITIATED. THE CAUSE OF THE LEAK WAS DETERMINED TO BE TWO PINHOLE LEAKS ON THE BOTTOM OF THE PIPE CAUSED BY INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED TO REPAIR THE ANOMALY. THE LINE WAS RETURNED TO SERVICE ON MARCH 14, 2004. THE PIPELINE WAS SUBSEQUENTLY CLEANED AND BATCH-TREATED WITH BIOCIDES TO PREVENT ADDITIONAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040029 | 2004-03-30 | SUPPLEMENTAL FINAL | 792 |  | ATLANTA GAS LIGHT CO | 630 WEST CHERRY STREET | JESUP | WAYNE | GA | 31545 | 205 | 2004-02-22 | 2004 | JESUP | WAYNE | GA | 31545 | NORTH OF OAK LANDING & BE | N/A |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202091 | 122709.6063 | 183675.3215 | 110670 | 57082.4211 | 91421 | 126592.9004 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 35 | 714033 | 2004-02-22 | 978 | 1066 | YES | NO | NO | NO | NO | NO | SCOTT CRIDER,DESIGN ENGINEER | 4045844697 | SCRIDER@AGLRESOURCES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1999 | 12 | 0.22 | API-5L-X52 | 52000 | ELECTRIC-RESISTANCE WELDED (ERW) | N/A | UNKNOWN |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | OTHER | LOGGING | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | THIS EVENT IS STILL UNDER INVESTIGATION. THERE HAS BEEN RECENTLY LOGGING AND UNAUTHORIZED GRADING WITHIN THE RIGHT-OF-WAY OF THIS PIPE. ATLANTA GAS LIGHT COMPANY'S RIGHT-OF-WAY SURVEYOR, WHO HAD WALKED THIS LINE A WEEK BEFORE THE INCIDENT, REPORTED SIGNIFICANT LANDSCAPE AND GRADING CHANGES. ATLANTA GAS LIGHT COMPANY WAS MADE AWARE OF THE PIPELINE FAILURE THROUGH MONITORING PRESSURE LOGS AT JESUP AND BELLE VISTA, DOWNSTREAM OF THE FAILURE. 6-28-04 ON SUNDAY, FEBRUARY 22, 2004 AT APPROXIMATELY 1:30 AM, A SECTION OF THE BRUNSWICK LATERAL 7.5 MILES SOUTH OF THE DOCTORTOWN (JESUP) MAINLINE VALVE (MLV) FAILED. THE PRESSURE DROP WAS FIRST NOTED BY ATLANTA GAS LIGHT COMPANY PERSONNEL AT 1:35AM. THIS LINE IS LOCATED ON AN EASEMENT OWNED BY AGLC. IN THE WEEK PRIOR TO THE INCIDENT, THE RIGHT-OF-WAY WAS INSPECTED BY AGLC PERSONNEL AND THE GRASS WAS MOWED. AT THE TIME OF THAT INSPECTION, NO UNUSAL CONDITIONS WERE NOTED. CONVERSELY, IN THE POST-INCIDENT INSPECTION THE FOLLOWING FACTS WERE MOTED: 1. HEAVY MACHINERY USED IN CONSTRUCTION AND GRADING ACTIVITIES WAS FOUND PARKED IN THE RIGHT-OF-WAY. 2. A DIRT PATH HAD BEEN ESTABLISHED ROUGHLY PERPENDICULAR TO THE PIPE ACROSS THE RIGHT-OF-WAY. TIRE TRACKS WERE NOTED, INDICATING THAT THE HEAVY MACHINERY HAD CROSSED THE PIPE AT THIS LOCATION. 3. A DRAINAGE CULVERT HAD BEEN INSTALLED ROUGHLY PERPENDICULAR TO AND UNDER THE PIPE ACROSS THE RIGHT-OF-WAY. VISUAL INSPECTION OF THE RUPTURED PIPE AND FRAGMENTS FOUND ON-SITE SHOWED A GOUGE IN THE PIPE. THE RUPTURE OCCURRED AT THE CULVERT WHERE THE SOIL WAS SATURATED. SUBSEQUENT LABORATORY ANALYSIS INDICATED THAT THE GOUGE CONTAINED FRAGMENTS OF FOREIGN METALS, INDICATING DAMAGE BY A METALLIC OBJECT-MOST LIKELY THE HEAVY CONSTRUCTION EQUIPMENT SEEN ON-SITE. IT WAS DETERMINED THAT EMBRITTLEMENT DUE TO HYDROGEN STRESS CRACKING OCCURRED AT THE SITE OF THE GOUGE. THIS CRACKING WAS ACCELERATED DUE TO THE HIGH MOISTURE CONTENT OF THE SURROUNDING SOIL, AND ULTIMATELY LED TO THE FAILURE OF THE PIPE.
2022-01-31 10:32 | YES | YES | GG (Gas Gathering) | 20040030 | 2004-04-14 10:12 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | ONE WILLIAMS CENTER | TULSA | TULSA | OK | 74101 | 1230 | 2004-02-26 | 2004 |  | SAN JUAN | NM |  |  | N/A | 36.50 .11 | 108.5.50 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 20000 | 12463.9395 | 27694.4904 | 0 | 0 | 20000 | 27694.4904 | 0 | 0 | NO | NO | YES | NO | 0 |  | 0 | 15 | N/A |  | 440 | 497 | YES | NO | NO | NO | NO | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING | OTHER | CLOSURE ON PIG TRAP | STEEL |  | NO | NO | NO | OTHER | PIG TRAP | 1976 | 16 | 0 | 0 | 0 | 0 | 0 | TUBE TURN | 1976 | ABOVE GROUND |  | 0 | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 6 |  |  | EMPLOYEE ATTEMPTED TO OPEN A 12-INCH PIG LAUNCHER AT THE THOMPSON COMPRESSOR STATION WITHOUT FIRST RELIEVING THE PRESSURE. EMPLOYEE SUSTAINED INJURIES TO JAWBONE, RIBS, AND MULTIPLE LACERATIONS. EMPLOYEE WAS ADMITTED TO A LOCAL HOSPITAL AND TREATED AND RELEASED AFTER 1-1/2 DAYS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040031 | 2004-04-19 10:38 | ORIGINAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 901 | 2004-03-20 | 2004 | HADDAM | WASHINGTON | KS | 66944 | 417 | 19388.16.5 | 39 48.353 | 97 19.27 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 243655.4772 | 386619.8118 | 192500 | 99289.4737 | 177500 | 245788.6025 | 30000 | 41541.7356 | NO | YES | NO | NO | 0 |  | 1 | 54 | 716561 | 2004-03-20 | 689 | 712 | NO | NO | YES | NO | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 36 | 0.34 | 5L-X52 | 52000 | ELECTRONIC FLASH WELD |  | AO SMITH | 1958 | UNDER GROUND |  | 126 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | LONGITUDINAL TENSILE STRESSES IN EXCESS OF THE LONGITUDINAL TENSILE STRENGTH OF THE PIPE
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040032 | 2004-03-23 | SUPPLEMENTAL FINAL | 11384 |  | LENOX MUNICIPAL GAS SYSTEM | 200 S. MAIN | LENOX | TAYLOR | IA | 50851 | 2000 | 2004-02-22 | 2004 | PRESCOTT | ADAMS | IA | 50859 | PRESCOTT BORDER STATION |  | W 94.60718 | N 41.02487 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68900 | 42938.2715 | 95407.5195 | 0 | 0 | 0 | 0 | 68900 | 95407.5195 | NO | NO | NO | NO | 0 |  |  |  | 714130 | 2004-02-22 | 600 | 650 | NO | YES | NO | NO | NO | NO | LYNN CHRISTENSEN - GAS SUPERVISOR | 6413332228 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 4 | 0.19 | SCH 40 | 22 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | WASHOUT | [50 empty] | MELTING SNOW WITH ICE AND DEBRIS IN THE WATER PUSHING AGAINST THE GAS PIPE |  | AT APPROXIMATELY 8:00 PM ON FEB 22, 2004 WE RECEIVED A CALL ABOUT A POSSIBLE GAS TRANSMISSION LINE BREAK. UPON INVESTIGATION BY OUR GASMEN IT WAS DETERMINED THE LINE THAT CROSSED THE BRANCH OF THE NODAWAY RIVER HAD BROKEN. AT THIS TIME THE GAS SYSTEM WAS SHUT DOWN. THE TOWNS OF LENOX,CLEARFIELD AND BEDFORD WERE AFFECTED BY THE OUTAGE.IOWA PIPELINE WAS CONTACTED AFTER 11:00PM ON THE 22ND TO ASK THEM HOW LONG IT WOULD TAKE TO GET STARTED ON THE REPAIRS.IOWA PIPELINE ARRIVED AT 600AM ON MONDAY MORNING TO BEGIN THE WORK. A DIRECTIONAL BORE UNDER THE RIVERBED RESTORED SERVICE AND GAS WAS FLOWING AGAIN BY 630PM ON TUESDAY THE 24TH . WE ASKED FOR MUTUAL AID TO HELP TO RESTORE THE SEVICES AND BUSINESSES. THREE OTHER COMMUNITIES ASSITED US. WE HAD 10 QUALIFIED GAS PERSONNEL ASSISTED BY APPROX 30 VOLUNTEERS TO HELP IN THE LIGHTING OF PILOTS. WE HAD 100% COVERAGE OF THE TOWN BY 1:00 AM ON THE 25TH WITH COMPLETION OF EVERYONE IN THE CITIES OF LENOX AND CLEARFIELD RESTORED BY 6:30 PM ON THE 25TH .
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040033 | 2004-04-09 | SUPPLEMENTAL FINAL | 15329 |  | PEOPLES GAS LIGHT & COKE CO | 130 E RANDOLPH DRIVE | CHICAGO | COOK | IL | 60601 | 1230 | 2004-03-06 | 2004 | CHICAGO | COOK | IL | 60623 | UNKNOWN | UNKNOWN | 41.8462750 | -87.7382760 | ONSHORE | 4 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146000 | 90986.7581 | 202169.7801 | 0 | 0 | 146000 | 202169.7801 | 0 | 0 | YES | NO | NO | NO | 0 |  | 7 | 30 | 715322 | 2004-03-06 | 161 | 300 | NO | YES | NO | NO | NO | NO | JOHN J JUST, GENERAL MANAGER FIELD OPERATIONS | 7733957415 | JJJUST@PEOPLESGASDELIVERY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 20 | 0.38 | API 5LB | 3500 | UNKN | UNKN | UNKN |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | RAILROAD |  | NO |  |  |  |  | YES |  | YES | [38 empty] | THE WORKERS WERE DRIVING SHEET PILINGS INTO THE GROUND TO SUPPORT RAILROAD BED ROCKS UNDER TIES. THE WORKERS HIT PEOPLES GAS' 24" CASING AND 20" HIGH PRESSURE MAIN WITH THE SHEET PILINGS. THE 20" HIGH PRESSURE MAIN RUNS PERPENDICULARLY UNDER THE RAILROAD TRACKS. THE RAILROAD HAD CALLED JULIE, THE ONE CALL SYSTEM FOR AREA OURSIDE OF CHICAGO. ALL FACILITIES OPERATED IN CHICAGO ARE LOCATED BY CALLING CHICAGO'S ONE CALL SYSTEM, DIGGER. THE RAILROAD AND THEIR SUBCONTRACTOR ARE RESPONSIBLE TO KNOW WHEN THEIR WORK IS IN THE CITY OF CHICAGO AND THERFORE, TO NOTIFY DIGGER FOR LOCATES. 6/25/2012: FINAL REPORT WITH UPDATED PROPERTY DAMAGE/LOSS AMOUNT. 8/24/2012: FINAL REPORT WITH UPDATED INFORMATION. THE FOLLOWING REQUESTED DATA WAS NOT PROVIDED SINCE THE SECTION OF DAMAGED PIPE WAS NEVER EXPOSED AND WAS ABANDONED IN PLACE: PART A - RUPTURE MEASUREMENTS AND COST OF GAS LOST. PART D - SEAM TYPE (ALSO, EXISTING RECORDS DO NOT INDICATE SEAM TYPE). 9/27/2012: UPDATED FINAL REPORT TO INCLUDE COORDINATES FOR LOCATION OF INCIDENT. 4/22/2013: UPDATED FINAL REPORT IN PART A, QUESTION 5.D TO SELECT THE CHECK BOX TO DENOTE THAT THE INCIDENT DID OCCUR IN AN HCA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040034 | 2004-04-19 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 322 | 2004-04-08 | 2004 | GARNER | HANCOCK | IA | 50438 |  |  | 43.1130 | -93.5230 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 682.5955 | 1436.3035 | 100 | 51.5789 | 1000 | 1384.7245 | 0 | 0 | NO | NO | NO | NO | 0 | [7 empty] | NO | NO | NO | NO | NO | NO | JOHN A GORMLEY, SR. PIPELINE SAFETY SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | OTHER | NO FAILURE INVOLVED - UNPLANNED ESD ACTIVATION | OTHER | COPPER WIRE | NO | NO | NO | OTHER | LNG FACILITY | [9 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | AN ADDITIONAL ESD ACTIVATION STATION WAS INSTALLED AT THE GARNER LNG FACILITY SOMETIME DURING 2003. THE POOR DESIGN ALLOWED MOISTURE TO ENTER THE CONDUIT AND EXPLOSION PROOF BOX THAT HOUSED THE ESD ACTIVATION SWITCH. THE WIRES CORRODED AND WHEN THE BOX FILLED WITH ENOUGH WATER TO BECOME THE CONNECTION, THE ESD WAS ACTIVATED. NO INJURIES OR PROPERTY DAMAGE RESULTED FROM THE STATION SHUTDOWN. GARNER LNG WAS LIQUIFYING NATURAL GAS WHEN THE ESD ACTIVATED SO THERE WAS NO RELEASE OR SPILL. A SMALL AMOUNT OF NATURAL GAS IS VENTED DURING THE RE-START. THE PLANT WAS RETURNED TO SERVICE LATER THE SAME DAY. THIS IS BEING REPORTED BECAUSE OF COMPANY OPERATING PROCEDURE 180.109 THAT SAYS A REPORTABLE INCIDENT IS ONE WHICH RESULTS IN A UNPLANNED ESD OF A LNG FACILITY (3.1.2.). IT IS ALSO REQUIRED BY 49 CFR 191.3 AND 191.5.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040035 | 2004-04-23 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 900 | 2004-03-25 | 2004 | WOODWARD |  | IA | 50276 | MP 16.36 | N/A | 41.847 | -93.893 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235000 | 144552.508 | 268929.4844 | 65000 | 33526.3158 | 153000 | 211862.8517 | 17000 | 23540.3169 | NO | NO | YES | NO | 0 |  | 1 | 30 | 716963 | 2004-03-25 | 790 | 800 | NO | NO | NO | NO | YES | NO | JACK GUINN, SENIOR PIPELINE SAFETY ENGINEER | 4023987396 | JACK.GUINN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 16 | 0.28 | API 5LX | 46000 | FLASH WELD |  | A.O. SMITH | 1950 | UNDER GROUND |  | 65 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DRAIN TILE | NO |  |  |  |  | YES |  | YES | ACCURATE | YES | [36 empty] | AT APPROXIMATELY 9:00 A.M. ON MARCH 25, 2004, THE NORTHERN NATURAL GAS COMPANY (NORTHERN) 16-INCH DES MOINES "B" BRANCH LINE RUPTURED APPROXIMATELY 1 3/4 MILES SOUTHEAST OF WOODWARD, IA. THE FIRE AND EXPLOSION WERE REPORTED TO NORTHERN'S OPERATIONS COMMUNICATION CENTER BY A PASSERBY. NO EMPLOYEES OR THIRD PARTIES WERE PRESENT AT THE TIME OF THE RUPTURE AND THERE WERE NO INJURIES. NORTHERN DISCOVERED THAT A TILING CONTRACTOR, KUEHI BROTHERS, L.L.C. (KUEHI), INSTALLED TILING OVER THE GAS PIPELINE IN DECEMBER 2003. THERE WAS NO ONE-CALL PLACED FOR THIS EXCAVATION. NORTHERN TRANSPORTED SAMPLES OF THE DAMAGED PIPE TO BRYAN LABORATORIES, INC., IN HOUSTON, TEXAS FOR ANALYSIS. THE REPORT FROM BRYAN LAB STATES THAT THE RUPTURING OF THE PIPE WAS THE RESULT OF THE WEAKENING AFFECTS OF RECENT GOUGING AND DENTING OF THE EXTERNAL SURFACE. THE APPEARANCE AND THE SEVERITY OF THE DAMAGE ARE CONSISTENT WITH THAT RESULTING FROM EXCAVATING OR FARMING OPERATIONS. BRYAN LABS FOUND NO DEFECTS IN MATERIAL OF MANUFACTURING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040036 | 2004-04-23 | ORIGINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 845 | 2004-03-13 | 2004 | RACHEL | BROOKS | TX | 78353 | 59.4 |  | 26.922N | 98.321W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47303 | 28155.6947 | 26136.2596 | 45303 | 23366.8105 | 2000 | 2769.449 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 |  |  | 650 | 672 | YES | NO | NO | NO | NO | NO | KEVIN P. SEHY, PR. COMPLIANCE SPECIALIST | 2105284206 | KEVIN.SEHY@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | VALVE/FLANGE | [6 empty] | UNKNOWN | UNKNOWN |  | UNDER GROUND |  | 15 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | 2" FLANGED VALVE | [8 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | 2' BLOW DOWN VALVE BLEW OFF FLANGE DUE TO CONNECTION FAILURE. FLANGE WAS THREADED AND PLUGGED. LINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040037 | 2004-04-23 | ORIGINAL | 31651 |  | OSPREY PETROLEUM CO INC | 15995 N BARKERS LANDING #350 | HOUSTON | HARRIS | TX | 77079 | 2000 | 2003-12-16 | 2003 | CORPUS CHRISTI | NUECES | TX |  |  |  | N27 39.483 | W97 13.977 | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | OTHER | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 | 30 | 708287 | 2003-12-16 | 520 | 700 | NO | NO | NO | NO | NO | NO | SHARON H. KOUDELKA | 2815823120 | SKOUDELKA@OSPREYPETROLEUM.COM | TRANSMISSION | OTHER | WELD | OTHER | ALUMINUM | NO | NO | NO | PIPELINE |  | 1964 | 5.55 | 0.22 | 6061 - T6 ALUM. |  | SEAMLESS | 6" 600 SERIES WKM GATE VALVE | ALCOA ALUMINUM |  | UNDER WATER |  | 26 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [7 empty] | NO | YES | 5 | 6 | 2003 | NATURAL GAS |  |  | 700 | [12 empty] | FAILURE WAS IN A 40 YEAR OLD WELD. UNKNOWN CAUSE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040038 | 2004-04-29 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 EAST GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 2300 | 2004-03-29 | 2004 | PETAL | FORREST | MS | 39465 | MP 4.84, STN 255+44 |  | N 31.33933 | W 89.26292 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90319 | 56277.2088 | 124789.7437 | 319 | 164.5368 | 90000 | 124625.2069 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 717399 | 2004-03-29 | 350 | 400 | NO | NO | NO | NO | YES | NO | MIKE L JARRETT, AREA BUSINESS LEADER | 6019680322 | MICHAEL.JARRETT@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1944 | 8 | 0.19 |  | 24000 |  |  |  |  | UNDER GROUND |  | 50 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1944 | NO | [57 empty] | PIPELINE SEGMENT REPLACED AND BACK IN SERVICE. CAUSE OF LEAK STILL UNDER INVESTIGATION. 10-18-04 LOCALIZED CORROSION PIT, LOCATED 5 FEET INSIDE THE EDGE OF CASING. PIPELINE REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040040 | 2004-05-06 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 900 | 2004-04-09 | 2004 | JOHNSTON | POLK | IA | 50131 | MP 29.98 |  | 41.6996 | -93.7324 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79479 | 47486.2315 | 49231.0669 | 70000 | 36105.2632 | 9479 | 13125.8037 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 718704 | 2004-04-09 | 350 | 500 | YES | NO | NO | NO | NO | NO | JOHN A GORMLEY. SR, PIPELINE SAFETY SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 16 | 0.31 | API 5L | 35000 | ERW |  | US STEEL |  | UNDER WATER |  | 10 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | IMPROPER CATHODIC PROTECTION |  | YES | 1980 | NO | [57 empty] | A SMALL PINHOLE LEAK WAS DISCOVERED IN THE DES MOINES A BRANCH LINE (IAB65001) WHERE IT CROSSED BEAVER CREEK IN THE CAMP DODGE, IA PROPERTY. THE LEAK WAS ABOUT 3 FEET FROM THE EAS BANK UNDER 10 INCHES OF WATER. A COFFER DAM HAD TO BE BUILT TO REPAIR THE LEAK. THE ENTIRE CREEK WAS RETURNED TO ITS NATURAL STATE AFTER THE REPAIR.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040041 | 2004-05-04 | SUPPLEMENTAL FINAL | 13580 |  | NORTH CAROLINA NATURAL GAS CORP | 5625 DILLARD DRIVE | CARY | WAKE | NC | 27511 | 851 | 2004-03-30 | 2004 | AHOSKIE | HARTFORD | NC | 27901 | MP 0.73 | 38+53 | 36.28838N | 77.02484W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305000 | 188348.7639 | 370990.3934 | 59096 | 30481.0947 | 245904 | 340509.2987 | 0 | 0 | NO | NO | NO | YES | 50 | PRECAUTIONARY | 2 | 54 | 717443 | 2004-03-30 | 728 | 1000 | NO | YES | NO | NO | NO | NO | THEODORE R HODGES, MANAGER ENGINEERING SERVICES | 9192356004 | THEODORE.HODGES@PIEDMONTNG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2002 | 12 | 0.25 | API 5LX-52 | 52000 | ELECTRIC RESISTANCE WELD | N/A | AMERICAN STEEL PIPE | 2002 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GOVERNMENT | ROAD WORK |  | NO |  |  |  |  | YES |  | YES | [38 empty] | A CONTRACTOR, EMPLOYED BY THE NORTH CAROLINA DEPARTMENT OF TRANSPORTATION, WAS DRIVING PILINGS NEXT TO A BRIDGE CROSSING AHOSKIE CREEK AS PART OF BRIDGE MAINTENANCE PROJECT. THE 12-INCH TRANSMISSION PIPELINE, WHICH HAD BEEN INSTALLED IN 2002 WITH A HORIZONTAL DIRECTIONAL DRILL, WAS AT A DEPTH OF APPROXIMATELY 23 FEET WHEN IT WAS STRUCK BY ONE OF THE PILINGS. THE NORTH CAROLINA ONE CALL CENTER HAD NOT BEEN NOTIFIED PRIOR TO THE WORK AND THEREFORE THE PIPELINE HAD NOT BEEN LOCATED. A PERMANENT PIPELINE MARKER WAS INSTALLED ON ONE SIDE OF THE CREEK CROSSING NEXT TO THE PAVEMENT.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040042 | 2004-05-12 09:43 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | ONE WILLIAMS CENTER, MAIL DROP WRC3-9 | TULSA | TULSA | OK | 74101 | 1300 | 2004-04-14 | 2004 | N/A | N/A | [6 empty] | OFFSHORE |  | GALVESTON | 394 | TX | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187973 | 116706.8132 | 247280.258 | 14973 | 7722.9158 | 173000 | 239557.3422 | 0 | 0 | NO | NO | NO | NO | 0 |  | 144 |  | 719139 | 2004-04-14 | 1075 | 1440 | NO | YES | NO | NO | NO | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 |  | API-5LX | [5 empty] | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1990 | NO | [57 empty] | THE LEAK WAS AT THE 9:00 O¿ CLOCK POSITION AND IT HAS BEEN DETERMINED LEAK WAS WAS CAUSED BY INTERNAL CORROSION. A HIGH PRESSURE CLAMP WAS INSTALLED, LINE WAS THEN RECOATED AND PUT IT BACK IN SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040043 | 2004-05-12 10:15 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | ONE WILLIAMS CENTER, MAIL DROP WRC3-9 | TULSA | TULSA | OK | 74101 | 530 | 2004-04-14 | 2004 | [8 empty] | OFFSHORE |  | BRAZOS | 538 |  | YES | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81600 | 50852.873 | 112993.5209 | 0 | 0 | 81600 | 112993.5209 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 718869 | 2004-04-14 | 1100 | 1440 | NO | YES | NO | NO | NO | YES | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING |  |  |  |  | NO | NO | NO | OTHER | JUNCTION PLATFORM | [9 empty] | OTHER | JUNCTION PLATFORM |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | UNINTENDED ESD OF PLATFORM | [10 empty] | SEE ABOVE
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040044 | 2004-05-12 10:34 | SUPPLEMENTAL FINAL | 30826 |  | WILLIAMS FIELD SERVICES | ONE WILLIAMS CENTER, MAIL DROP WRC3-9 | TULSA | TULSA | OK | 74101 | 1800 | 2004-04-13 | 2004 | [8 empty] | OFFSHORE |  | SHIP SHOAL | 332 |  | YES | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 62319.6973 | 138472.4521 | 0 | 0 | 100000 | 138472.4521 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 719367 | 2004-04-15 | 1089 | 1440 | NO | YES | NO | NO | NO | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING |  |  |  |  | NO | NO | NO |  |  |  | 24 | 0.63 | API-5LX | 60 | DSAW |  |  |  | UNDER WATER |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | NO | [40 empty] | A BRUCE FFTS MK4 ANCHOR WAS USED AS A PIGGYBACK ANCHOR FOR INSTALLATION OF THE GULFTERRA 30-INCH OIL PIPELINE. THE ANCHOR WAS INSTALLED BY ALLSEA "M/V SOLITAIRE". WFS DID NOT RECEIVE PRIOR NOTIFICATIONS OF THE PLANNED ANCHOR ARRANGEMENTS. THE "M/V SOLITAIRE" ATTEMPTED TO RETRIEVE THE ANCHOR ON OR ABOUT APRIL 10, 2004 RESISTANCE WAS OBSERVED. AN ROV INSPECTION CONFIRMED THAT THE ANCHOR WAS ATTACHED TO THE 24-INCH PIPELINE, WFS WAS NOTIFIED OF THE EVENT ON APRIL 13, 2004. INSPECTIONS HAVE BEEN MADE AN NOTIFICATIONS OF THE INSPECTIONS HAVE BEEN SENT TO THE OPS, SOUTHWEST REGION AND TO THE MMS. THE REPAIR IS ONGOING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040045 | 2004-05-20 15:21 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 915 | 2004-05-04 | 2004 | SUMMERSVILLE | GREEN | KY |  | MLV 95-5 +4.96 |  | 37.3409009 | -85.49328597 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | SMALL CRACK IN BODY OF PIPE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95200 | 57137.451 | 66655.6459 | 75000 | 38684.2105 | 20200 | 27971.4353 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 720681 | 2004-05-04 | 745 | 750 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 30 | 0.31 | API | 52000 | DSAW |  | REPUBLIC STEEL | 1956 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | SMALL CRACK | [10 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 4 | 1 | 1969 | WATER |  | 8 | 1018 | [12 empty] | DISCOVERED SMALL LEAK ON PIPELINE, AFTER ANOMALY DIG FOLLOW-UP. DAMAGED AREA WAS FOUND TO BE DUE TO IMPINGEMENT FROM ROCK BED. PIPELINE WAS REPAIRED WITH A PERMANENT WELD SLEEVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040046 | 2004-06-01 11:18 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1615 | 2004-05-16 | 2004 |  |  | LA |  | SV 523M-601 + 0.00 |  |  |  | OFFSHORE |  | SHIP SHOAL | 144 |  | YES | NO | INTERSTATE | OTHER | LEAK DUE TO DAMAGED PIPE IN A SUB-SEA ASSEMBLY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205000 | 127025.0793 | 262145.1507 | 25000 | 12894.7368 | 180000 | 249250.4138 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 721956 | 2004-05-16 | 1200 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1985 | 6.63 | 0.31 | API | 42000 |  |  | USS | 1985 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A SHRIMPER'S NET OR AN ANCHOR APPARENTLY SNAGGED A SUB-SEA ASSEMBLY, UNDER THE VALVE GUARD AT SIDE VALVE 523M-601, IN SHIP SHOAL BLOCK 144, OFFSHORE GULF OF MEXICO, DAMAGING A SECTION OF 6 IN. PIPE AND CAUSING A LEAK. THE LEAK WAS REPAIRED ON 5/18/04 BY CLOSING A 12 IN. SUB-SEA BALL VALVE AND REMOVING THE DAMAGED PIPING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040048 | 2004-05-27 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1600 | 2004-05-19 | 2004 | LIND | ADAMS | WA |  | 78.6 | E S 4150+08 | TWN 16-N | RANGE 34-E | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56642 | 34520.8566 | 55283.3988 | 26642 | 13741.6632 | 30000 | 41541.7356 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 722441 | 2004-05-20 | 640 | 811 | NO | YES | NO | NO | NO | NO | LARRY D OLSEN, SR COMPLIANCE SPECIALIST | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | OTHER | SLEEVE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.25 | 100 | 1300 | GIRTH WELD ON SLEEVE | N/A | KAISER | 1956 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | REPAIR SLEEVE |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 6 | 10 | 1956 | WATER |  | 8 | 1062 | [12 empty] | PIN HOLE LEAK IN WELDED SLEEVE GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040049 | 2004-06-04 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1040 | 2004-05-07 | 2004 | LITTLE FALLS | PASSAIC | NJ | 07424 | 1828.270 |  | 40.86700 | -74.21088 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84100 | 52320.3082 | 113761.6336 | 3100 | 1598.9474 | 81000 | 112162.6862 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 | 0 | 720998 | 2004-05-07 | 615 | 638 | NO | NO | NO | NO | YES | NO | JAMES MATHIS, ENGINEER II | 7132153792 | JAMES.G.MATHIS@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 36 | 0.5 | API 5LX | 52000 | DSAW | N/A | BETHLEHEM STEEL CORPORATION | 1959 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | DENT | [11 empty] | CONSTRUCTION DEFECT | PROCEDURE NOT FOLLOWED | NO | YES |  |  | 1959 | WATER |  | 8 | 1099 | [12 empty] | OPERATIONS REPORTED A SUSPECTED LEAK ON THE CALDWELL LOOP "B" UPSTREAM OF 88 RIDGE RD., LITTLE FALLS, NJ. THE LINE WAS ISOLATED AND DRAWN DOWN TO 18.5 PSI (2:14 PM EASTERN STANDARD ON 05/07/04) WILLIAMS PERSONNEL STARTED DIGGING THE LINE ON THE 05/07/04. PIPE WAS FOUND SETTLING ON COBBLE ROCK. THE COATING WAS DAMAGED AND THE PIPE WAS LEAKING GAS. LOCATION OF THE LEAK OCCURRED AT THE 6:00 O'CLOCK POSITION ON THE PIPE. THE LEAK WAS CUT OUT ON 05/09/04 AND REPLACED WITH NEW PIPE. LINE WAS PUT BACK INTO SERVICE AT 12:32 A.M. ON 05/11/04.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040050 | 2004-06-09 10:39 | SUPPLEMENTAL FINAL | 1007 |  | K N INTERSTATE GAS TRANSMISSION CO | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228 | 1500 | 2004-05-28 | 2004 | OBERLIN | DECATUR | KS | 67749 |  | 18554+98 | 39.8580598 | -100.6903715 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52000 | 31091.7021 | 32903.598 | 45000 | 23210.5263 | 5500 | 7615.9849 | 1500 | 2077.0868 | NO | NO | NO | NO | 0 |  | 12 |  | 723361 | 2004-05-28 | 940 | 956 | YES | NO | NO | NO | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 22 | 0.28 |  | 52000 | FLASH WELD |  | AO SMITH | 1954 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | LF ERW |  | MATERIAL DEFECT |  | NO | YES | 10 | 18 | 1996 | WATER |  | 8 | 1275
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040051 | 2004-06-10 17:32 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1015 | 2004-05-10 | 2004 | RUSTON | LINCOLN | LA | 71270 | FM-17 | 50+70 | 32.5307 | 92.61041 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8360 | 5165.2323 | 10246.8264 | 1530 | 789.1579 | 6830 | 9457.6685 | 0 | 0 | NO | NO | NO | YES | 12 | PRECAUTIONARY | 1 |  | 721245 | 2004-05-10 | 225 | 300 | NO | NO | NO | YES | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 6 | 0.28 | API5L | 24000 | DSAW | NA | UNKNOWN |  | UNDER GROUND |  | 24 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | RAILROAD |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE EMERGENCY RESPONDER PERSONNEL EVACUATED 12 PERSONS FROM THEIR HOMES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040052 | 2004-06-04 | ORIGINAL FINAL | 1552 |  | BLUE DOLPHIN PIPELINE COMPANY | 801 TRAVIS, SUITE 2100 | HOUSTON | HARRIS | TX | 77002 | 1440 | 2004-05-24 | 2004 | [6 empty] | 28 54' 12"N | 94 46' 01" W | OFFSHORE |  | GALVESTON | 287 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 722855 | 2004-05-24 | 390 | 600 | NO | YES | NO | NO | NO | NO | LARRY J TURPIN | 7132277660 | LTURPIN@BLUE-DOLPHIN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS | N/A |  |  | UNDER GROUND |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | CO2 AND WATER | YES | 1965 | NO | [57 empty] | PINHOLE GAS LEAK CAUSED BY APPARENT LOCALIZED INTERNAL CORROSION. LEAK WAS REPAIRED BY INSTALLATION OF 1440 PSIG WP BOLTED PIPELINE CLAMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040053 | 2004-06-22 15:49 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 230 | 2004-05-29 | 2004 | ALBANY | DOUGHERTY | GA |  | 0.632 |  | 31.4979 | -84.09584 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176401 | 106106.4969 | 130457.1535 | 130976 | 67556.0421 | 45425 | 62901.1114 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 723388 | 2004-05-29 | 1063 | 1090 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 6.63 | 0.19 | API | 35000 | ERW |  | REPUBLIC | 1960 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | LOCALIZED PITTING |  | STRESS CORROSION CRACKING |  | YES | 1960 | NO | [57 empty] | A RUPTURE OCCURRED AT APPROXIMATELY 2:30 A.M. ON MAY 29, 2004, ON THE EAST DOUGHERTY LINE (LINE 26), ABOUT ONE MILE SOUTH OF THE ALBANY COMPRESSOR STATION. THE CAUSE OF THE RUPTURE WAS DETERMINED TO BE HIGH PH, STRESS CORROSION CRACKING(SCC).
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040054 | 2004-06-10 | SUPPLEMENTAL FINAL | 1472 |  | BLACK MARLIN PIPELINE CO | ONE WILLIAMS CENTER - WRC3-9 | TULSA | TULSA | OK | 74101 | 750 | 2004-05-12 | 2004 | [6 empty] | X=3578667.00 | Y=510685.00 | OFFSHORE |  | HI | A6 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 49709.6978 | 106433.2865 | 5000 | 2578.9474 | 75000 | 103854.3391 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 721506 | 2004-05-12 | 800 | 1367 | YES | NO | NO | NO | NO | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | [8 empty] | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | MATERIAL DEFECT |  | NO | YES | 8 | 26 | 1966 | WATER |  | 24 | 1920 | [12 empty] | LEAK WAS CAUSED BY DAMAGED 12-INCH GASKET IN FLANGE PAIR, FLANGE GASKET REPLACED.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040055 | 2004-07-07 16:04 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1800 | 2004-06-11 | 2004 | HOUMA | TERREBONNE | LA |  | 127.44 | 6728+89 | 29 18. 573 N | 91 09 .072 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 370996.9829 | 743941.208 | 100000 | 51578.9474 | 490000 | 678515.0154 | 10000 | 13847.2452 | NO | NO | NO | NO | 0 |  |  |  | 724726 | 2004-06-11 | 640 | 1169 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 30 | 0.41 | API 5LX | 60000 | DSAW | N/A | US STEEL | 1965 | UNDER WATER |  | 192 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1965 | NO | [57 empty] | A POSSIBLE LEAK WAS REPORTED TO WGP GAS CONTROL AT APPROXIMATELY 1800 HOURS ON 6/11/04. THE NRC WAS CALLED AN HOUR LATER. THE O'BRIAN GROUP WAS DISPATCHED TO CONTAIN AND REMEDIATE A LIGHT CONDENSATE SHEEN ON THE WATER AND TO COORDINATE AGENCY REPORTING. THE LEAK WAS DISCOVERED AT FOUR LEAGUE BAY ON SELA 30" LINE B. THE LINE WAS BLOWN DOWN. UT READINGS REVEALED AN ISOLATED 1/4" PINHOLE AT 6:30 POSITION CAUSED BY INTERNAL CORROSION. DIVERS INSTALLED A HYDROTECH CLAMP. THE CLAMP WAS PRESSURE TESTED AND THE LINE RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040056 | 2004-07-08 14:36 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1330 | 2004-06-19 | 2004 | [6 empty] | 28*28.46 | 95*45.24 | OFFSHORE |  | BRAZOS | 450 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 55795.6075 | 115935.8564 | 10000 | 5157.8947 | 80000 | 110777.9617 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 725558 | 2004-06-19 | 957 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12 | 0.31 | API 5LX | 60000 | ERW | ANSI 600 | STUPP CORPORATION | 1990 | UNDER WATER |  | 12 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1990 | NO | [57 empty] | LEAK WAS DISCOVERED OFFSHORE AT BA 450 AND REPORTED TO WGP GAS CONTROL. DIVERS DISCOVERED THE LEAK COMING FROM THE WELD THAT CONNECTED THE CATHODIC PROTECTION ANODE TO THE PIPE. THE LEAK WAS CLAMPED AND THE PIPELINE RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040057 | 2004-07-08 16:21 | ORIGINAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 1500 | 2004-06-08 | 2004 | OLYPHANT | INDEPENDENCE | AR | 72139 | 204 | 1418+67 | 3532136 | 0912253 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57471 | 35031.9074 | 56265.3688 | 26833 | 13840.1789 | 30638 | 42425.1899 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 724673 | 2004-06-11 | 174 | 450 | NO | NO | YES | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 22 | 0.31 |  | 30000 |  |  |  |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1978 | NO | [57 empty] | LEAK WAS FOUND DURING NORMAL OPERATIONS WHILE CHECKING RECTIFIER IN THE SAME GENERAL AREA ON 6/8/04. LEAK WAS NOT DETERMINED TO BE REPORTABLE AT FIRST, HOWEVER ONCE LEAK WAS EXPOSED IT WAS DETERMINED THAT A 40 FOOT SECTION OF PIPE NEEDED TO BE REPLACE. BECAUSE OF THE TIME AND LABOR INVOLVED ON THE REPAIR, THE COST EDGED ABOVE THE $50,000 REPORTING LIMIT AND WAS REPORTED ON 6/11/04.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040058 | 2003-05-28 | SUPPLEMENTAL FINAL | 31304 |  | DEVON GAS SERVICES LP | 415 PR 3502 | BRIDGEPORT | WISE | TX | 76426 | 1855 | 2003-05-28 | 2003 | NEW FAIRFAX (DECATUR) | WISE | TX | 76234 | STATION B-117 COMPRESSOR | NO. N/A | N 33 08.986 | W 97 29.667 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | 1/2" NIPPLE BROKE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1378460 | 879648.0976 | 1954459.6397 | 100 | 58.6325 | 0 | 0 | 1378360 | 1954401.0073 | NO | YES | NO | NO | 0 |  |  | 30 | 646291 | 2003-05-28 | 120 |  | NO | NO | NO | NO | NO | NO | MARK GRINNELL - SUPERINTENDENT OF PIPELINE OPERATIONS | 9406836055 | MARK.GRINNELL@DVN.COM | GATHERING | OTHER | 1/2" NIPPLE ON A COMPRESSOR STARTING SYSTEM | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2002 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | THE INCIDENT WAS REPORTED INITIALLY BY TELEPHONE AT THAT TIME THE EXTENT OF DAMAGE WAS UNKNOWN. DEVON DETERMINED ITS LOSS TO BE $100.00 IT WAS DETERMINED THAT THIS DOLLAR VALUE DID NOT TRIGGER THE LEVEL DICTATING A REPORT BE FILED FOR THE INCIDENT. AFTER IDENTIFYING THE DAMAGE THAT OCCURRED TO THE COMPRESSION RENTAL COMPANY, (HANOVER COMPANY) WE REEVALUATED AND ARE NOW SUBMITTING A REPORT. HANOVER PROVIDED THE ATTACHED REPORT MARKED ATTACHMENT 1 CONCERNING THEIR FIRE AT OUR B-117 STATION. ATTACHMENT 1 1. It id believed that at some point between 10:45 and 18:55, a ?" nipple supplying the pre/post lube system fractured. This nipple is located on the starting system supply manifold with 120 lb pressure of continuous natural gas flow (it is normal for start systems to have no safety shut-off protection).The nipple was downstream of a 1 1/2" tee bushed down to a 1 1/2" and connected to the pre/post lube regular. 2. There is no evidence of gas accumulation and any explosion. It is believed that the leaking gas ignited immediately with the failure of the ?" nipple. 3. We believed this leaking nipple and ensuing fire created a torching effect to the area above this 1 1/2" nipple thus potentially torching the ignition system and /or any surrounding wiring and probably causing unit shutdown. (Note - Fire severely destroyed the unit's safety panel, so exact determination of what actually caused unit to shut down is unknown.) 4. We also believe the 1/2" nipple completely separated at rapid rate. With full separation there was a stream of 1/2" 120 psi gas supplying the fire. 5. There are signs of natural gas "blowing against the coupling guard. (Unlit gas left the separated nipple at 120 psi and ignited after striking the coupling guard 18" away. The fact that the coupling guard was not distorted and molten aluminum was everywhere but in that area leads us to this conclusion.) 6. This ricocheting flame created heat stress on two cast aluminum starter relay valves (SRV's) and other parts of the unit in the surrounding area. 7. Heat continued and the SRV's failed due to heat distortion thus allowing both 1 1/2" starter supplies (120 psi) to fuel the fire. 8. At some point in this process, heat distorted the GSOV thus releasing another 1 1/2" line at 45 psi to fuel the fire. (Note: This was the auto shut-off valve for fuel gas supply to the engine.) 9. Other gas leaks from process cylinder valve cap o-rings and packing probably occurred as the fire continued. 10. The fire continued to burn until discovered and was shut off with the inlet valve to the station by Jeff Murphy (Devon employee).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040059 | 2004-07-06 | SUPPLEMENTAL FINAL | 30750 |  | MIDAMERICAN ENERGY COMPANY | 401 DOUGLAS ST | SIOUX CITY | WOODBURY | IA | 51102 | 100 | 2004-05-31 | 2004 | CEDAR RAPIDS | LINN | IA | 52404-7457 |  | APPRX 112+62 | 41.952108 N | 91.685286 W | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381940 | 235630.2198 | 457681.1458 | 81940 | 42263.7895 | 300000 | 415417.3563 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 723505 | 2004-05-31 | 475 | 600 | NO | YES | NO | NO | NO | NO | ROGER N LORENZEN, GAS STANDARDS SUPERVISOR | 7122777678 | MLORENZEN@MIDAMERICAN.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 10 | 0.25 | API 5L GR B | 35000 | UNKNOWN |  | UNKNOWN | 1950 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | WASHOUT | [52 empty] | A METALLURGICAL ANALYSIS WAS CONDUCTED ON THE CAUSE OF THE PIPELINE FAILURE. THAT ANALYSIS CONCLUDED THAT OVERLOADING OF THE PIPELINE OCCURRED AS A RESULT OF THE RIVER FLOODING, LOSS OF COVER AND THE FLOATING LINE BEING PUSHED BY THE CURRENT WHILE THE PIPE AND GIRTH WELD WERE PINNED AT THE EDGE OF THE EAST BANK OF THE RIVER. THESE CONDITIONS RESULTED IN ABNORMAL AXIAL TENSILE LOADING AND BENDING OF THE PIPELINE AT THE GIRTH WELD.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040060 | 2004-07-16 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 3800 FREDERICA STREET; BOX 20010 | OWENSBORO | DAVIESS | KY | 42304 | 200 | 2004-07-04 | 2004 | HESSTON | HARVEY | KS | 67062 | HESSTON STATION | LINE W 240/291495 | 3814716 N | 97.45448 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | STATION ESD, STATION INLET VALVE DID NOT CLOSE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80552 | 47846.6767 | 41547.8737 | 80552 | 41547.8737 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 727150 | 2004-07-04 | 611 | 960 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR, SR. PIPELINE SAFETY SPECIALIST | 2708524424 | DAVID.SINCLAIR@SSCGP.COM | TRANSMISSION | OTHER | VALVE OPERATOR | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1978 | [8 empty] | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | FROM THE STATION EVENT LOG, IT APPEARS THAT DUE TO A LIGHTNING STRIKE NEAR THE CONTROL BUILDING, THE ESD SOLENOID TRIPPED OUT INITIATING ESD. NORMALLY THE ESD SOLENOID IS HELD ENERGIZED BY BOTH THE FIRE AND GAS DETECTION SYSTEMS AS WELL AS SOME MANUAL PUSH BUTTONS. ALL OF THESE THINGS HAVE INDIVIDUAL ANNUNCIATION ATTACHED TO THEM AND NOTHING WAS ANNUCIATED BY SCADA. IT WOULD APPEAR THAT THE LIGHTNING GENERATED A CHANGE IN VOLTAGE ON THE ESD DC VOLTAGE SYSTEM CAUSING THE ESD TO TRIP. AT 2:00 AM, GAS CONTROL NOTIFIED ANDREW BUCHANON THAT THE STATION HAD ESDED. WHEN THE OPERATORS ARRIVED AT THE STATION, THE BLOWOFFS WERE STILL BLOWING. THE BLOWOFFS WERE CLOSED WHEN THE OPERATORS DETERMINED IT WAS SAFE TO CLOSE THEM. THE REASON THE ESD BLOWOFFS WERE STILL BLOWING WAS BECAUSE GATE NUMBER 55 HAD FAILED TO CLOSE AS IT SHOULD HAVE DURING A NORMAL ESD. IT WAS DETERMINED THE REASON VALVE 55 DID NOT CLOSE WAS A RUSTED ACTUATOR PISTON ON THE OPERATOR. THE ACUTATOR WAS REPAIRED AND THE GATE RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040061 | 2004-07-01 | ORIGINAL FINAL | 22175 |  | DYNEGY MIDSTREAM SERVICES, L.P. | 1000 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1715 | 2004-06-01 | 2004 | [6 empty] | 29.10.54 | 93.18.51 | OFFSHORE |  | WEST CAMERON | 225 |  | YES | NO | INTRASTATE |  |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156200 | 96563.4065 | 193093.4044 | 26700 | 13771.5789 | 129500 | 179321.8255 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 723657 | 2004-06-01 | 950 | 1300 | NO | YES | NO | NO | NO | NO | TIM HUFFER, ES & H ADVISOR | 3375834642 | TIM.HUFFER@DYNEGY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 12 | 0.31 | API 5LX | 52000 | SMLS |  | UNKNOWN |  | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1969 | NO | [57 empty] | THE TIME REPORTED FOR THE ELASPED TIME UNTIL AREA WAS MADE SAFE REFLECTS THE TIME REQUIRED TO DEPRESSURE PIPELINE IN ORDER TO SAFELY AFFECT REPAIR AND COMPLETE REPAIR. THE DOLLAR VALUE FOR GAS LOSS INCLUDES $2,000 FOR GAS THAT LEAKED AND $24,700 FOR GAS THAT WAS DUE TO DEPRESSURING THE PIPELINE FOR REPAIR.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040062 | 2004-07-30 16:43 | SUPPLEMENTAL FINAL | 26330 |  | ENOGEX INC (EX. MUSTANG FUEL CORP) | 515 CENTRAL PARK DRIVE, SUITE 600, PO BOX 24300 | OKLAHOMA CITY | OKLAHOMA | OK | 73124 | 1730 | 2004-07-02 | 2004 | OOLAGAH | ROGERS | OK | 74053 | NORTHEAST POWER STATION |  | N36.25.77 | W95.42.06 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35100 | 21871.2926 | 48516.9372 | 100 | 51.5789 | 35000 | 48465.3582 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 727085 | 2004-07-03 | 650 | 780 | YES | NO | NO | NO | NO | NO | ARTHUR L. NEWTON | 4055584676 | NEWTONAL@OGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2000 | 12 | 0.31 | API 5L | 42000 | HF-ERW |  | UNKNOWN |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | IMPROPER CATHODIC PROTECTION |  | YES | 2000 | NO | [57 empty] | THE CAUSE(S) ARE STILL UNDER INVESTIGATION AND WILL BE FILED IN A SUPPLEMENTAL REPORT AT A LATER DATE. 08/12/08 UPDATE: IN 2003 A 12 INCH FBE COATED PIPELINE WAS INSTALLED BEWTWEEN THE LP GAS YARD AND THE HP GAS YARD TO SUPPLEMENT THE FUEL GAS SUPPLY TO THE POWER STATION'S TURBINE GENERATORS. DURING THE INVESTIGATION IT WAS DETERMINED THAT THE NEW LINE HAD BEEN ISOLATED FROM ALL EXISTING CATHODIC PROTECTION SYSTEMS AS INSULATING KITS WERE INSTALLED AT EACH END OF THE LINE SEGMENT DURING CONSTRUCTION. AS A REULT, THE NEW LINE IN EFFECT BECAME A MORE EFFICIENT ANODE THAN THE DEEP WELL ANODE BED LOCATED NEARBY. LOCALIZED CORROSION PITTING WAS FOUND IN A SMALL AREA ON AN UNDERGROUND 12 INCH PIPING HEADER INSTALLED IN 2000. BECAUSE OF THE INSULATING FLANGES, THIS HEADER WAS NO LONGER ADEQUATELY PROTECTED. THE AFFECTED HEADER PIPING WAS REPLACED AND THE UPSTREAM INSULATING FLANGE KIT WAS SHORTED, THUS PROVIDING ADEQUATE CATHODIC PROTECTION THROUGHOUT THE PIPE SEGMENT.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040063 | 2004-07-30 17:02 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1035 | 2004-07-06 | 2004 |  | OCS |  |  |  |  | 302986.66 | 3210936.93 | OFFSHORE |  | GALVESTON | 394 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 49563.6378 | 102088.6112 | 10000 | 5157.8947 | 70000 | 96930.7165 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 727360 | 2004-07-06 | 1089 | 1250 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12 | 0.31 | API 5LX | 52000 | SEAMLESS | ANSI 600 |  | 1990 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1990 | NO | [57 empty] | LEAK WAS DISCOVERED OFFSHORE AT GA 394 AND REPORTED TO WGP GAS CONTROL. DIVERS DISCOVERED THE LEAK COMING FROM A PINHOLE IN THE PIPE. THE LEAK WAS CLAMPED AND THE PIPELINE RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040064 | 2004-07-26 | ORIGINAL FINAL | 22175 |  | DYNEGY MIDSTREAM SERVICES, L.P. | 1000 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1800 | 2004-07-11 | 2004 | [6 empty] | 29,10,54 N | 93,18,51 W | OFFSHORE |  | WEST CAMERON | 225 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59000 | 36505.7133 | 73878.3313 | 9000 | 4642.1053 | 50000 | 69236.2261 | 0 | 0 | NO | NO | NO | NO | 0 |  | 46 | 40 | 727952 | 2004-07-11 | 976 | 1300 | NO | YES | NO | NO | NO | NO | TIM HUFFER ES&H ADVISOR | 3375834642 | TIM.HUFFER@DYNEGY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 12 | 0.31 | API 5LX | 52000 | SMLS |  | UNKNOWN |  | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1969 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040065 | 2004-08-03 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1430 | 2004-07-06 | 2004 |  |  | TX |  | 1.5 MILES DOWNSTREAM OF M | N/A | N 27.5643 | W 96.6985 | OFFSHORE |  |  | 805 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 402156.8315 | 813177.434 | 100000 | 51578.9474 | 550000 | 761598.4866 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 727389 | 2004-07-06 | 950 | 1250 | YES | NO | NO | NO | NO | NO | JACK GUINN, SR PIPELINE SAFETY ENGINEER | 4023987396 | JACK.GUINN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.38 | API 5L | 60000 | DOUBLE SUBMERGED ARC WELD |  | STELCO | 1985 | UNDER WATER |  | 72 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1986 | NO | [57 empty] | ON JULY 6, 2004 AT APPROXIMATELY 2:30 PM A LEAK WAS DETECTED ON THE NORTHERN NATURAL GAS COMPANY (NNG). MUSTANG ISLAND 20" LINE SEGMENT TOS 84061 (MMS-#7292). NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AND MMS ON THAT DAY. A HYDROTECH CLAMP WAS UTILIZED TO REPAIR THE LEAK. THE CLAMP IS RATED AT 2220 PSI (WORKING PRESSURE). ONCE THE CLAMP WAS IN PLACE, THE LINE WAS LEAK TESTED. THE LINE WAS THEN BACK FILLED TO THE ORIGINAL SIX FOOT DEPTH OF COVER UTILIZING SAND BAGS. REPAIR WAS COMPLETED ON JULY 14, 2004.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040066 | 2004-08-03 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1515 | 2004-07-16 | 2004 | NORTHFIELD | DAKOTA | MN | 55057 | MP 93.011 |  | 44.47 N | 93.23 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | PIPE NIPPLE CRACKED AT THREADED CONNECTION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23720 | 14118.5353 | 13103.4614 | 22720 | 11718.7368 | 1000 | 1384.7245 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 728525 | 2004-07-16 | 630 | 800 | NO | NO | NO | NO | YES | NO | PAT VAUGHAN, SR PIPELINE SAFETY ENGINEER | 4023987185 | PAT.VAUGHAN@NNGCO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 1 | [7 empty] | OPEN DITCH |  |  | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | AT APPROXIMATELY 3:15 PM ON JULY 16, 2004, A NORTHERN NATURAL GAS (NORTHERN) CONTRACTOR WAS EXCAVATING THE 16-INCH TIE-OVER LINE BETWEEN THE 26-INCH MNM80102 - B LINE AND THE 30-INCH MNM80103-C LINE IN PREPARATION FOR A STOPPLE INSTALLATION. DUE TO THE HEAVY RAINS AND GROUND MOISTURE, MATTING WAS REQUIRED TO SUPPORT THE EXCAVATION EQUIPMENT. THE EQUIPMENT OPERATOR HAD PLACED HIS BUCKET ON A MAT TO REPOSITION THE EQUIPMENT WHEN THE MAT SLID AND STRUCK AN ABANDONED FARM TAP VALVE CRACKING THE THREADS AT THE TAP VALVE. THE TAP VALVE WAS AT GROUND LEVEL ON THE B LINE BLOWDOWN RISER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040067 | 2004-08-17 09:27 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION CORP (DUKE) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 2230 | 2004-07-19 | 2004 |  | GREENE | PA | 15320 | MP 1156.71 | 61074+50 | 39.9175 | 79.9428 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64700 | 38793.056 | 44146.3735 | 52300 | 26975.7895 | 12400 | 17170.5841 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 45 | 728841 | 2004-07-20 | 721 | 1000 | NO | YES | NO | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1992 | 24 | 312 | API 5L | 65000 | DSAW | N/A | STUPP | 1992 | UNDER GROUND |  | 30 | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | CRACK OCCURRED IN THE PIPELINE NEAR THE CIRCUMFERENTIAL WELD IMMEDIATELY FOLLOWING PLANNED BLASTING ACTIVITIES 6 MILES NORTH OF GREENSBORO,PA. THE BLASTING CONTRACTOR DID NOT FOLLOW THEIR BLASTING PLAN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040068 | 2004-08-16 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1807 | 2004-07-15 | 2004 | PRINCETON | MERCER | NJ | 08540 | 1773+40 |  | 40.33526 | -74.72893 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104778 | 62236.5564 | 54043.3895 | 104778 | 54043.3895 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 728537 | 2004-07-16 | 575 | 800 | NO | NO | NO | NO | YES | YES | COLIN W COCHRAN, ENGINEER | 7132152855 | COLIN.W.COCHRAN@WILLIAMS.COM | TRANSMISSION | OTHER | BLOWDOWN VALVE | STEEL |  | NO | NO | NO | OTHER | YARD PIPING | 2001 | 42 | 0.75 | [6 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | A MALFUNCTION OF THE STATION EMERGENCY BLOW DOWN SYSTEM CAUSED AS A STATION BLOWDOWN VALVE TO OPEN (FAIL SAFE MODE) AND SAFELY VENT GAS THROUGH A MUFFLER TO ATMOSPHERE. STATION ON-CALL PERSONNEL RESPONDED TO THE INCIDENT AND MANUALLY CLOSED THE VALVES INVOLVED. UPON INVESTIGATION, A COMINATION OF CLOGGED ORIFICE AND A MINUTE LEAK ON ONE OF HE STATIONS MANUAL BLOW DOWN HAND VALVES CAUSED THE STATION BLOW DOWN VALVE TO OPEN (FAIL-SAFE).
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040069 | 2004-08-19 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1018 | 2004-07-25 | 2004 | ENGLEWOOD | CLARK | KS | 67840 | 0.42 | 22+05 | 37.0302 | -99.9850 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67620 | 42140.5793 | 93635.0721 | 0 | 0 | 67620 | 93635.0721 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 729499 | 2004-07-25 |  | 500 | YES | NO | NO | NO | NO | NO | JOHN GORMLEY, SR PIPELINE SAFETY SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION |  |  |  |  | NO | NO | NO | REGULATOR/METERING |  | 1986 | [8 empty] | OTHER | TOWN BORDER STATION |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | ON JULY 25, 2004 AT 10:18AM A MR. MIKE DAY WITH KANSAS GAS SERVICES (KGS) CALLED TO REPORT THAT "ONLY 37% GAS IS COMING INTO THE TOWN OF ENGLEWOOD, KS" THROUGH NORTHERNS ENGLEWOODS TBS. THE PRESSURE WAS OK BUT CUSTOMERS ARE REPORTING PILOT LIGHTS GOING OUT AND YELLOW FLAMES ON THEIR STOVES. NNG LOCKED AND TAGGED THE TBS AT 12:10 PM. INITIAL INDICATIONS WERE THAT THE PIPELINE WAS FILLED WITH CONDENSATE. KGS CHROMATOGRAPH REPORTED FROM THEIR SYSTEM. IT IS ESTIMATED THAT 57 METERS WERE IMPACTED WHEN THE TBS WAS SHUT-IN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040070 | 2004-08-25 16:07 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 9 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1300 | 2004-08-05 | 2004 |  |  |  |  | 507K-104 +28.90 |  | N 29 21.040 | W 93 01.255 | OFFSHORE |  | WEST CAMERON | 177 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 76439.0211 | 129643.8128 | 50000 | 25789.4737 | 75000 | 103854.3391 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 730893 | 2004-08-05 | 835 | 1050 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8326764169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 2 | 0.22 | API | 35000 |  |  | UNKNOWN | 1974 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | TO BE EXAMINED AT A LATER DATE | GALVANIC |  | YES | 1974 | NO | [57 empty] | 30 FT. BUBBLE CIRCLE DISCOVERED IN W.C. BLK. 177. NO SHEEN PRESENT. THE LEAK WAS DISCOVERED TO BE NEAR THE TGP 26" LINE NO. 507K-100 AT APPROXIMATE M.P. 507K-104+28.90 ON LINE NO. 507K-1000. LEAK IS APPARENTLY DUE TO INTERNAL CORROSION ON THE 2" BY-PASS AROUND THE 10" VALVE NO. 507K-1001. LEAK WAS REPAIRED BY REMOVING A TEE ASSEMBLY AND INSTALLING A 900# BLIND FLANGE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040071 | 2004-08-23 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1100 | 2004-07-29 | 2004 |  |  | TX |  | 1.75 MILES UPSTREAM OF MU | N/A | N 27.5649 | W 96.6972 | OFFSHORE |  |  | 805 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605800 | 375026.3359 | 764311.4878 | 85800 | 44254.7368 | 520000 | 720056.751 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 729995 | 2004-07-29 | 950 | 1250 | YES | NO | NO | NO | NO | NO | JACK GUINN, SENIOR PIPELINE SAFETY ENGINEER | 4023987396 | JACK.GUINN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.38 | API 5L | 60000 | DOUBLE SUBMERGED ARC WELD |  | STELCO | 1985 | UNDER WATER |  | 72 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1986 | NO | [57 empty] | A LEAK WAS REPORTED TO NORTHERN NATURAL GAS COMPANY (NNG) ON 7/29/2004, BY PERSONNEL AT MUSTANG ISLAND 787. THE INITIAL REPORT INDICATED A SMALL AREA WITH LIGHT SHEEN AND BUBBLES AT APPROXIMATE COORDINATES N27 33.84 W96 41.29. A HELICOPTER WAS DISPATCHED WITH LYNDON LANGE OF CENTERPOINT ENERGY TO INVESTIGATE. THE LEAK WAS DETERMINED TO BE ON THE 20" NNG LINE SEGMENT TOS 84061 (MMS #7292). WHEN UNCOVERED BY DIVERS IT WAS REPORTED TO BE A PIN HOLE LEAK AT THE 6 O'CLOCK POSITION. THE LEAK WAS REPAIRED USING A 20" X 24" 1500 PSI PLIDCO CLAMP. THE REPAIR WAS COMPLETED ON 8/8/2004.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040072 | 2004-08-27 11:37 | SUPPLEMENTAL FINAL | 26330 |  | ENOGEX INC (EX. MUSTANG FUEL CORP) | 515 CENTRAL PARK DRIVE | OKLAHOMA CITY | OKLAHOMA | OK | 73124 | 530 | 2004-07-30 | 2004 | EL RENO | CANADIAN | OK | 73036 | LINE 106 |  | 35.27.53.8 | 97.56.48.4 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 12 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91000 | 54782.9319 | 68660.2183 | 66000 | 34042.1053 | 20000 | 27694.4904 | 5000 | 6923.6226 | NO | NO | NO | NO | 0 |  | 0 | 15 | 730122 | 2004-07-30 | 742 | 960 | NO | NO | YES | NO | NO | NO | ARTHUR L. NEWTON | 4055584676 | NEWTONAL@OGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12 | 0.2 | API 5L | 52000 | HF - ERW |  | STUPP CORPORATION | 1967 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | TEMPORARY ASPHALT PLANT-EXCAVATION INSIDE OF PLANT | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | WESTERN PLAINS CONSTRUCTION COMPANY (WPCC) HAD EXCAVATED OVER ENOGEX'S PIPELINE WITH OUT FILING A ONE CALL LOCATE WITH CALL OKIE AS REQUIRED BY TITLE 63 PART 142 OKLAHOMA UNDERGROUND FACILITIES PREVENTION ACT SECTION 142.6. AT THE TIME OF THE RUPTURE WPCC WAS NOT EXCAVATING OVER THE PIPELINE HOWEVER, ENOGEX'S IVESTIGATION OF THE PIPELINE RUPTURE REVEALED MULTIPLE DENTS AND GOUGES DUE TO THE EXCAVATION ACTIVITY, RESULTING IN THE PIPLINE RUPTURE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040073 | 2002-02-15 | SUPPLEMENTAL | 2436 |  | AQUILA SOUTHWEST (EX. CLAJON GAS CO) | 800 SONTERRA BLVD #400 | SAN ANTONIO | BEXAR | TX | 78258-4141 |  | 2001-11-07 | 2001 | INDEPENDENCE |  | TX | 77833 |  |  | 096 | 30' 16.44 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63342 | 43119.8033 | 55738.0806 | 42870 | 25707.0105 | 20472 | 30031.0701 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  |  | 2002-01-22 | 960 | 1200 | YES | NO | NO | NO | NO | NO | BILL HAYMAN, EH&S COORDINATOR | 9742189452 | BHAYMAN@UTILICORP.COM | GATHERING | OTHER | ENCROACHMENT BY BACKHOE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 24 | 0.34 |  |  | ERW |  |  |  | UNDER GROUND |  | 54 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | YES | [36 empty] | LANDOWNER WAS USING A BACKHOE TO DIG DITCHES AND A HOLE FOR A NEW SEPTIC SYSTEM ON HIS PROPERTY. UPON HITTING AQUILA'S 24" PIPELINE, LANDOWNER MADE A VISUAL INSPECTION, DETERMINED THAT THE PIPE WAS NOT DAMAGED JUST HAD SOME COATING SCRAPED OFF. LANDOWNER DECIDED TO COVER HOLE AND DITCHES BACK UP UNTIL A LATER DATE. AQUILA EMPLOYEE NOTICED DIGGING ON 1-15-02 WHILE MAKING HIS ROUNDS. THIS EMPLOYEE INVESTIGATED THE DIG SITE AND DISCOVERED LANDOWNER MAY HAVE HIT AQUILA'S 24" PIPELINE. WENT BACK 1-21-02 WITH DIGGING EQUIPMENT DISCOVERED 24" PIPELINE HAD BEEN HIT. (LANDOWNER STATED THAT THE PIPE HAD ACTUALLY BEEN HIT ON 11-7-2001). REPAIR BEGAN ON 1-22-02, COMPLETED ON 1-23-02.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040074 | 2004-08-30 | ORIGINAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO (ENRON) | PO BOX 4657 | HOUSTON | HARRIS | TX | 77210-4657 | 1150 | 2004-07-30 | 2004 | MIAMI | DADE | FL | 33184 | 6.00 | 316+80 | N | W | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25383 | 15325.4224 | 20478.2321 | 16883 | 8708.0737 | 8500 | 11770.1584 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 730151 | 2004-07-30 | 552 | 1066 | YES | NO | NO | NO | NO | NO | MERLIN H MOSEMAN, PIPELINE SAFETY ENGINEER | 7133451625 | MERLIN.MOSEMAN@CROSSCOUNTRYENERGY.COM | TRANSMISSION | BODY OF PIPE |  |  |  | NO | NO | NO | PIPELINE |  | 1970 | 8 | 0.22 | API5LX | 42000 | ERW |  | INTERLAKE | 1970 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | SEWER |  | YES | 7 | 16 | 2004 | ONE-CALL SYSTEM | YES | FLAGS |  | ACCURATE | YES
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040075 | 2004-09-01 | ORIGINAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA, | HOUSTON | HARRIS | TX | 77046 | 934 | 2004-08-04 | 2004 | COLUMBIA | MARION | MS | 39429 | MP 37.1 | 94+58 | N31.26668 | W89.85710 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 9 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113511 | 68306.3511 | 84799.1757 | 83300 | 42965.2632 | 30211 | 41833.9125 | 0 | 0 | NO | NO | NO | YES | 100 | PRECAUTIONARY | 1 | 30 | 730736 | 2004-08-04 | 325 | 430 | NO | NO | YES | NO | NO | NO | RICKY CARLISLE, AREA BUSINESS LEADER | 6015835402 | RICKY.CARLISLE@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 10 | 0.25 | UNKNOWN | 24000 | FURNACE LAP WELD |  | UNKNOWN | 1930 | UNDER GROUND |  | 6 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | ROAD GRADER WAS GRADING A PRIVATE DRIVEWAY TRAVERSING THE PROPERTY OF EDWIN JOHNSON. THE OPERATOR OF THE GRADER WAS IN THE PROCESS OF MAKING THE SECOND PASS WHEN HE HIT THE PIPELINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040076 | 2004-09-10 18:17 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1450 | 2004-08-12 | 2004 | NORPHLET | UNION | AR | 71759 |  | 26197 | 33.31857 | -92.66751 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74000 | 46087.364 | 101600.6795 | 1000 | 515.7895 | 63000 | 87237.6448 | 10000 | 13847.2452 | NO | NO | NO | YES | 1 | THREAT TO THE PUBLIC | 1 |  | 731651 | 2004-08-12 | 50 | 60 | YES | NO | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | WELD | STEEL |  | NO | NO | NO | OTHER | WELD | 1966 | 8 | 0.19 | UNKNOWN | 24000 | UNKNOWN | NA | UNKNOW |  | UNDER GROUND |  | 24 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1966 | NO | [57 empty] | ON AUGUST 12 OUR FIELD PERSONNEL RECEIVED A CALL ABOUT A LEAK IN NORPHLET, AR. BESIDE A HOUSE AT 508 PURE ST. UPON ARRIVAL GAS DETECTION EQUIPMENT INDICATED 100% LEL BESIDE THE HOUSE. COMPANY PERSONNEL SHUT-IN PIPELINE KM-3 AND UPON EXCAVATION FOUND A LEAK IN A WELD ON THE PIPELINE. THE SECTION WAS CUT OUT AND REPLACE WITH PRE-TEST PIPE. ONE PERSON WAS EVACUATED OVER NIGHT.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040078 | 2004-09-20 | ORIGINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1430 | 2004-08-09 | 2004 | [6 empty] | 28 15.22 N | 93 56.04 W | OFFSHORE |  | HIGH ISLAND | A 469 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345000 | 214564.7756 | 464695.9341 | 15000 | 7736.8421 | 330000 | 456959.092 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 731322 | 2004-08-09 | 898 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R MCDONALD, PRINCIPAL COMPLIANCE | 8326765459 | JIM.MCDONALD@ELPASO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | 0.5 | API 5LX-X42 | 42000 | SEAMLESS |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL |  |  |  | OTHER | SUSPECT INTERNAL CORROSION | YES |  | NO | [57 empty] | UNDER WATER PIPELINE IN APPROXIMATELY 190' OF WATER. SUBSEA CLAMP WAS INSTALLED TO ALLEVIATE THE LEAK. INTERNAL CORROSION IS SUSPECTED EVEN THOUGH NO MEANS TO INVESTIGATE IS AVAILABLE BY VISUAL INSPECTION.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040079 | 2004-09-14 | ORIGINAL FINAL | 30850 |  | GREAT LAKES CHEMICAL CORP | PO BOX 7020 | EL DORADO | UNION | AR | 71731 | 1510 | 2004-08-24 | 2004 | EL DORADO | UNION | AR | 71730 |  |  | 33.11300 | -92.53390 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | [5 empty] | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 732896 | 2004-08-24 | 30 | 30 | NO | NO | NO | NO | NO | NO | JOHN R "PETE" HOWARD, REM ENVIRONMENTAL MGR | 8708641543 | PHOWARD@GLCC.COM | GATHERING | BODY OF PIPE |  | PLASTIC |  | NO | NO | NO | PIPELINE |  | 1992 | 10 | 0.97 | SDR11 HDPE |  | FUSED | N/A | UNKNOWN |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040080 | 2004-09-15 | ORIGINAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1543 | 2004-08-21 | 2004 | ALVA | WOODS | OK | 73717 | 0/0 | 0+00 | W 98-41-27 | N 36-43-34 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | INCORRECT TORQUE VALUE USED ON STUD BOLTS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525000 | 327140.4354 | 725850.758 | 1300 | 670.5263 | 523700 | 725180.2317 | 0 | 0 | NO | NO | YES | NO | 0 |  | 0 | 12 | 732605 | 2004-08-21 | 1280 | 1380 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS, PRINCIPLE ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENGERGY.COM | TRANSMISSION | JOINT |  | OTHER | SYNTHEIC FIBER GASKET | NO | NO | NO | COMPRESSOR |  | 2003 | [8 empty] | INSIDE/UNDER BUILDING |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | INCORRECT TORQUE VALUE USED ON STUD BOLTS |  | IN 2003, A CONTRACTOR WAS REATTACHING THE PULSATION BOTTLE ON UNIT E201. HE INSERTED A NEW FLANGE GASKET BETWEEN THE COMPRESSOR CYLINDER AND THE FLANGE OF THE PULSATION BOTTLE. THE GASKET USED WAS LISTED AS APPROVED IN THE COMPANY PROCEDURES FOR THAT PRESSURE AND APPLICATION. THE CONTRACTOR TORQUED THE BOLTS ACCORDING TO THE TORQUE VALUE GIVEN TO HIM. DURING THE INVESTIGATION, IT WAS FOUND THAT THE TORQUE VALUES GIVEN TO THE CONTRACTOR WERE TAKEN FROM THE INCORRECT TORQUE VALUE TABLE. A CONTRIBUTING FACTOR WAS THAT THE ACTUAL PRESSURE RATING OF THE GASKET USED WAS LOWER THAN THE RANGE SPECIFIED IN THE COMPANY PROCEDURES. PRIMARY CAUSE WAS DETERMINED TO BE THE INCORRECTLY TORQUED BOLTS WITH A CONTRIBUTING FACTOR OF INADEQUATE PRESSURE RATING FOR THE GASKET ALLOWED BY THE COMPANY PROCEDURES.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040081 | 2004-09-25 14:28 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1530 | 2004-08-30 | 2004 | [8 empty] | OFFSHORE |  | GALVESTON | 394 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50800 | 31342.9165 | 60959.5072 | 10800 | 5570.5263 | 40000 | 55388.9808 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 733558 | 2004-08-30 | 1095 | 1250 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12 | 0.31 | API 5LX | 52000 | SEAMLESS | ANSI 600 |  | 1990 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1990 | NO | [57 empty] | THE LEAK WAS DISCOVERED OFFSHORE AT GA 394 AND REPORTED TO WGP GAS CONTROL. DIVERS DISCOVERED A 1/2" HOLE IN THE 5:00 POSITION. THE LEAK WAS CLAMPED AND THE PIPELINE RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040082 | 2004-09-22 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 2345 | 2004-09-06 | 2004 | PERRYTOWN | OCHILTREE | TX | 79070 | 65.906 TXM10302 |  | 36.3000 | -100.7997 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR PART FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 150687.1414 | 194117.497 | 175000 | 90263.1579 | 75000 | 103854.3391 | 0 | 0 | NO | NO | YES | NO | 0 |  | 3 | 15 | 734270 | 2004-09-07 |  | 860 | YES | NO | NO | NO | NO | NO | JOHN A GORMLEY, SR PIPELINE SAFETY SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | OTHER | COMPRESSOR UNIT DISCHARGE VALVE CAP JACK BOLT | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1950 | [8 empty] | INSIDE/UNDER BUILDING |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | COMPRESSOR VALVE JACK BOLT | [8 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | AT 11:45 PM ON SEPTEMBER 6, 2004 NORTHERNS GAS CONTROL RECEIVED NOTIFICATION THAT THE NORTHRUP COMPRESSOR STATION HAD EXPERIENCED AN ESD. GAS CONTROL HAD ALSO RECEIVED ALARM SIGNALS FROM BOTH THE GAS AND FIRE DETECTION SYSTEMS. AT 12:02 AM ON SEPTEMBER 7, 2004 NORTHERNS OPERATIONS COMMUNICATION CENTER (OCC) RECEIVED A CALL FROM THE OCHILTREE COUNTY, TX SHERIFF'S DEPARTMENT REPORTING AN EXPLOSION AND FIRE AT THE NORTHRUP COMPRESSOR STATION. THE STATION WAS UNMANNED AT THE TIME AND NO INJURIES WERE REPORTED. THE NORTHRUP COMPRESSOR STATION IS LOCATED 6 MILES SOUTH OF PERRYTOWN, TX ON US HIGHWAY 83. THE STATION HAS TWO NATURAL GAS COMPRESSOR UNITS AND A STATION DEHYDRATION UNIT, AND COMPRESSES GAS RECEIVED FROM GATHERING FIELDS INTO THE TEXAS A-LINE (TXM10301) UPSTREAM OF THE BEAVER COMPRESSOR STATION. THE STATION WAS FLOWING 27 MMCF/D AT THE TIME OF THE ESD. THE CAUSE OF THE INCIDENT WAS A JACK BOLT ON THE OUTBOUND DISCHARGE VALVE CAP ON COMPRESSOR CYLINDER FOUR OF UNIT ONE CAME LOOSE AND ALLOWED GAS TO ESCAPE INTO THE ENGINE ROOM. A JACK BOLT IS A VERY LONG BOLT THAT THREADS THROUGH THE CENTER OF THE COMPRESSOR VALVE CAP. ITS PURPOSE IS TOE PUSH THE VALVE TO THE POINT THAT IT COMPRESSES THE GASKET WHEN THE VALVE IS INSTALLED, THUS FORMING A NECESSARY SEAL. THE JACK BOLT PROTRUDES OUT OF THE AP COMPLETELY AND HAS A LOCK NUT THAT IS TIGHTENED AGAINST THE CAP. GAS LEAKING FROM THE MISSING JACK BOLT WAS MOST LIKELY IGNITED BY DEBRIS EXITING THE LEAK AND STRIKING STRUCTURAL STEEL ADJACENT TO THE UNIT. THE RESULTING EXPLOSION CAUSED EXTENSIVE DAMAGE TO THE BUILDING SKIN, DOORS, WINDOWS AND LIGHTER SUPPORT PURLINS. FIRE DAMAGE WAS LIMITED AND MINIMAL. IN ORDER TO COME LOOSE THE JACK BOLT WOULD HAVE HAD TO LOSE PRELOAD. PRELOAD COULD HAVE BEEN LOST DUE TO GASKET FAILURE, VALVE FAILURE, IMPROPER TORQUEING, OR IMPROPER VALVE ASSEMBLY. AN AUGUST 25, 2004 COMPRESSOR ANALYSIS SHOWED NO INDICATION OF IMPROPER VALVE ASSEMBLY. THERE ARE NO FINDINGS THAT PROVIDE AN ABSOLUTE DETERMINATION OF THE CAUSE OF THE FAILURE. IT MAY HAVE BEEN A COMBINATION OF THE FACTORS ABOVE OR IT MAY HAVE BEEN A FACTOR NOT YET CONSIDERED.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040083 | 2004-09-22 | ORIGINAL FINAL | 22175 |  | DYNEGY MIDSTREAM SERVICES, L.P. | 1000 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 850 | 2004-08-30 | 2004 | [6 empty] | 29,11,45 N | 93,18,17 W | OFFSHORE |  | WEST CAMERON | 225 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53000 | 32854.1675 | 68176.7893 | 6000 | 3094.7368 | 47000 | 65082.0525 | 0 | 0 | NO | NO | NO | NO | 0 |  | 37 | 10 | 733503 | 2004-08-30 | 940 | 1300 | NO | YES | NO | NO | NO | NO | TIM HUFFER ES&H ADVISOR | 3375834642 | TIM.HUFFER@DYNEGY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 12 | 0.31 | API 5LX | 52000 | SMLS |  | UNKNOWN |  | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1969 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040084 | 2004-09-29 09:32 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1000 | 2004-09-28 | 2004 | ALIQUIPPA | BEAVER | PA | 15001 |  | 59+00 |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | CIRCUMFERENTIAL CRACK AND LEAK IN WRINKLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 105943.4855 | 235403.1686 | 0 | 0 | 170000 | 235403.1686 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 736638 | 2004-09-28 | 150 | 200 | NO | NO | NO | NO | YES | NO | DAVID ANDERSON | 7242232766 | DDANDERSON@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 16 | 0.25 | API 5LX | 42000 | EW |  | UNKNOWN |  | UNDER WATER |  | 0 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | DAMAGE BY FLOOD DEBRIS | [51 empty] | COLUMBIA GAS TRANSMISSION LINE 1913 WAS WASHED OUT BY HEAVY RAINS AND SEVERE FLOOD CONDITIONS DUE TO HURRICANE IVAN. LARGE ROCKS AND OTHER DEBRIS WASHED DOWN THE STREAM, DAMAGING THE PIPELINE. THE PIPE DAMAGE AND A SMALL LEAK WERE DISCOVERED ON SEPTEMBER 27, 2004. FURTHER INVESTIGATION ON SEPTEMBER 28, 2004 SHOWED THAT THE LEAK HAD INCREASED IN SIZE. IMMEDIATE ACTION WAS TAKEN TO ISOLATE THIS SECTION OF PIPELINE AND REDUCE THE LINE PRESSURE TO A SAFE LEVEL. THIS SECTION OF PIPE HAS BEEN REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040085 | 2004-09-30 07:59 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 2305 | 2004-09-16 | 2004 | PERRYSVILLE | RICHLAND | OH | 44864 |  |  | 40.70678 | -82.36367 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | EQUIPMENT FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69907 | 41523.7068 | 36057.2947 | 69907 | 36057.2947 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 11 | 735412 | 2004-09-17 | 1040 | 1200 | NO | NO | YES | NO | NO | NO | MARK A. NEWMAN | 3043572869 | MNEWMAN@NISOURCE.COM | TRANSMISSION | OTHER | AUTOMATION ON SENSING LINES | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1964 | 1 | 0.18 | GRADE B | 35000 |  |  |  |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | ORIFICES ON SENSING LINES | [10 empty] | BACKGROUND AT APPROXIMATELY 11:05 PM ON SEPTEMBER 16, 2004 THE UNLOADER BOTTLE ON COMPRESSOR CYLINDER #5 OF UNIT #4, A CLARK TLA-10, AT LUCAS COMPRESSOR STATION FAILED CAUSING A STATION BLOW-DOWN, WHICH TRIGGERED THE ESD SYSTEM. DURING THE STATION BLOW-DOWN, FIRE GATES ON SL-3054 AND SL-3136 FAILED TO CLOSE RESULTING IN A GAS LOST OF 11,758 MCF. THE TOTAL COST FOR THIS INCIDENT WAS $69,907. FAILURE ANALYSIS COOK MANLEY CONDUCTED A FAILURE ANALYSIS ON THE UNLOADER BOTTLE (SEE ATTACHED REPORT) AND DETERMINED THAT THE ROOT CAUSE OF THIS FAILURE WAS A DATA ENTRY ERROR IN THE BOLT SIZING PROGRAM. COOK MANLEY ALSO INVESTIGATED ALL OTHER UNLOADER BOTTLES INSTALLED ON COMPRESSOR UNITS FOR THE LAST FIVE YEARS AND HAVE CONFIRMED THAT CALCULATIONS FOR ALL OTHER ASSEMBLIES ARE CORRECT. COLUMBIA CONDUCTED A ROOT CAUSE ANALYSIS FOR THE ESD FAILURE AND DETERMINED THAT THE 1" COMPRESSED AIR ESD SUPPLY LINE HAD PLUGGED OFF DUE TO BLACK POWDER LIKE MATERIAL. THE SYSTEM WAS CLEANED AND THE ESD WAS RE-TESTED AND PERFORMED TO SATISFACTION. REMEDIAL ACTION COOK MANLEY WILL REPLACE THE AFFECTED ASSEMBLIES. COLUMBIA HAS REQUESTED THAT COOK MANLEY SUPPLY 0.750 INCH BOLTS WITH 16 THREADS PER INCH TO SECURE THE ACTUATOR TO THE VALVE CAP. THIS STUD SIZE IS IN EXCESS OF WHAT IS REQUIRED HOWEVER IT WILL SERVE TO FURTHER BOLSTER THE SAFETY FACTOR ON THIS UNIT. COOK MANLEY WILL ALSO TAKE THE FOLLOWING CORRECTIVE ACTION TO FURTHER REDUCE THE CHANCES OF SUCH AN ERROR FROM HAPPENING AGAIN: 1) THE COMPUTER PROGRAM WILL BE REVISED TO INCLUDE A NOTE, REMINDING DESIGNERS OF THE IMPLICATIONS AND IMPORTANCE OF USING SUCTION PRESSURE INSTEAD OF AMBIENT PRESSURE. 2) A FUTURE REVISION TO THE PROGRAM WILL REQUIRE THE DESIGNER TO SELECT THE PROPER ASSEMBLY AND THEN PROMPT THE USER FOR THE CORRECT PRESSURE. 3) COOK MANLEY IS REVIEWING ALL OF THE CRITICAL CALCULATIONS IN OUR DESIGNS AND VERIFYING THE RESULTS AUTOMATED CALCULATIONS. THE PURPOSE IS TO IDENTIFY AREAS WHERE A DESIGN ERROR COULD RESULT IN THE RELEASE OF GAS. A LIST OF THESE CALCULATIONS/DECISIONS WILL BE INCORPORATED INTO AN ENGINEERING STANDARD. PROCEDURES WILL BE PUT INTO PLACE REQUIRING THE DRAWING ROOM CHECKER TO REVIEW AND INITIAL A COPY OF THE ENGINEERING STANDARD CERTIFYING THAT THE LIST OF CALCULATIONS WAS CRITICALLY REVIEWED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040086 | 2004-09-24 | SUPPLEMENTAL FINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 2330 | 2004-08-15 | 2004 | RACHEL | BROOKS | TX | 78353 | 54.3 |  | 26.51.31 | 98.21.14 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434406 | 265215.1212 | 437770.5345 | 188463 | 97207.2316 | 225943 | 312868.8125 | 20000 | 27694.4904 | NO | NO | NO | NO | 0 |  | 3 | 0 | 731930 | 2004-08-16 | 665 | 672 | NO | NO | NO | YES | NO | NO | KEVIN P SEHY, PR COMPLIANCE SPECIALIST | 2105284206 | KEVIN.SEHY@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 20 | 0.25 | X52 | 52000 | SAW |  |  |  | UNDER GROUND |  | 39 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED |  |  | STRESS CORROSION CRACKING | PRELIMINARY INVESTIGATION INDICATES SCC | YES | 1960 | NO | [57 empty] | PIPELINE RUPTURED WHILE OPERATING BELOW MAOP. PIPE SECTION WAS REMOVED AND SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS. PRELIMINARY INVESTIGATION INDICATES STRESS CORROSION CRACKING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040087 | 2004-10-04 20:59 | SUPPLEMENTAL FINAL | 17090 |  | RATON GAS TRANSMISSION CO | 1115 SOUTH SECOND STREET | RATON | COLFAX | NM | 87740 | 1530 | 2004-09-15 | 2004 |  | LAS ANIMAS | CO | 81082 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | PERFORATION, 1/2 | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41389 | 25382.7787 | 45095.1364 | 14060 | 7252 | 27329 | 37843.1364 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 45 | 735105 | 2004-09-15 | 285 | 455 | NO | YES | NO | NO | NO | NO | DAVID N. LINK | 2148910892 | DLINK@RATONGAS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 8.63 | 0.16 | X-42 |  | ERW |  | US STEEL | 1963 | UNDER GROUND |  | 30 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | NO |  |  |  |  | YES |  | YES | ACCURATE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040088 | 2004-09-17 | SUPPLEMENTAL FINAL | 117 |  | AIR PRODUCTS & CHEMICALS INC | 1002 STRANG ROAD | LAPORTE | HARRIS | TX | 77571 | 1004 | 2004-07-28 | 2004 | PORT ARTHUR | JEFFERSON | TX | 77641 |  |  | 29.889067 | -93.9835358 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE |  |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 124493.3346 | 272600.229 | 5000 | 2578.9474 | 195000 | 270021.2816 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 40 |  | 2004-07-28 | 780 | 860 | NO | YES | NO | NO | NO | NO | KERRY J SERNER, GLOBAL OPERATIONS/PIPELINE MAINT | 6104818422 | STERNEKI@APCI.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1992 | 6 | 0.28 | AP5L | 42000 | ERW | N/A | HACKNEY INC | 1991 | UNDER GROUND |  | 324 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 7 | 28 | 2004 | ONE-CALL SYSTEM | YES |  | YES | INACCURATE | YES | [36 empty] | 1. THE AIR PRODUCTS PIPELINE LATERAL WAS NOT PROPERLY LOCATED BY THE APCI "CONTRACT" PIPELINE TECHNICIAN. 2. AN EXISTING PIPELINE P.I. MARKER WAS MIS-LOCATED AND SERVED TO ENHANCE FALSE LOCATION OF THE APCI LATERAL INVOLVED. 3. DESPITE THE APCI PIPELINE LATERAL NOT BEING PROPERTY LOCATED, THE "PROPOSED" DIRECTIONAL DRILL PATH, IF PROPERLY EXECUTED BY THE 3RD PARTY CONTRACTOR, WAS ON A PATH WHICH WAS CLEAR AND SHOULD HAVE NOT STRUCK THE APCI PIPELINE. THIS IS BASED ON A PLOTTING OF THE 3RD PARTY SUPPLIED "PROPOSED DRILL PROFILE" SUBMITTED TO APCI AND EXISTING "AS-BUILT" PROFILE OF THE APCI PIPELINE LATERAL INVOLVED. AN "AS BUILT" PROFILE OF THE 3RD PARTY DRILL HAS NOT BEEN MADE AVAILABLE BY THE 3RD PARTY DRILL OPERATOR. 4. THE INVESTIGATION OF THIS INCIDENT HAS BEEN COMPLETED AND CORRECTIVE ACTION IMPLEMENTED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040089 | 2004-10-07 12:05 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | PO BOX 770000 | SAN FRANCISCO | SAN FRANCISCO | CA | 94177-0001 | 305 | 2004-09-06 | 2004 | DOS PALOS | MADERA | CA | 93620 | 19.31 |  | 36.98291 | -120.4991 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 46447.6529 | 95164.9886 | 10000 | 5157.8947 | 65000 | 90007.0939 | 0 | 0 | NO | YES | NO | NO | 0 |  | 3 | 25 | 734230 | 2004-09-06 | 210 | 625 | NO | NO | YES | NO | NO | NO | JEFF BORDERS | 4159735568 | JPB0@PGE.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 6 | 0.28 | GRADE B | 35000 | SEAMLESS | UNKNOWN | UNKNOWN | 1954 | OTHER | VALVE PIT | 36 | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | GRASS FIRE, POSSIBLY STARTED BY ARSON, CAUSED REDWOOD VAULT TO CATCH ON FIRE. RESULTING VAULT FIRE BURNED FLANGE GASKET MATERIAL FOR MAIN LINE VALVE, ALLOWING GAS TO ESXCAPE AND IGNITE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040090 | 2004-10-11 11:38 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | -77002 | 1115 | 2004-09-16 | 2004 |  |  | LA |  | 523M-102+2.68 |  | 28 *41.52' | 91*02.43' | OFFSHORE |  | SHIP SHOAL | 157 |  | YES | NO | INTERSTATE | OTHER | SMALL TEARS IN 12 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2250000 | 1358375.1736 | 1812227.6014 | 1500000 | 773684.2105 | 750000 | 1038543.3909 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 45 | 735259 | 2004-09-16 | 1138 | 1440 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | SUB-SEA TIE-IN-6 IN. | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 26 | 0.49 | API | 60000 | DSAW |  |  | 1974 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IVAN DAMAGE | [51 empty] | SMALL LEAK DISCOVERED IN SHIP SHOAL BLOCK 157, AFTER HURRICANE IVAN, WITH A <20 FT. BUBBLE CIRCLE OBSERVED. SUSPECTED IMPACT DAMAGE WITH VALVE GUARD PULLED OFF VALVE ASSEMBLY AND SUB-SEA TIE-IN (6 IN.)ASSEMBLY DAMAGED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040091 | 2004-10-11 15:38 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1640 | 2004-09-16 | 2004 |  |  | LA |  | 523Q-101+35.5 |  | 28*46' | 90*54' | OFFSHORE |  | SHIP SHOAL | 120 |  | YES | NO | INTERSTATE | OTHER | DAMAGE ON LINE NEAR SUB-SEA TIE-IN. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2250000 | 1358375.1736 | 1812227.6014 | 1500000 | 773684.2105 | 750000 | 1038543.3909 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 735311 | 2004-09-16 | 1000 | 1200 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | SUB-SEA TIE-IN | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 36 | 0.6 | API | 60000 | DSAW |  |  | 1979 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IVAN DAMAGE | [51 empty] | LEAK DISCOVERED IN SHIP SHOAL BLOCK 120, AFTER HURRICANE IVAN, WITH A 30 FT. BUBBLE CIRCLE OBSERVED. SUSPECTED IMPACT DAMAGE DUE TO ANCHOR DRAG OR DEBRIS AT SUB-SEA TIE-IN (8 IN.) ASSEMBLY NEAR SV 523Q-301.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040092 | 2004-10-12 16:03 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1515 | 2004-09-17 | 2004 |  |  | LA |  | 526A-701+ 10.81 |  | 28*49.83' | 89*24.21' | OFFSHORE |  | SOUTH PASS | 77 |  | YES | NO | INTERSTATE | OTHER | LINE SEPARATED@SAFETYJOINT DUE TO MUDSLIDE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6550000 | 4080479.5744 | 9026498.8612 | 50000 | 25789.4737 | 6500000 | 9000709.3876 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 735475 | 2004-08-17 | 900 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | BREAKAWAY JOINT ON RISER SECTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 26 | 0.75 | API | 60000 | DSAW |  |  | 1982 | OTHER | UNDERWATER IN RISER SECTION |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | MUDSLIDE | [52 empty] | A LEAK WAS DISCOVERED ON THE 26 IN. SOUTH PASS 77 LINE (FROM SP 77 TO SP 55), LINE NO. 527A-700, NEAR THE BASE OF THE RISER IN THE VICINITY OF THE 'BREAK-AWAY'JOINT. PRELIMINARY DIVE REPORTS INDICATED THAT A MUDSLIDE CAUSED BY HURRICANE IVAN MOVED THROUGH THIS LOCATION, WITH AT LEAST 15 FT. DEPOSITION OF MATERIAL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040093 | 2004-10-14 12:04 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1600 | 2004-09-16 | 2004 |  |  | LA |  |  |  | 29* 16.254' | 88* 33.834' | OFFSHORE |  | MAIN PASS | 293 |  | YES | NO | INTERSTATE | OTHER | MAIN PASS 293 PLATFORM DESTROYED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100000 | 3175383.3626 | 6975201.5532 | 100000 | 51578.9474 | 5000000 | 6923622.6058 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 735309 | 2004-09-16 | 1100 | 1200 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | UNKNOWN AT THIS TIME | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 24 | 0.5 | A | 60000 | SAW |  | US STEEL | 1970 | OTHER | MAIN PASS 293 PLATFORM |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | 52 FT. WAVE HEIGHTS DURING HURRICANE IVAN | [51 empty] | MAIN PASS 293 PLATFORM DESTROYED DURING HURRICANE IVAN, ALONG WITH DAMAGE TO MP 289 LINE (24 IN. LINE FROM MP 289), MP 306 LINE (18 IN. LINE FROM MP 306)AND THE MP 293 LINE (24 IN. LINE TO MP 298). ALL PRODUCTION UPSTREAM OF MP 293 WAS SHUT-IN. REVIEWING OPTIONS TO REPLACE PLATFORM OR INSTALL A SUB-SEA TIE-IN ASSEMBLY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040094 | 2004-10-14 15:09 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 930 | 2004-09-17 | 2004 |  |  | LA |  | MAIN PASS 293, MP 17.191 |  | 29* 16.4' | 88* 43.3' | OFFSHORE |  | MAIN PASS | 298 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 311598.4866 | 692362.2606 | 0 | 0 | 500000 | 692362.2606 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 735396 | 2004-09-17 | 1100 | 1200 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | RISER SECTION, BELOW WATER | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 24 | 0.5 | API | 60000 | SAW |  | UNKNOWN | 1971 | OTHER | UNDERWATER IN RISER SECTION, MAIN PASS 293 LINE |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | SEVERE WAVE LOADS DAMAGED RISER | [51 empty] | WHILE ASSESSING THE CONDITION OF THE MAIN PASS 293 LINE (24 IN. LINE FROM MP 293) LEAK WAS DISCOVERED, WITH BUBBLES OBSERVED ON SURFACE NEAR THE MAIN PASS 298 PLATFORM. APPARENTLY, MP 293 LINE WAS DAMAGED BY HURRICANE IVAN, CAUSING SEVERE DAMAGE TO THE RISER SECTION, AT THE -150 FT. ELEVATION. GAS LOSS WAS REPORTED ON REPORT ID 20040093 -- 1075.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040095 | 2004-10-05 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1130 | 2004-09-06 | 2004 | GULF OF MEXICO |  | TX |  | 1.5 MILES UPSTREAM OF MUS | N/A | N 27.5646 | W 96.6981 | OFFSHORE |  |  | 805 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351800 | 216734.3047 | 412591.4595 | 85800 | 44254.7368 | 266000 | 368336.7226 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 734231 | 2004-09-06 | 950 | 1250 | YES | NO | NO | NO | NO | NO | JACK GUINN, SENIOR PIPELINE SAFETY ENGINEER | 4023987396 | JACK.GUINN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.38 | API 5L | 60000 | DOUBLE SUBMERGED ARC WELD |  | STELCO | 1985 | UNDER WATER |  | 72 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1986 | NO | [57 empty] | A LEAK WAS REPORTED TO NORTHERN NATURAL GAS COMPANY (NNG) ON 9/6/2004, BY PERSONNEL AT MUSTANG ISLAND 787. THE INITIAL REPORT INDICATED SMALL BUBBLES IN A 3' AREA WITH NO SHEEN AT APPROXIMATE COORDINATES N27 33.878 W96 41.888. A HELICOPTER WAS DISPATCHED WITH LYNDON LANGE OF CENTERPOINT ENERGY TO INVESTIGATE. THE LEAK WAS DETERMINE TO BE ON THE 20" NNG LINE SEGMENT TOS 84061 (MMS #7292). THE LEAK WAS REPAIRED USING A PLIDCO CLAMP RATED AT 1500 PSIG (WORKING PRESSURE). THE REPAIR WAS COMPLETED ON 9/11/2004. NORTHERN DETERMINE THAT IT WOULD NOT RETURN THIS SEGMENT OF PIPELINE TO SERVICE UNTIL AN ABANDONMENT HAD BEEN COMPLETED ON THIS SECTION OF PIPING. THEREFORE, THE LEAK CLAMP WAS INSTALLED, BUT A LEAK TEST HAS NOT BEEN PERFORMED AND SAND BAGS HAVE NOT BEEN INSTALLED FOR COVER. SAND BAGS WILL BE INSTALLED OVER THE LEAK AREA ONCE THE ABANDONMENT HAS BEEN COMPLETED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040096 | 2004-10-19 | ORIGINAL FINAL | 31613 |  | ENBRIDGE PIPELINES (EAST TEXAS) L.P. | 540 PRIVATE ROAD 2297 | LONGVIEW | HARRISON | TX | 75604 | 810 | 2004-09-03 | 2004 | CAYUGA | ANDERSON | TX | 75832 | MILE POST 11.68 | 617.14 | 31 59.022" | 95 51.451"W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33685 | 19141.7457 | 25901.075 | 20685 | 10669.1053 | 11000 | 15231.9697 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 |  |  | 780 | 1038 | YES | NO | NO | NO | NO | NO | ROBERT VON HAUSEN, EH&S DEPARTMENT | 9034513004 | BOB.VONHAUSEN@ENBRIDGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 12.75 | 0.22 | X-42 |  | ERW | NA | LONE STAR STEEL | 1970 | UNDER GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  |  |  | YES |  | NO | [57 empty] | 9:30 AM: NOTIFICATION RECEIVED REGARDING PIPELINE LEAK ON OUR "TRI CITIES TO GRAPELAND 12" LOCATED IN ANDERSON COUNTY TX. THIS LEAK WAS INITIALLY REPORTED TO ENBRIDGE/HOUSTON GAS CONTROL BY 'PIPELINE MOWERS' WORKING FOR ANOTHER OPERATOR. SYSTEM DESCRIPTION: THIS 17.5 MILE, 12" JURISDICTIONAL/TRANSMISSION LINE OPERATING UNDER T-4 PERMIT # 04409, CURRENTLY MOVING - ~20MMCF OF 'SWEET' GAS @ ~750 PSI WITH ISOLATION BLOCK VALVES LOCATED AT VALERO & TRI - CITIES. DRIVING DIRECTIONS TO LEAK: TRAVEL NORTH OUT OF CAYUGA ON HWY 59 TO FM 2961 AND TURN RIGHT. TRAVEL ~ 7 MILES TO SITE. NOTIFICATIONS: 10:00 AM ENBRIDGE ED&S NOTIFIED PIPELINE SAFETY/AUSTIN/'JULIE' PROVIDING HER W/DETAILS AS CURRENTLY KNOWN. RECEIVED TRACKING NO 04-CA-005 10:15 AM: ENBRIDGE EH&S NOTIFIED PIPELINE SAFETY/KILGORE/'BOB REED' PROVIDING HIM W/DETAILS AS CURRENTLY KNOWN. CONFIRMED TRACKING NO 04-CA-005. RRC - IN ACCORDANCE WITH 49 CFR PART 191; NO LATER THAN 30 DAYS AFTER THE INCIDENT, FORM RSPA F 7100.2 FOR "INCIDENT REPORT - GAS TRANSMISSION & GATHERING SYSTEM" WILL BE SUBMITTED. ON OCT 1, 2004 THIS REPORT WAS FAXED TO RRC/PIPELINE SAFETY/AUSTIN MEETING THE 30 DAY WRITTEN REPORT REQUIREMENT. 'HARD COPY(S) OF REPORT WILL BE MAILED ON MONDAY, OCT 4, 2004.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040097 | 2004-10-27 10:04 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1722 | 2004-09-24 | 2004 | HOPKINTON | MIDDLESEX | MA |  | 266-1 +9.31 |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72000 | 44782.546 | 97093.3604 | 3000 | 1547.3684 | 0 | 0 | 69000 | 95545.992 | YES | NO | NO | YES | 28 | THREAT TO THE PUBLIC | 2 | 30 | 736271 | 2004-09-24 | 610 | 700 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 24 | 0.5 | API | 52000 | DSAW |  | US STEEL | 1977 | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | PIPE RESTING ON ROCK LEDGE | [10 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 7 | 2 | 1977 | WATER |  | 8 | 1110 | [12 empty] | THE LEAK OCCURRED ON TENNESSEE GAS PIPELINE'S MAIN LINE 200-1, 24" X52 PIPELINE, JUST UPSTREAM OF COMPRESSOR STATION 267. THE LEAK WAS APPARENTLY DUE TO THE PIPE RESTING ON A ROCK LEDGE, WHICH SUBSEQUENTLY DAMAGED THE PIPE. THE PIPELINE SEGMENT WAS ISOLATED, BLOWN DOWN AND REPAIRED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040098 | 2004-10-27 15:59 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1200 | 2004-10-05 | 2004 | JENA | LA SALLE | LA |  | 2-501/ VS 8 |  | 31*31'32 | -92*12'13 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BROKEN 1/2 IN. TAP VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92000 | 54705.0406 | 49190.5017 | 90000 | 46421.0526 | 2000 | 2769.449 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 15 | 737301 | 2004-10-04 | 710 | 858 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | 1/2 IN. TAP VALVE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1973 | 36 | 0.33 | API | 65000 | UNKNOWN |  | NIPPON | 1973 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | WHILE PERFORMING VALVE MAINTENANCE ACTIVITY AT THE JENA COMPRESSOR STATION, A CONTRACT EMPLOYEE BROKE A 1/2 IN. TAP VALVE CONNECTION TO THE 2-501 LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040099 | 2004-10-29 14:46 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 121 | 2004-09-29 | 2004 | SHELDON | HOUSTON | MN |  | M.P. 5.50 |  | 43.73311N | 91.5458W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239500 | 143939.0891 | 173495.3442 | 182000 | 93873.6842 | 50000 | 69236.2261 | 7500 | 10385.4339 | NO | NO | NO | NO | 0 |  | 1 | 24 | 736785 | 2004-09-29 | 530 | 800 | NO | YES | NO | NO | NO | NO | PATRICK L VAUGHAN | 4023987185 | PAT.VAUGHAN@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 6 | 0.16 | API 5L | 35000 | ERW |  | LONE STAR STEEL | 1966 | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | A CONTRACTOR WAS CUTTING A LOGGING ROAD ON A STEEP HILL SIDE NEAR HOUSTON, MINNESOTA AND STRUCK THE LINE WITH THE CORNER OF THE DOZER BLADE. THE BULLDOZER OPERATOR SHUT THE MACHINE OFF AND ABANDONED IT IN PLACE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040100 | 2005-10-06 | SUPPLEMENTAL FINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 |  | 2004-09-17 | 2004 | [6 empty] | 28 51 55.037 | 89 16 41.02 | OFFSHORE |  | VIOSCA KNOLL | 817 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26251249 | 16350935.3184 | 36090067.6872 | 300000 | 154736.8421 | 25951249 | 35935330.8451 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 736541 | 2004-09-26 | 901 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY, JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 20 | 0.5 | API 5L | 65000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | <P>HURRICANE IVAN'S PATH CROSSED OVER ENTERPRISE'S (FORMERLY EL PASO FIELD SERVICES) VK 817 PLATFORM CAUSING DAMAGE TO THE PLATFORM AND DEPARTING PIPELINES. STRUCTURE REPAIRS TO THE PLATFORM AND PIPING FACILITIES HAVE BEEN COMPLETED. THIS INCIDENT WAS ORIGINALLY FILED UNDER EL PASO FIELD SERVICES, OPS ID NO. 30950 </P> <P>UPDATED BY PHMSA 4/10/2015: THE ORIGINAL INCIDENT REPORT WAS SUBMITTED BY EL PASO UNDER OPID 30950 SINCE THEY OWNED AND OPERATED THE VK 817 PLATFORM AND DEPARTING PIPELINES.&nbsp; EPROD PURCHASED THE ASSETS AND A YEAR LATER FILED AN ORIGINAL INCIDENT REPORT FOR THE SAME INCIDENT; HOWEVER, THAT REPORT SHOULD HAVE BEEN A SUPPLEMENTAL TO THE ORIGINAL EL PASO REPORT.&nbsp; SINCE THE REPORT AND PROPERTY DAMAGES WERE BEING DOUBLE COUNTED, PHMSA RE-ASSOCIATED THE EPROD FILING AND MADE IT A SUPPLEMENTAL/FINAL REPORT TO THE EL PASO REPORT 20040100-1097.&nbsp; THE GAS TRANSMISSION REPORT NUMBER 20050116-1523 WHICH WAS FOR THE ORIGINAL EPROD REPORT NUMBER IS NOW REPRESENTED AS 20040100-1523 AND IS THE SUPPLEMENTAL/FINAL REPORT FOR THE 9/17/2004 INCIDENT INVOLVING THE VK 817 PLATFORM AND DEPARTING PIPELINES.&nbsp; IT'S PHMSA'S UNDERSTANDING THAT THESE ASSETS HAVE SINCE BEEN ABANDONED AND ARE NO LONGER IN OPERATION. - JPENDER</P>
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20040101 | 2004-10-28 | SUPPLEMENTAL FINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1430 | 2004-08-26 | 2004 | [6 empty] | 28 13.755 N | 94 11.039W | OFFSHORE |  | HIGH ISLAND | 489 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394008 | 245416.586 | 541784.8658 | 4382 | 2260.1895 | 389626 | 539524.6763 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 733153 | 2004-08-26 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R MCDONALD, PRINCIPAL COMPLIANCE | 7138032494 | JMCDONALD@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.44 | API-5LX 52 | 52000 | SEAMLESS |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | SUB SEA INSPECTION | OTHER | SUSPECT INTERNAL CORROSION | YES | 1981 | NO | [57 empty] | UNDER WATER PIPELINE IN APPROXIMATELY 190' OF WATER. SUBSEA CLAMP WAS INSTALLED TO ALLEVIATE THE LEAK. INTERNAL CORROSION IS SUSPECTED EVEN THOUGH NO MEANS TO INVESTIGATE IS AVAILABLE BY VISUAL INSPECTION. 2ND LEAK WAS IDENTIFIED UPON PRESSURING UP PIPELINE AND NRC 735634 WAS ASSIGNED TO THAT LEAK. GAS LOSS AND DAMAGE FIGURES ARE A COMBINED TOTAL FOR THE REPAIR OF BOTH LEAKS.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20040102 | 2004-10-28 | ORIGINAL | 30950 |  | EL PASO FIELD SERVICES | FOUR GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1345 | 2004-09-19 | 2004 | [6 empty] | 28 13.755 N | 94 11.039W | OFFSHORE |  | HIGH ISLAND | 489 |  | YES | NO | INTRASTATE |  |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 735634 | 2004-09-19 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R MCDONALD, PRINCIPAL COMPLIANCE | 8326765459 | JIM.MCDONALD@ELPASO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.44 | API 5LX-52 | 52000 | SEAMLESS |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL |  |  |  | OTHER | SUSPECT INTERNAL CORROSION | YES |  | NO | [57 empty] | UNDER WATER PIPELINE IN APPROXIMATELY 190' OF WATER. SUBSEA CLAMP WAS INSTALLED TO ALLEVIATE THE LEAK. INTERNAL CORROSION IS SUSPECTED EVEN THOUGH NO MEANS TO INVESTIGATE IS AVAILABLE BY VISUAL INSPECTION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040103 | 2004-11-09 | ORIGINAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 EAST GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 830 | 2004-10-12 | 2004 | ARNAUDVILLE | ST LANDRY | LA | 70512 | 60.27 | 3182+40 | 30.41764 | 91.89729 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  |  | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61608 | 37858.3461 | 69379.0531 | 18334 | 9456.4842 | 43274 | 59922.5689 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 738085 | 2004-10-12 | 855 | 1000 | YES | NO | NO | NO | NO | NO | JULES MAYEUX, AREA BUSINESS LEADER | 3379887105 | JULES.MAYEUX@GULFSOUTHPL.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | 2" TAP FLANGE | 1989 | 2 | 0.25 | ANSI 600 | [5 empty] | UNDER GROUND |  | 84 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | ON OCT 4, 2004 A GULF SOUTH EMPLOYEE REPORTED A LEAK INDICATION AT AN UNDERGROUND TAP VALVE NEAR 304 KOCH RD., ARNAUDVILLE, LA. THE TIME OF ACTUAL LEAK OCCURRENCE IS UNKNOWN. AT THE TIME OF DISCOVERY OF THE LEAK WAS CLASSIFIED AS A GRADE 2 REQUIRING SCHEDULED REPAIR ACTION. A 20% REDUCTION OF PRESSURE ON THE PIPELINE PRIOR TO EXCAVATING THE LEAK WAS INITIATED ON 10-5-04 AND WAS ACHIEVED BY 10-8-04. HOWEVER BECAUSE THE REDUCTION IN PRESSURE DID NOT SIGNIFICANTLY CHANGE IN THE LEAKAGE RATE THE DECISION WAS MADE TO REDUCE THE LINE PRESSURE TO ZERO TO PROVIDE EMPLOYEE SAFETY DURING THE EXCAVATION. A COMPRESSOR WAS BROUGHT IN TO REDUCE THE AMOUNT OF GAS THAT WOULD BE RELEASED TO ATMOSPHERE TO REMOVE THE PIPELINE FROM SERVICE. ON 10-12-04 AT 8:30 AM AN EVALUATION OF THE ESTIMATED COST OF REPAIR AND GAS LOST WAS DETERMINE THAT THE THRESHOLD OF $50,000 MIGHT BE MET AND THEREFORE A TELEPHONIC REPORT WAS MADE TO THE NATIONAL RESPONSE CENTER AT 10:15 AM. AT 11:30 AM 10-12-04 THE REDUCTION TO ZERO PRESSURE WAS INITIATED AND COMPLETED AT 6:14 AM ON 10-14-04. THE TAP WAS EXCAVATED ON 10-14-04 AND THE CAUSE OF THE LEAK WAS DETERMINED TO BE A CRACK IN A 2" WELD NECK FLANGE. IT APPEARS A SUMMER DRAUGHT MAY HAVE CAUSED SETTLING OF THE SOIL AROUND THE TAP VALVE ASSEMBLY THUS PUTTING UNDUE PRESSURE ON THE COMPONENT CAUSING IT TO CRACK. THE CRACKED FLANGE WAS REMOVED AND A NEW ONE INSTALLED ON 10-14-04.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040104 | 2004-11-09 | SUPPLEMENTAL FINAL | 30950 |  | EL PASO FIELD SERVICES | 4 GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1520 | 2004-09-29 | 2004 | ENCINAL | LASALLE | TX | 78019 | MP 103 |  | 28.06919 | 98.86062 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 51949.3223 | 87288.8576 | 35000 | 18052.6316 | 50000 | 69236.2261 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 736813 | 2004-09-29 | 580 | 1030 | NO | NO | NO | NO | YES | NO | KEVIN P SEHY, PR COMPLIANCE SPECIALIST | 2105284206 | KEVIN.SEHY@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 20 | 0.28 | X52 | 52000 | SAW |  |  |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | GENERAL CORROSION |  | STRESS CORROSION CRACKING |  | YES | 1961 | NO | [57 empty] | PIPELINE RUPTURED BELOW MAOP WHILE BEING RETURNED TO SERVICE FROM ROUTINE MAINTENANCE. PIPE SECTION WAS REMOVED AND SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS TO DETERMINE CAUSE. 12-16-04 PIPELINE RUPTURED BELOW MAOP WHILE BEING RETURNED TO SERVICE FROM ROUTINE MAINTENANCE. PIPE SECTION WAS REMOVED AND SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS. THE CAUSE WAS DETERMINED TO BE STRESS CORROSION CRACKING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040105 | 2004-11-22 14:34 | SUPPLEMENTAL FINAL | 1007 |  | K N INTERSTATE GAS TRANSMISSION CO | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228 | 1729 | 2004-11-08 | 2004 | DAVENPORT | THAYER | NE | 68335 |  | 1871+50 | 40.2728042 | -97.8009666 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | OUTSIDE FORCE DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92100 | 57045.8971 | 117105.9078 | 12000 | 6189.4737 | 100 | 138.4725 | 80000 | 110777.9617 | NO | YES | NO | NO | 0 |  | 1 | 30 | 740808 | 2004-11-08 | 600 | 800 | YES | NO | NO | NO | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 6 | 0.13 | X42 | 42000 | ERW |  | TEX-TUBE |  | UNDER GROUND |  | 46 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | NO |  |  |  |  | NO
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040106 | 2004-11-23 12:17 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 10 | 2004-11-23 | 2004 | RANGELY | RIO BLANCO | CO |  | 268 | 14146+98 | 39.54.49 | -108.44.29 | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54000 | 32221.248 | 32197.3068 | 49000 | 25273.6842 | 5000 | 6923.6226 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 740555 | 2004-11-05 | 613 | 809 | NO | YES | NO | NO | NO | NO | PETER THOMAS | 8015846663 | PETER.C.THOMAS@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 26 | 0.28 | API 5L | 52000 | DSAW |  |  |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1958 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040107 | 2004-11-16 | SUPPLEMENTAL FINAL | 13063 |  | NATIONAL FUEL GAS SUPPLY CORP | 1100 STATE STREET | ERIE | ERIE | PA | 16501 | 535 | 2004-10-12 | 2004 | SUMMIT | ERIE | PA | 16509 | N/A | N/A | -80.0638 W | +42.0512 N | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251000 | 149236.2856 | 133807.8331 | 246000 | 126884.2105 | 5000 | 6923.6226 | 0 | 0 | YES | NO | NO | NO | 0 |  | 1 | 15 | 738101 | 2004-10-13 | 790 | 824 | YES | NO | NO | NO | NO | NO | MICHAEL D COLPOYS, SUPERINTENDENT | 8148718339 | COLPOYSM@NATFUEL.COM | TRANSMISSION | OTHER | 2 INCH WELD CONNECTION | STEEL |  | NO | NO | NO | OTHER | VALVE SETTING | 1995 | 2 | 0.15 | ASTM A105 | 35000 | N/A | N/A | N/A |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON OCTOBER 12, 2004, AT APPROXIMATELY 5:35AM, A SILHOUETTE MINI-VAN REGISTERED TO MS. IRENE WASHOK STRUCK AND DAMAGED A NATIONAL FUEL PIPELINE VALVE CAUSING EXTENSIVE DAMAGE AND GAS LOSS. THE INCIDENT TOOK PLACE IN THE NATIONAL FUEL SUMMIT STORAGE FIELD IN THE GENERAL VICINITY OF THE INTERSECTION OF CURTIS AND ROBISON ROADS. IT IS UNKNOWN AT THIS TIME WHO THE DRIVER/PASSENGERS WERE. THE INCIDENT IS CURRENTLY BEING INVESTIGATED BY THE PENNSYLVANIA STATE POLICE, CRIMINAL INVESTIGATION DIVISION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040108 | 2004-11-15 | ORIGINAL | 9012 |  | J - W PIPELINE CO | 3400 WEST MARSHALL SUITE 330 | LONGVIEW | HARRISON | TX | 75604 | 1120 | 2004-10-15 | 2004 | NEW FAIRVIEW | WISE | TX |  |  |  | N 33 9.040' | 97 24.634' | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE |  |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 6085.9097 | 9502.57 | 5000 | 2578.9474 | 5000 | 6923.6226 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 800 | 1236 | NO | YES | NO | NO | NO | NO | CATHY FRAZIER, SAFETY & REGULATORY | 9032957770 | CFRAZIER@JWOPERATING.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6 | 0.16 | X-42 | 42000 | ERW |  | TEX TUBE | 2000 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | ELECTRIC |  | YES | 10 | 6 | 2004 |  | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040109 | 2004-11-15 | SUPPLEMENTAL FINAL | 12408 |  | DTE ENERGY - MICHIGAN CONSOLIDATED GAS | 2000 SECOND AVENUE | DETROIT | WAYNE | MI | 48226 | 1042 | 2004-10-25 | 2004 | SOUTH LYON | OAKLAND | MI | 48178 |  | 515+68 | 42.47142 | -83.62917 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 60859.0968 | 95025.6997 | 50000 | 25789.4737 | 50000 | 69236.2261 | 0 | 0 | NO | NO | NO | YES | 100 | PRECAUTIONARY | 5 | 17 | 739427 | 2004-10-25 | 600 | 823 | NO | YES | NO | NO | NO | NO | JOHN D LUEDERS, PE | 6166322646 | LUEDERSJ@DTEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 12 | 0.25 | API5L | 52000 | ERW |  |  |  | UNDER GROUND |  | 0 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | RESIDENTIAL DEVELOPMENT | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | PERMANENT PIPELINE MARKERS WERE IN PLACE. THE EXCAVATOR ADVISED STAKER THAT ADDITIONAL SOIL WAS TO BE FILLED IN PRIOR TO EXCAVATION. STAKER ADVISED EXCAVATOR TO CALL HIM PERSONALLY OR MISS DIG FOR RESTAKING WHEN ALL FILL IN WAS COMPLETED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040110 | 2004-11-29 15:04 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1010 | 2004-11-12 | 2004 |  |  | LA |  | MP 507F-1601+0.00 |  | 29* 20'20.93 | 92*41'25.18 | OFFSHORE |  | EAST CAMERON | 71 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 90558.3449 | 120815.1734 | 100000 | 51578.9474 | 50000 | 69236.2261 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 714208 | 2004-11-12 | 890 | 999 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 12.75 | 0.5 | API | 42000 | SEAMLESS | BALL | GROVE | 1964 | OTHER | ON PLATFORM PIPING |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | PIN HOLE | GALVANIC |  | YES | 1971 | NO | [57 empty] | A SMALL LEAK WAS REPORTED ON THE TENNESSEE GAS PIPELINE (TGP) LINE NO. 507F-1600, AT THE EAST CAMERON BLOCK 71 PLATFORM. A PIN HOLE LEAK WAS FOUND ON THE 12 IN. BLOCK VALVE, NO. 507F-1601. PLATFORM PERSONNEL INITIATED AN ESD, AND THE PIPELINE WAS SUBSEQUENTLY BLOWN DOWN. THE PLATFORM WAS NOT EVACUATED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20040111 | 2004-11-29 16:59 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY - PO BOX 58900 | SALT LAKE CITY | SALT LAKE | UT | 84108 | 857 | 2004-11-09 | 2004 | OREGON CITY | CLACKAMAS | OR |  | M.P. 28.90 | 1526+12 | 45 17' 54 | 122 34' 21 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 46506.0769 | 96902.8587 | 8000 | 4126.3158 | 67000 | 92776.5429 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 20 | 740872 | 2004-11-09 | 816 | 898 | NO | YES | NO | NO | NO | NO | LARRY D. OLSEN | 8015846117 | LARRY.D.OLSEN@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1976 | 16 | 0.28 | X52 | 1826 | SEAMLESS | N/A | UNKNOWN | 1976 | UNDER GROUND |  | 60 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | RESULTS PENDING METALLURGICAL REPORT. SECTION WAS EXPOSED WAS COULD NOT FIND LEAK USING FI. REMOVE SECTION OF PIPE AND HYDROTESTED WAS NOT ABLE TO FIND LEAK.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20040112 | 2004-12-01 13:33 | SUPPLEMENTAL FINAL | 17620 |  | ROCKY MOUNTAIN NATURAL GAS CO INC | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228- | 1500 | 2004-11-16 | 2004 | SNOWMASS | PITKIN | CO | 81654 |  |  | 106 59.36 | 39 20.200 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | MECHANICAL DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 71300 | 43411.5238 | 68318.1317 | 35000 | 18052.6316 | 36300 | 50265.5001 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 741578 | 2004-11-16 | 685 | 720 | NO | NO | NO | YES | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 6 | 0.19 | X-46 | 2610 |  |  |  |  | UNDER GROUND |  | 38 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040113 | 2004-11-02 | SUPPLEMENTAL | 31130 |  | DUKE ENERGY FIELD SERVICES INC | 370 17TH STREET | DENVER | DENVER | CO | 80202 | 830 | 2004-08-18 | 2004 | RAYMONDVILLE | KENNEDY | TX | 78580 | 52.6 |  | 26 36 50 N | 97 49 58 W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104000 | 61891.2841 | 57117.8455 | 100000 | 51578.9474 | 4000 | 5538.8981 | 0 | 0 | NO | NO | NO | NO | 0 |  | 13 | 30 | 732230 | 2004-08-18 | 1236 | 1029 | YES | NO | NO | NO | NO | YES | CYNTHIA L MUNOZ, SR P/L MGMT COMPLIANCE SPECIALIST | 3615848518 | CLMUNOZ@DUKE-ENERGY.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.19 |  | 52000 | ELECTRIC RESISTANCE WELD | N/A | N/A |  | UNDER GROUND |  | 48 | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | ESD VALVE | [10 empty] | ON AUGUST 18, 2004, DEFS WAS NOTIFIED OF A PIPELINE LEAK ON THE GARCIA PROPERTY LOCATED APPROXIMATELY 7.5 MILES NORTHWEST OF RAYMONDVILLE, TX IN KENNEDY COUNTY. THE LINE OVER-PRESSURED AND OUR ESD VALVE FAILED. ALL PRODUCERS AND MAINLINE VALVES WERE SHUT IN AND THE RUPTURED SECTION OF THE LINE WAS ISOLATED. REPAIRS WERE MADE AND LINE WAS BACK IN SERVICE ON 8-25-04. (DTIP WILLAMAR LATERAL)
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040115 | 2004-10-07 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 |  | 2004-10-26 | 2004 | [6 empty] | 28 31 51.58 N | 91 39 21.67 W | OFFSHORE |  | EUGENE ISLAND | 240 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275000 | 169918.5671 | 337352.4909 | 50000 | 25789.4737 | 225000 | 311563.0173 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 739547 | 2004-10-26 | 850 | 1250 | NO | YES | NO | NO | NO | NO | MARY S FRIEND, SENIOR ENGINEER PIPELINE SAFETY & SYSTEM INTE | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 24 | 0.44 | API 5LX 60 | 60000 | SEAMLESS |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1975 | NO | [57 empty] | LEAK DISCOVERED BY MMS DURING ROUTINE OFFSHORE FLIGHT ON 10/26/04. LEAK WAS CONFIRMED ON SAME DATE. REPAIRS WERE DELAYED DUE TO BOTH THE LACK OF QUALIFIED DIVERS AND BAD WEATHER. LEAK WAS DETERMINED TO BE AN INTERNAL, PIN HOLE LEAK, LOCATED AT APPROXIMATELY 6:00 POSITION, NEXT TO A SEAM. LEAK WAS REPAIRED WITH A 24" X 21.26" DASPIT SEA CLAMP. THE REPAIR WAS COVERED WITH SAND-CEMENT BAGS. REPAIR WAS COMPLETED ON 11/20/04.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040116 | 2004-12-07 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 |  | 2004-11-08 | 2004 | [6 empty] | 28 28 44.33N | 91 39 51.96W | OFFSHORE |  | EUGENE ISLAND | 264 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253000 | 154659.9971 | 260834.994 | 103000 | 53126.3158 | 150000 | 207708.6782 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 740748 | 2004-11-08 | 850 | 1250 | NO | YES | NO | NO | NO | NO | MARY S FRIEND, SENIOR ENGINEER PIPELINE SAFETY & SYSTEM INTE | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 20 | 0.44 | API 5LX-52 | 52000 | SEAMLESS |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1975 | NO | [57 empty] | LEAK DISCOVERED MY MMS DURING ROUTINE OFFSHORE FLIGHT ON 11/08/04. LEAK WAS CONFIRMED ON SAME DATE. REPAIRS WERE DELAYED DUE TO BOTH THE LACK OF AVAILABLE DIVERS AND BAD WEATHER. LEAK WAS DETERMINED TO BE AN INTERNAL PIN HOLE LEAK, LOCATED AT APPROXIMATELY 6:00 POSITION. LEAK WAS REPAIRED WITH A 20" X 21.25" DASPIT SEA CLAMP. THE REPAIR WAS COVERED WITH SAND-CEMENT BAGS. REPAIR WAS COMPLETED ON 11/22/04.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040117 | 2004-12-06 | ORIGINAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056-5306 | 136 | 2004-11-03 | 2004 | CYPRESS | HARRIS | TX | 77429 | VALVE SECTION 31 | 30+15 | 29 59'38.40N | 95 39'5.83W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 50 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 120099.8482 | 141912.3979 | 155400 | 80153.6842 | 44600 | 61758.7136 | 0 | 0 | NO | NO | NO | YES | 0 | PRECAUTIONARY | 0 | 44 | 740276 | 2004-11-03 | 856 | 875 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENGERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 24 | 0.28 | API 5LX | 52000 | DSAW | N/A | KAISER | 1951 | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | SITE PREPARATION - GRADING | NO |  |  |  |  | YES |  | YES | [38 empty] | EXAMINATION OF THE FAILED PIPE SHOWED NUMEROUS GOUGES, AT APPROXIMATELY THE 12 O'CLOCK POSITION ON THE PIPE, CONSISTENT WITH THIRD PARTY DAMAGE. FOREIGN METAL WAS ALSO FOUND IN BOTTOM OF THE GOUGES INDICATING CONTACT WITH A METALLIC OBJECT. THE CONDITION OF THE COATING IN THAT AREA SUPPORT THIS CONCLUSION. FAILURE OF THE PIPE RESULTED WHEN THE PRESSURE IN THE PIPE EXCEEDED THE PIPE'S PRESSURE HOLDING CAPACITY AT THE DAMAGED SECTION. THE CONCLUSION WAS THAT THIRD PARTY DAMAGE WAS THE CAUSE OF THE INCIDENT. EVACUATION WAS SUGGUESTED BY EMERGENCY OFFICIALS, BUT IT IS UNKNOWN HOW MANY PERSONS HEEDED THIS SUGGESTION. 3 OTHER PERSONS EVACUATED OF THEIR OWN VOLITION (WHEN ASKED, THEY CLAIMED THAT NO EMERGENCY OFFICIAL HAD MADE THE REQUEST).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040118 | 2004-12-10 17:42 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1115 | 2004-11-11 | 2004 | PRATTSVILLE | GRANT | AR | 72129 |  | 655+90 | 33.31857 | 92.55560 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198083 | 123325.4534 | 270742.5255 | 4083 | 2105.9684 | 194000 | 268636.5571 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 43 | 741096 | 2004-11-11 | 300 | 470 | YES | NO | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1920 | 14 | 0.25 |  | 35000 | ERW |  | UNKNOW |  | UNDER GROUND |  | 48 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | GALVANIC |  | YES | 1978 | NO | [57 empty] | COMPANY EMPLOYEES MAKING ROUTINE SURVEILLANCE OF PIPELINE AM-19 DISCOVER BUBBLES IN WATER ALONG HIGHWAY DITCH. THIS LOCATION WAS A ROAD CROSSING AND WAS MADE SECURE. PIPELINE WAS BLOWN DOWN AND PIPE REMOVE TO DETERMINE CAUSE OF LEAK. NEW PRETESTED PIPE WAS INSTALLED VIA A NEW ROAD BORE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040119 | 2004-12-10 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE -TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1245 | 2004-11-09 | 2004 | SAYREVILLE | MIDDLESEX | NJ | 08872 | 6.75 |  | 40.436(NORTH) | -74.347(WEST) | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 155203.3183 | 328454.8553 | 20400 | 10522.1053 | 229600 | 317932.7501 | 0 | 0 | NO | NO | NO | NO | 0 |  | 17 | 15 | 740888 | 2004-11-09 | 705 | 800 | NO | NO | NO | NO | YES | NO | JAMES MATHIS | 7132153792 | JAMES.G.MATHIS@WILLIAMS.COM | TRANSMISSION | OTHER | TAP CONNECTION | STEEL |  | NO | NO | NO | PIPELINE |  |  | 2 | 0.38 | API 5L | 52000 | DSAW | N/A |  | 1990 | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | HOT TAP |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 11 | 19 | 1990 | INERT GAS |  | 1 | 663 | [12 empty] | INVESTIGATION OF GAS ODOR AT SAYREVILLE TAP VALVE J-525 ON 11/09/04 REVEALED A DEFECT IN THE HOT-TAP NIPPLE (20") BRANCH ON A 42" LINE WHICH CAUSED GAS TO ESCAPE ALONG THE OUTER EDGE OF THE HOT TAP SPLIT SLEEVE. IN ORDER TO FIND THE LEAK, LEATECH WAS SPRAYED AROUND THE EDGES OF THE SPLIT SLEEVE. SMALL BUBBLES SHOWED GAS WAS LEAKING FROM THE OUTER EDGED OF THE SLEEVE. TRANSCO COORDINATED WITH CUSTOMER COMPANIES TO ISOLATE, AND THEN DRAW PRESSURE DOWN IN A 5-MILE SECTION OF 42 INCH MAIN LINE FROM A LINE PRESSURE OF 705 PSIG TO 190 PSIG. THE REMAINING PIPELINE PRESSURE WAS THEN BLOWN TO ATMOSPHERE AT THE 200C50 VALVE SITE BLOWOFF VALVE - B-2 ON 11/10/2004. THE 20 INCH HOT TAP AND 42-INCH PIPING IMMEDIATELY SURROUNDING THE HOT TAP WAS CUT OUT AND SENT AWAY FOR FURTHER ANALYSIS. A NEW, HYDROSTATICALLY TESTED SECTION OF 42 INCH PIPELINE WAS PUT INTO PLACE AD NON-DESTRUCTIVELY TESTED AT THE WELDS. THE 5-MILE SECTION OF 42 INCH PIPELINE WAS PURGED OF AIR, PACKED, AND PLACED INTO FULL SERVICE ON 11/12/2004. MATERIALS TO PERFORM A NEW 20 INCH TAP ARRIVED ON SITE 11/15/04. A NEW 20 INCH X 42 INCH HOT TAP CONNECTION WITH SUPPORT SADDLE WAS INSTALLED, AND THE HOT TAP NIPPLE WAS NON-DESTRUCTIVELY TESTED. A 20 INCH HOT TAP WAS PERFORMED ON THE NEW SECTION OF 42 INCH TRUCK PIPING, AND THE 20 INCH PIPELINE WAS RECONNECTED AT FLANGES. THE LATERAL PIPING WAS PURGED OF AIR, AND THE METER STATION RETURNED TO FULL SERVICE ON 11/17/04.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040120 | 2004-12-15 | SUPPLEMENTAL FINAL | 8040 |  | AMEREN IP | 500 SOUTH 27TH STREET | DECATUR | MACON | IL | 62521 | 634 | 2004-10-24 | 2004 | ARTHUR | DOUGLAS | IL | 61911 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | LEAK IS THE RESULT OF BEING STRUCK BY BORING EQUIP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95905 | 59727.4516 | 131604.6127 | 1378 | 710.7579 | 94527 | 130893.8548 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 20 | 739651 | 2004-10-27 | 655 | 857 | NO | NO | NO | NO | YES | NO | RONALD E KELLY, SENIOR GAS QUALITY ADMINSTRATOR | 2174246706 | RKELLY@AMEREN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 12 | 0.25 | API 5L | 42000 | ERW |  | REPUBLIC | 1960 | UNDER GROUND |  | 72 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 8 | 25 | 2004 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | EXCAVATION CONTRACTOR WAS INSTALLING A WATER LINE USING DIRECTIONAL BORING METHOD. BEGAN EXCAVATING ON AN EXPIRED ONE CALL (JULIE), MARKS WERE STILL EVIDENT, BUT DID NOT POTHOLE EXISTING UTILITIES BEFORE CROSSING. THE SUBSEQUET DAMAGE RESULTED IN A 3" LONG HAIRLINE CRACK TO A 12" DOT TRANSMISSION PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040121 | 2004-12-28 11:07 | ORIGINAL FINAL | 4900 |  | KINDER MORGAN TEJAS PIPELINE L.P. | 500 DALLAS STREET 1000 | HOUSTON | HARRIS | TX | 77002 | 2332 | 2004-12-20 | 2004 | PASADENA | HARRIS | TX | 77505 |  |  | 95 7 3 | 29 37 21 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 59398.4962 | 51578.9474 | 100000 | 51578.9474 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 55 | 744849 | 2004-12-20 | 844 | 844 | NO | NO | NO | NO | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | RELIEF VALVE | [9 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20040123 | 2006-01-13 08:48 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1200 | 2005-12-19 | 2005 | MILTONVALE | CLOUD | KS | 67466 | 28.3 | 1494+24 | 39.3511 | -97.5000 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800000 | 476342.1141 | 1027582.5974 | 50000 | 19780.8535 | 750000 | 1007801.7439 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 782926 | 2005-12-19 | 707 | 800 | NO | NO | NO | NO | YES | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 26 | 0.28 | 5LX | 52000 | FURNACE WELD |  | AO SMITH | 1951 | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | GIRTH WELD |  |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 7 | 7 | 1985 | WATER |  | 8 | 1012 | [12 empty] | AT 2:34 PM ON DECEMBER 19 A KINDER MORGAN EMPLOYEE CONTACTED NORTHERN NATURAL GAS EMPLOYEES TO REPORT BLOWING GAS SOUTH OF THE CLIFTON COMPRESSOR STATION. THE LEAK AREA WAS LOCATED AND THE VALVE SECTION WAS ISOLATED AND BLOWN DOWN. THE LEAK WAS CAUSED BY A CRACKED GIRTH WELD. THE WELD OPENED FROM ABOUT THE 9:00 O'CLOCK POSITION ACROSS THE TOP TO THE 3:00 O'CLOCK POSITION. METALLURGICAL ANALYSIS INDICATED THAT THE GIRTH WELD WAS OF POOR QUALITY AND MAY HAVE BEEN AGGRAVATED BY CORROSION. NORTHERN CONDUCTED METALLURGICAL ANALYSIS OF SOME UNDAMAGED WELDS, SMART PIGGED THE ENTIRE VALVE SECTION AND HYDROSTATICALLY TESTED THE ENTIRE VALVE SECTION PRIOR TO RETURNING THE PIPELINE TO SERVICE. THE COMPANY ALSO REINFORCED WELDS NEAR US HIGHWAY 24. OPS WAS UPDATED THROUGHOUT THE ENTIRE PROCESS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050001 | 2004-12-27 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 EAST GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 2135 | 2004-11-24 | 2004 | KILGORE | GREGG | TX | 75662 | MP 48.99 | 2587+19 | N32.42662 | W094.89946 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134264 | 80997.5948 | 106338.9747 | 91583 | 47237.5474 | 42681 | 59101.4273 | 0 | 0 | NO | NO | NO | YES | 200 | PRECAUTIONARY | 2 | 55 | 742398 | 2004-11-24 | 572 | 720 | YES | NO | NO | NO | NO | NO | JACK L ADAMS, MANAGER DOT | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 12 | 0.19 | API 5LX | 52000 | ERW | N/A | YOUNGSTOWN | 1966 | UNDER GROUND |  | 72 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1966 | NO | [57 empty] | ACTUAL CAUSE WILL BE DETERMINED BASED ON METALLURGICAL ANALYSIS. PIPE SENT TO METALLURGICAL LABORATORY NOVEMBER 30, 2004 AND FINAL REPORT IS EXPECTED TO BE DELIVERED THE WEEK OF DECEMBER 21, 2004. TIME OF INCIDENT IS THE TIME THAT GULF SOUTH RECEIVED FIRST INDICATION, A ROD LOAD ALARM ON LONGVIEW COMPRESSOR STATION #2 UNITS 2 AND 3 WHICH WERE RUNNING AT THE TIME. OPERATOR WAS WORKING ON UNIT 1 AND WAS ATTEMPTING TO PUT INTO SERVICE WHEN ALARM ACTIVATED. OPERATOR OBSERVED THAT SUCTION PRESSURE ON INDEX 8 AT 240 PSIG AT APPROXIMATELY 9:35 PM AND NOTIFIED GAS CONTROL. GAS CONTROLLER DISPATCHED FIRST RESPONDERS AT 9:40 PM. THE LOW ALARM ON THE SCADA, SET AT 170 PSIG ACTIVATED AT 9:45PM. A REVIEW OF THE PRESSURE DATA INDICATES THAT THE ACTUAL RUPTURE PROBABLY OCCURRED BETWEEN 8:53PM AND 8:58PM. THE ELAPSED TIME UNTIL AREA WAS MADE SAFE IS BASED ON THE TIME THAT THE PRODUCTION THAT FEEDS INTO THE LINE WAS SHUT IN AND ALL ISOLATING VALVES WERE CLOSED. THE NEAREST DWELLING WAS APPROXIMATELY 2,000 FEET FROM THE RUPTURE SITE. THEREFORE, THE AREA WAS ACTUALLY SAFE ONCE THE SITE HAD BEEN SECURED UPON ARRIVAL BY THE FIRST RESPONDERS. 1-24-05 METALURGICAL ANALYSIS OF THE FAILED SECTION OF PIPE DETERMINED THAT THE RUPTURE WAS CAUSED BY PITTING CORROSION ON THE INSIDE OF THE PIPE ALONG THE BOTTOM OF THE PIPELINE, WHERE THE SEAM WELD WAS LOCATED. THE APPEARANCE OF THE CORROSION INDICATED IT WAS MOST LIKELY DUE TO MICROBIOLOGICALLY INDUCED CORROSION (MIC) AND THERE WAS NO INDICATION THAT THE FAILURE INITIATED IN THE WELD, BUT THE PROPERTIES OF THE WELD PROBABLY ACCOUNT FOR FRACTURE PROPAGATION BEYOND THE PITTED AREA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050003 | 2005-01-06 | SUPPLEMENTAL FINAL | 19580 |  | TRANSCOLORADO PIPELINE COMPANY | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228 | 400 | 2004-12-12 | 2004 | WHITEWATER | MESA | CO |  |  |  | 38 59 35 | 108 23 21 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FIRE IN CONTROL BUILDING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 155799.2433 | 346181.1303 | 0 | 0 | 250000 | 346181.1303 | 0 | 0 | NO | NO | YES | NO | 0 |  | 1 | 0 | 744026 | 2004-12-12 | 950 | 1287 | NO | YES | NO | NO | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | OTHER | COMPRESSOR/TURBINE |  |  | NO | NO | NO | COMPRESSOR |  | 2004 | [8 empty] | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | COMPRESSOR UNLOADER SHAFT | [10 empty] | DURING NORMAL OPEATIONS A COMPRESSOR UNLOADER FAILED AND ALLOWED GAS TO MIGRATE BACK THROUGH A PNEUMATIC CONTROL LINE INTO THE AIR DRYER LOCATED IN THE CONTROL BUILDING. THE AIR DRYER VENTED INTO THE CONTROL BUILDING AND THE GAS WAS IGNITED DAMAGING THE STRUCTURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050004 | 2005-01-07 | SUPPLEMENTAL | 30984 |  | CITY OF BRYAN DBA BRYAN TEXAS UTILITIES | PO BOX 1000 | BRYAN | BRAZOS | TX | 77805 | 1200 | 2004-10-15 | 2004 | BRYAN | BRAZOS | TX | 77805 |  |  | 30.6436214 | -96.3890457 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33000 | 20331.804 | 38744.4288 | 8000 | 4126.3158 | 25000 | 34618.113 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 750 | 915 | NO | YES | NO | NO | NO | NO | MARK BECKMANN, PLANT MANAGER | 9798215945 | MBECKMANN@BTUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1993 | 8 | 0.32 | API 5L/API 5LN | 42000 | SEAMLESS | N/A |  |  | OPEN DITCH |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 10 | 5 |  |  | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | PIPELINE WAS ALREADY UNCOVERED AT THE TIME OF THE INCIDENT. TRENCH SHORING WAS BEING REMOVED WHEN THE SHORING WAS ALLOWED TO COME INTO CONTACT WITH PIPELINE. THE CONTACT CAUSED A GOUGE APPROX 1 1/2" LONG AND 1/16" DEEP. GOUGE WAS DETERMINED TO EXCEED LIMITS SET FORTH BY DOT. THE DAMAGED SECTION OF PIPE WAS REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050005 | 2005-01-14 15:22 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVENUE | CHARLESTON | KANAWHA | WV | 25314 | 924 | 2004-12-18 | 2004 | URBANA | CHAMPAIGN | OH | 43078 | N/A | 0+00 | 40.1970 | -83.7694 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK FROM A CIRCUMFERENTIAL CRACK IN A VALVE BODY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60465 | 37068.1528 | 65479.7322 | 21000 | 10831.5789 | 39465 | 54648.1532 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 744773 | 2004-12-20 | 205 | 225 | NO | NO | YES | NO | NO | NO | STEVEN P. BURNLEY | 6077210112 | SBURNLEY@NISOURCE.COM | TRANSMISSION | COMPONENT |  | OTHER | CAST IRON | NO | NO | NO | PIPELINE |  | 1956 | 6 |  | UNKNOWN |  |  | BALL, FLANGED | ORBIT VAVLE | 1956 | UNDER GROUND |  | 43 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | YES | 10 | 10 | 1957 | WATER |  | 24 | 700 | [12 empty] | A CRACK FORMED BETWEEN THE BALL VALVE¿S BODY AND ONE OF ITS FLANGES. THE CRACK WAS APPROXIMATELY 12 INCHES LONG AS MEASURED CIRCUMFERENTIALLY. THE FAILED VALVE IS BEING SENT TO AN INDEPENDENT LAB FOR CRACK MORPHOLOGY AND ANALYSIS. BECAUSE THE PIPELINE WAS A SOLE MARKET FEED, THE VALVE COULD NOT BE READILY ISOLATED. THIS RESULTED IN BLOWING GAS BEING MANAGED WHILE A STOPPLED BYPASS COULD BE FABRICATED, THUS RESULTING IN COSTS EXCEEDING $50K. SYNOPSIS OF MARCH 21, 2005, EDISON WELDING INSTITUTE REPORT EWI PROJECT NO. 48804CSP: THE LIKELY CAUSE OF FAILURE WAS CRACK INITIATION FROM A VOID TYPE CASTING DEFECT. STRESS IMPARTED FROM THE CONNECTED PIPING CONTRIBUTED TO SUBSEQUENT CRACK GROWTH. THE CRACK PROPAGATED FROM THE OUTSIDE SURFACE OF THE BALL VALVE AS EVIDENT BY THE INCREASED CORROSION PRODUCTS FOUND ACROSS THE FRACTURE SURFACE. MICROSTRUCTURE LIKELY PLAYED A ROLE IN THE CRACK PROPAGATION TOO. THE PRESENCE OF GRAPHITE FLAKES WITHIN THE MATRIX IS INDICATIVE OF A WEAKER MICROSTRUCTURE. SEM EXAMINATION OF THE FRACTURE SURFACE INDICATED BRITTLE-LIKE PROPAGATION OF THE CRACK. THE CHEMICAL ANALYSIS CONFIRMS THAT THE MATERIAL IS A CAST IRON, WITH A CARBON COMPOSITION OF 3 PERCENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050006 | 2005-01-14 | SUPPLEMENTAL FINAL | 117 |  | AIR PRODUCTS LP | 1002 STRANG ROAD | LAPORTE | HARRIS | TX | 77571 | 815 | 2004-12-14 | 2004 | WALLISVILLE | CHAMBERS | TX | 77597 |  |  | 29.83595 | -94.76383 | ONSHORE | 2 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 155653.1833 | 341836.4551 | 5000 | 2578.9474 | 245000 | 339257.5077 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 45 | 744246 | 2004-12-14 | 780 | 860 | NO | YES | NO | NO | NO | NO | KERRY J SERNER, GLOBAL OPERATIONS/PIPELINE MAINT | 6104818422 | STERNEKJ@APCI.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1940 | 8 | 0.32 | ASTM Gr. B | 35000 | SEAMLESS | N/A | UNKNOWN |  | UNDER WATER |  | 360 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | STRESS CRACK | [6 empty] | FITTING | [5 empty] | NO | YES | 12 | 12 | 1996 | WATER |  | 8 | 1210 | [12 empty] | INVESTIGATION/INSPECTION HAS CONFIRMED THAT A STRESS CRACK HAD DEVELOPED ADJACENT TO A FILLET WELD AT THE LOCATION OF AN APPLIED SPLIT/COUPLING. THE MAGNITUDE OF THE CRACK WAS 2 1/8" IN LENGTH ON THE CIRCUMFERENCE OF THE 8" X .325 WALL PIPE AND PENETRATED THREW THE WALL TO THE INSIDE OF THE PIPE. THIS PIPE WAS INSTALLED ON THE RIVER BOTTOM WITH LESS THAN 2-'0" OF COVER IN CIRCA 1940. WE HAVE NO HISTORY AS TO WHY THIS COUPLING WAS INSTALLED OTHER THAN THE MATING PIPE SEGMENTS WHERE NOT OF THE SAME WALL THICKNESS IE- .325 TO 340. WALL. IT IS SUSPECTED THAT CURRENT FLOW OF THE TRINITY RIVER AND POSSIBLY BUOYANCY DUE TO LOSS OF COVER CONTRIBUTED TO THE STRESSING OF THIS PIPE AS NO EXTERIOR DAMAGE WAS FOUND ON THE PIPE OR COUPLING, NOR WAS ANY CORROSION OF ANY TYPE PRESENT. 1,100 FEET OF THIS PIPELINE WAS REPLACED WITH API5L-X42, .406 WALL BY DIRECTIONAL DRILL AT A DEPTH OF 20'0" UNDER THE RIVER BOTTOM PER REQUIREMENTS SET FORTH BY THE CORP OF ARMY ENGINEERS. THE METALLURIGICAL REPORT IS ATTACHED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050007 | 2005-01-24 | ORIGINAL | 22435 |  | WEST TEXAS GAS INC | 211 NORTH COLORADO | MIDLAND | MIDLAND | TX | 79701 | 530 | 2004-12-16 | 2004 | TRICKHAM | COLEMAN | TX |  |  |  | N31 34.21 | W99 13.05 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 40 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15494 | 9337.6367 | 11990.4812 | 10892 | 5617.9789 | 4602 | 6372.5022 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 |  |  | 200 | 265 | NO | NO | NO | NO | YES | NO | RICHARD D HATCHETT, VICE PRESIDENT | 4326824349 | RHATCHETT@WESTTEXASGAS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 5.5 | 0.16 | UNKNOWN | 1005 | ERW |  | UNKNOWN |  | UNDER GROUND |  | 30 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE |  |  |  |  | YES | 1998 | NO
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050008 | 2005-01-25 14:47 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1100 | 2004-12-26 | 2004 | PICAYUNE | HANCOCK | MS | 39466 | 1.81 | 95+86 | 89.65794 | 30.4476 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70500 | 43029.8143 | 70686.0923 | 31000 | 15989.4737 | 39500 | 54696.6186 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 745346 | 2004-12-26 | 450 | 607 | NO | NO | NO | NO | YES | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 4.5 | 0.24 | UNKNOWN | 24000 | UNKNOWN | N/A | UNKNOWN | 1946 | OTHER | PIPE EXPOSED BY OFFROAD VEHICLE ACTIVITY |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | GAS CONTROL OBSERVED LOSS OF PRESSURE ON INDEX 300-43 AT 19:06 HOURS 12/25/2004 AND DISPATCHED TWO RESPONDERS TO INVESTIGATE. RESPONDERS SYSTEMATICALLY VISITED POINTS ON PIPELINE UNTIL SEGMENT OF PIPELINE IDENTIFIED. ARRIVED AT LEAK LOCATION AT 21:06 HOURS. LOCATION WAS APPROXIMATELY ¼ MILE FROM HWY 607 IN THE NASA BUFFER ZONE. THE LEAK RESULTED FROM A CIRCUMFERENTIAL CRACK IN THE PIPE CAUSED BY OFFROAD VEHICLES TRAVERSING THE RIGHTS-OF-WAY OVER THE PIPELINE, EXPOSING AND DENTING THE PIPELINE. SINCE LOCATION DID NOT POSE A HAZARD TO PEOPLE OR PROPERTY AND THIS PIPELINE WAS THE SOLE FEED TO PICAYUNE, MS, THE PIPELINE WAS LEFT IN SERVICE WHTH SECURITY BEING PROVIDED BY COMPANY PERSONNEL. THE INITIAL REPAIR DECISION WAS TO INSTALL A SPLIT SLEEVE ON THE PIPE WHICH WOULD BE COMPLETED WITHOUT MEETING THE REPORTABLE INCIDENT THRESHOLD. AROUND 10:00 HOURS 12/26/2004, THE DECISION WAS MADE TO REPAIR THE LEAK BY PIPE REPLACEMENT DUE TO SAFETY CONCERNS FOR COMPANY REPAIR CREW THAT AROSE DURING THE EARLY STAGES OF THE SPLIT SLEEVE REPAIR. THE PIPE REPLACEMENT REPAIR METHOD CAUSED THE REPAIR COST TO EXCEED THE REPORTING THRESHOLD. THEREFORE, THE INCIDENT WAS REPORTED TO THE NRC AT 11:15 HOURS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050009 | 2005-01-28 | ORIGINAL | 2714 |  | DOMINION TANSMISSION, INC. | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302 | 735 | 2005-01-02 | 2005 | VIENNA | WOOD | WV | 26105 | 605 GATE JUNCTION | 29+19 | N39.213 | W81.318 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81000 | 36903.1142 | 32044.9827 | 81000 | 32044.9827 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 28 | 745960 | 2005-01-01 | 238 | 500 | NO | YES | NO | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C_SCHWOEBLE@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 8.63 | 250 | GRADE B | 35000 | ERW | N/A | REPUBLIC STEEL, YOUNGSTOWN OHIO |  | UNDER GROUND |  | 84 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | BODY OF PIPE | [10 empty] | MATERIAL DEFECT |  | NO | YES | 8 | 24 | 1973 | WATER |  | 8 | 1340 | [12 empty] | DOMINION TRANSMISSION INC'S. TL-409 CROSSES UNDER THE CSX RAILROAD TRACKS WHERE THIS INCIDENT OCCURRED. IT WAS DETERMNINED THAT DUE TO SATURATED SOIL (RECENT HEAVY RAINS), SETTLING OF RAILROAD TRACKS, WEIGHT AND VIBRATION OF TRAIN TRAFFIC (OVER TIME), UNDO STRESS FROM EARTH MOVEMENT CONTRIBUTED AND RESULTED IN THE PIPELINE LEAKING. THERE WAS NO MATERIAL DEFECT BUT MARTY HAD TO ENTER A "FIELD" IN SECTION "A." OF "F-5" OF THIS INCIDENT FORM OR IT COULD NOT BE SUBMITTED. FORM SHOULD BE REVISED TO INCLUDE "OTHER".
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050010 | 2005-02-04 17:08 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1700 | 2005-01-06 | 2005 | MARION | CRITTENDEN | AR | 72364 | JM-24 TAKEOFF | 1125+69 | 35.2077 | 90.198908 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60210 | 36380.6679 | 80707.2191 | 210 | 83.0796 | 60000 | 80624.1395 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 746376 | 2005-01-06 | 585 | 680 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | GATE VALVE | STEEL |  | NO | NO | NO | OTHER | TAKE-OFF POINT BETWEEN TWO PIPELINES | 1954 | [8 empty] | UNDER GROUND |  | 36 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ON MAY 27 THE SUSPECTED MALFUNCTONED GATE VALVE WAS REMOVED AND DIASSEMBLED. IT WAS DETERMINED THAT THE STEM PIN HAD SHEARED AND WAS IN THE BODY OF THE GATE VALVE NOT ALLLOWING IT TO BE OPENED. HOWEVER THE STEM AND HANDLE WOULD ROTATE WHICH CAUSED THE OPERATOR THINK IT WAS IN THE OPEN POSITION. |  | ON JANUARY 26, AT ABOUT 10:00 A FIELD O&M TECHNICIAN WAS PERFORMING A TEST AT THE JM-24 TAKE-OFF POINT FROM LINE JM-23. THE TECHNICIAN OPERATED VALVE #3 (V3), BY PLACING A VALVE HANDLE EXTENSION ON THE BELOW GROUND VALVE. AFTER CLOSING THE VALVE THE TECHNICIAN THEN OPENED THE VALVE AND NOTED THAT THE VALVE STEM EXTENSION HANDLE SHOWED TO BE IN THE OPEN POSITION. LATER THAT DAY A DISTRIBUTION COMPANY NOTIFIED THE TECHNICIAN THAT LINE JM-24 WAS LOSING PRESSURE. THE TECHNICIAN RETURNED TO THE JM-24 TAKE-OFF AND CALLED OTHER COMPANY EMPLOYEES FOR HELP. AT ABOUT 1650 HOURS IT WAS DETERMINED THAT ALL PRESSURE WAS LOST ON THE JM-24 LINE. COMPANY PERSONNEL THEN RESPONSED TO PURGE AND RELOAD THE PIPELINE VIA A DIFFERENCE VALVE CONFIGURATION AT THE JM-24 TAKE-OFF POINT. THIS INCIDENT WAS REPORTED TO THE NRC AS IT WAS DEEMED TO BE A SIGNIFICANT EVENT IN THE JUDGEMENT OF THIS OPERATOR, AS IT AFFECT SEVERAL TOWN BORDERS ALONG THE JM-24 PIPELINE. THE SUSPECTED GATE VALVE WILL BE TAKEN OUT OF SERVICE AND EXAMINED DURING THE WARMER MONTHS FOR A FINAL CAUSED DETERMINATON. ON MAY 27 THE SUSPECTED MALFUNCTONED GATE VALVE WAS REMOVED AND DIASSEMBLED. IT WAS DETERMINED THAT THE STEM PIN HAD SHEARED AND WAS IN THE BODY OF THE GATE VALVE NOT ALLLOWING IT TO BE OPENED. HOWEVER THE STEM AND HANDLE WOULD ROTATE WHICH CAUSED THE OPERATOR THINK IT WAS IN THE OPEN POSITION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050011 | 2005-02-07 13:49 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1045 | 2005-01-09 | 2005 | VICKSBURG | WARREN | MS | 39181 | MP 1.91 | 101+35 | 32.28445 | 90.91050 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66700 | 39635.7847 | 85171.0111 | 4700 | 1859.4002 | 62000 | 83311.6108 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 13 | 746585 | 2005-01-09 | 325 | 1214 | YES | NO | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 20 | 0.28 | API5LX | 60000 | SUBMERGED ARC WELD | NA | KAISER | 1966 | UNDER GROUND |  | 168 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | AT 1807 HOURS JANUARY 8, 2005 GAS CONTROL RECEIVED A CALL FROM A PROPERTY OWNER REPORTING LEAK AND SMELL OF GAS IN AREA WHERE PIPELINES CROSS HIS PROPERTY. GULF SOUTH¿S PIPELINE AND A PIPELINE OPERATED BY CROSS TEX TRAVERSE HIS PROPERTY. FIELD OPERATIONS PERSONNEL CALLED PROPERTY OWNER AND PERSON THAT REPORTED THE SMELL OF GAS TO THE PROPERTY OWNER AND DETERMINED THAT OUR PIPELINE MIGHT BE LEAKING. GULF SOUTH DISPATCHED PERSONNEL TO INVESTIGATE REPORT. AFTER ARRIVING AT SITE, IT WAS DETERMINED THAT THE LEAK WAS ON GULFSOUTH¿S LINE. THE NEAREST HOUSE WAS OUTSIDE OF 660 FEET CORRIDOR AND DID NOT REQUIRE IIMMEDIATE ACTION (GRADE 2 LEAK SCHEDULED REPAIR). THEREFORE, THE DECISION WAS MADE THAT LEAK WOULD BE ADDRESSED NEXT MORNING. THE SITE WAS SECURED BY INSTALLING WARNING TAPE AROUND THE LEAK AREA AT 2120 HOURS. AT 1045 HOURS JANUARY 9, 2005 AFTER FURTHER INVESTIGATION OF SITE AND EVALUATION OF POTENTIAL REPAIR COSTS, A DETERMINATION WAS MADE THAT THE REPAIR COST OF THE LEAK WOULD MEET OR EXCEED THE THRESHOLD FOR REPORTING AS AN INCIDENT. THEREFORE, THE INCIDENT REPORT WAS MADE AT 1120 HOURS JANUARY 9, 2005. 2009-06-23 SOIL AT ROAD AND PIPELINE AREA HAS BEEN STABILIZED BY MDOT. GULF SOUTH IS NOW IN THE PROCESS TO REPLACE THE PIPE. 2010-04-02 GULF SOUTH HAS DECIDED NOT TO REPLACE THE LINE BECAUSE VOLUME NOT NEEDED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050012 | 2005-02-01 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 1556 | 2004-10-01 | 2004 | METTLER | KERN | CA |  | 1543 |  | N 35 03.497' | W119 07.072' | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 48 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66000 | 39670.3997 | 47945.066 | 50000 | 25789.4737 | 16000 | 22155.5923 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 746359 | 2005-01-06 | 360 | 390 | NO | NO | YES | NO | NO | NO | W JEFF KOSKIE, SAFETY SYSTEMS ADVISOR | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM |  |  |  |  | NO | NO | NO | PIPELINE |  | 1920 | 12 | 0.25 | N/A | 42000 |  |  | N/A | 1920 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | RIPPING-FARMER | YES | 6 | 4 | 2004 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | [37 empty] | ON OCTOBER 1, 2004 AT 12" HIGH PRESSURE MAIN OPERATING AT APPROXIMATELY 360 POUNDS PRESSURE FAILED AS A RESULT OF BEING STRUCK BY A RIPPER ONE OR TWO DAYS EARILER. SOUTHERN CALIFORNIA GAS WAS UNAWARE OF THE RIPPER DAMAGE UNTIL THE PIPELINE FAILED, OPENING A SECTION LONGITUDINALLY FOR APPROXIMATELY 48". THE INVOLVED SECTION OF PIPING WAS ISOLATED AND BLOWN DOWN. REPAIRS CONSISTED OF REMOVING AND REPLACING THE DAMAGED SECTION OF PIPING. INITIAL ESTIMATES OF GAS LOSS AND REPAIRS DID NOT EXCEED $50,000 AND AS A RESULT THIS INCIDENT WAS NOT REPORTED TO THE DEPARTMENT OF TRANSPORTATION OR THE CALIFORNIA PUBLIC UTILITIES COMMISSION. INVESTIGATION OF THE INCIDENT SHOWED THAT THE EXCAVATOR WAS AWARE OF THE PIPING, AND THAT IT WAS PROPERLY MARKED. NO FIRE, INJURIES, OR MAJOR MEDIA RESULTED FROM THIS INCIDENT. ON JANUARY 6, 2005, DURING RECONCILIATION OF INCIDENT COSTS, AN ERROR WAS DISCOVERED IN THE GAS LOST CALCULATION. CORRECTION OF THIS CALCULATION RESULTED IN THE TOTAL COST RELATED TO THIS INCIDENT EXCEEDING $50,000 AND AS A RESULT THE INCIDENT WAS REPORTED IMMEDIATELY TO DEPARTMENT OF TRANSPORATION AND CALIFORNIA PUBLIC UTILITIES COMMISSION. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050013 | 2005-02-01 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 342 | 2004-12-09 | 2004 | METTLER | KERN | CA |  | 15.43 |  | N 35 03.498' | W 119 .07.080' | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 60 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 47956.9772 | 54297.1836 | 65000 | 33526.3158 | 15000 | 20770.8678 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 40 | 746361 | 2005-01-06 | 360 | 390 | NO | NO | YES | NO | NO | NO | W JEFF KOSKIE, SAFETY SYSTEMS ADVISOR | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1920 | 12 | 0.25 | N/A | 42000 |  |  | N/A | 1920 | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | OTHER | RIPPING-FARMER | YES | 6 | 4 | 2004 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | ON DECEMBER 9, 2004 AT 12" HIGH PRESSURE MAIN OPERATING AT APPROXIMATELY 360 POUNDS PRESSURE FAILED AS A RESULT OF BEING STRUCK BY A RIPPER APPROXIMATELY TWO MONTHS EARLIER. SOUTHERN CALIFORNIA GAS WAS UNAWARE OF THE RIPPER DAMAGE UNTIL THE PIPELINE FAILED, OPENING A SELECTION LONGITUDINALLY FOR APPROXIMATELY 60". THE INVOLVED SECTION OF PIPING WAS ISOLATED AND BLOWN DOWN. REPAIRS CONSISTED OF REMOVING AND REPLACING THE DAMAGED SECTION OF PIPING. INITIAL ESTIMATES OF GAS LOST AND REPAIRS DID NOT EXCEED $50,000 AND AS A RESULT THIS INCIDENT WAS NOT REPORTED TO THE DEPARTMENT OF TRANSPORTATION OR THE CALIFORNIA PUBLIC UTILITIES COMMISSION. INVESTIGATION OF THE INCIDENT SHOWED THAT THE EXCAVATOR WAS AWARE OF THE PIPING, AND THAT IT WAS PROPERLY MARKED. NO FIRE, INJURIES, OR MAJOR MEDIA RESULTED FROM THIS INCIDENT. ON JANUARY 6, 2005 DURING RECONCILIATION OF INCIDENT COSTS, AN ERROR WAS DISCOVERED IN THE GAS LOST CALCULATION. (THIS CALCULATION ERROR WAS CARRIED OVER FROM NRC INCIDENT #74639 WHICH INVOLVED THE SAME PIPING WITH SIMILAR GAS BLOWN DURATION). CORRECTION OF THIS CALCULATION RESULTED IN THE TOTAL COST RELATED TO THIS INCIDENT EXCEEDING $50,000, AND AS A RESULT THE INCIDENT WAS REPORTED IMMEDIATELY TO DEPARTMENT OF TRANSPORTATION AND CALIFORNIA PUBLIC UTILITIES COMMISSION. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050014 | 2005-02-07 | ORIGINAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1330 | 2005-01-22 | 2005 | ULYSSES | GRANT | KS | 67870 | 0 | 0+45 | 37.5563180343 | -101.1298116346 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BULLPLUG ON PIG LAUNCHER GATE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109964 | 50179.6322 | 44016.5677 | 109423 | 43289.6067 | 541 | 726.961 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 747945 | 2005-01-22 | 775 | 899 | NO | NO | YES | NO | NO | NO | DAVID SINCLAIR, SR PIPELINE SAFETY SPEC | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | OTHER | VALVE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1968 | [6 empty] | M&J VALVE CO | 1968 | UNDER GROUND |  | 24 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | VALVE THREADS | [9 empty] | GAS WAS FOUND LEAKING PAST 3/8" VENT BULL PLUG IN BODY OF VALVE. REPAIR OF BUILDING REQUIRED BLOWING DOWN APPROXIMATELY 20 MILES OF PIPE THUS CONSTITUTING A DOT REPORTABLE INCIDENT. INCIDENT WAS NEVER A HAZARD TO THE PUBLIC OR OPERATIONS PERSONNEL. REPAIR WAS MADE IN 13 HOURS WITH NO INTERRUPTION OF SERVICE, NO EVACUATIONS, AND NO NEED OF RESPONSE BY EMERGENCY PERSONNEL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050015 | 2005-02-01 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 1000 | 2004-12-25 | 2004 |  | TERREBONNE | LA |  | 6.8087(MP) TEXAS GAS VALV | NA | 29-12'-188 N | 90- 52'-217 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 984000 | 612407.8854 | 1338238.7475 | 28000 | 14442.1053 | 956000 | 1323796.6422 | 0 | 0 | NO | YES | NO | NO | 0 |  | 2 | 0 | 745282 | 2004-12-25 | 936 | 1440 | YES | NO | NO | NO | NO | NO | BRETT K KIGHT, SENIOR ENGINEER, PIPELINE SAFETY & INTEGRITY | 2706886372 | BRETT.K.KIGHT@TXGT.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 8 | 0.38 | API 5LX | 42000 | SEAMLESS WELD | NA | YOUNGSTOWN SHEET AND TUBE COMPANY | 1963 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | NATURAL | [35 empty] | ON THE EVENING OF DECEMBER 24, 2004 AT 10:30 PM (CST) TEXAS GAS' GAS CONTROL DEPT RECEIVED NOTIFICATION FROM A GAUGER. MR. GENE GILES [PHONE NO (985)232-9830], WITH HILCORP ENGINEERING THAT OUR TEXACO-DOG LAKE (METER NO 9836) FACILITIES WERE ON FIRE. THIS METER FACILITY IS ON A SMALL CONCRETE PLATFORM IN THE LOUISIANA MARSH. HILCORP ENGINEERING OPERATES PRODUCTION IN THE DOG LAKE AREA. TEXAS GAS WAS RECEIVING APPROXIMATELY 17 MMCF/D RATE AT THE TIME OF THE INCIDENT. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER BY 12:30 A.M. (CST) DECEMBER 25TH. AFTER THE INITIAL CALL FROM MR. GILES, GAS CONTROL IMMEDIATELY NOTIFIED THE YOUNGSVILLE-MORGAN CITY DISTRICT ONE-CALL PERSON WHO MOBILIZED WITH THREE EMPLOYEES FROM THE MORGAN CITY DISTRICT WHO ARRIVED BY CONTRACTED CREW BOAT AT THE AREA OF THE PLATFORM BY 1:30 A.M. AND FOUND THAT OUR PLATFORM WAS NOT ON FIRE, BUT PIPING 10- TO 15- FEET FROM THE PLATFORM WAS. THEY PROCEEDED TO ISOLATE THE TEXAS GAS PIPING DOWNSTREAM OF THE AFFECTED FACILITIES. HILCORP THEN SHUT IN THEIR PRODUCTION AND THERE WERE NO ACTIVE METERS UPSTREAM. SINCE TRANSCO HAS AN "INACTIVE" RISER AND SIDE VALVE INTERCONNECT (NO 8122) ON THE PLATFORM, WE NOTIFIED THEIR GAS CONTROL DEPT PROMPTLY. AFTER OUR PIPELINE WAS ISOLATED, THE FIRE CONTINUED AT THE SAME RATE. OUR EMPLOYEES REPORTED THAT THE FIRE APPEARED TO BE ORIGINATING FROM THE TRANSCO PIPELINE AREA. WE REPORTED THIS TO TRANSCO WHO THEN BEGAN MOBILIZING THEIR EMPLOYEES WHO ARRIVED ONSITE THE MORNING OF DECEMBER 25. THEY ISOLATED BOTH THEIR 6-INCH GAS PIPELINE AND A 3-INCH LIQUIDS PIPELINE WITH NO IMPACT TO THE FLAME. AT APPROXIMATELY 10:00 A.M. DECEMBER 25, AS REPORTED TO US BY A HILCORP ENGINEERING REPRESENTATIVE, THE FLAME GREATLY INTENSIFIED. TEXAS GAS BELIEVES THAT THIS GREATLY INTENSIFIED FLAME INDICATES THE RUPTURE OF OUR CBD 8" PIPELINE IN THE RISER LEAVING THE PLATFORM, DUE TO THE HEAT FROM THE FIRE. AT ABOUT THIS TIME, 10:00 A.M. DECEMBER 25, 2004, HILCORP ENGINEERING BEGAN MANUALLY SHUTTING-IN THEIR PRODUCTION LINES. THE FIRE DIMINISHED AND SUBSIDED OVER THE NEXT 2 TO 3 HOURS. WE HAD NO EMPLOYEES AT THE SITE WHEN THIS EVENT OCCURRED AS WE WERE IN THE PROCESS OF CHANGING CREWS AND REFUELING THE BOAT. THIS INFORMATIONS WAS RELAYED FROM THE HILCORP CREW BOAT THAT WAS ALSO MONITORING THE SITUATION. TEXAS GAS BELIEVES THAT THE INITIAL FIRE WAS CAUSED BY THE FAILURE AND IGNITION OF A PRODUCTION LINE OWNED BY HILCORP ENGINEERING. THE HEAT FORM THIS INITIAL FIRE CAUSED TEXAS GAS' CBD 8" PIPELINE TO RUPTURE. HILCORP REIMBURSED TEXAS GAS FOR THE MAJORITY OF THE LOSS. TEXAS GAS REPAIRED THE FACILITY ON PROJECT 46867.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050016 | 2004-11-02 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1430 | 2004-08-28 | 2004 | [6 empty] | N 28 7.669' | W 96 39.872' | OFFSHORE |  | MATAGRODA | 629 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 56087.7276 | 124625.2069 | 0 | 0 | 90000 | 124625.2069 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 |  |  | 450 | 1280 | NO | YES | NO | NO | NO | NO | ROBERT PENNINGTON, SR PROD ENGR | 7138401980 | PENNINGTON@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 10.7 | 0.28 | NA |  | NA | NA | NA |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1977 | NO | [57 empty] | SLEEVE CLAMP INSTALLED & RISER REPAIRED, PINHOLES FROM CORROSION WHERE CAUSE. REPORT BEING FINALIZED ON 07/12/07 WITH AMENDMENT OF THE DATE OF OCCURRANCE TO 08/28/2004 (INITIALLY REPORTED AS 09/28/07) WITH SELECT MISSING ITEMS AMENDED. NO CHANGE IN COST.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050017 | 2005-02-14 | SUPPLEMENTAL FINAL | 12408 |  | DTE ENERGY - MICHIGAN CONSOLIDATED GAS CO | 2000 SECOND AVENUE | DETROIT | WAYNE | MI | 48226 | 2339 | 2005-01-21 | 2005 | NEW HAVEN | GRATIOT | MI | 48889 |  |  | 43.23 | -84.73 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | BROKEN VALVE BODY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 22779.7001 | 19780.8535 | 50000 | 19780.8535 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 747907 | 2005-01-22 | 625 | 970 | NO | YES | NO | NO | NO | NO | LARRY K CROWDER, INVESTIGATOR | 3132359403 | CROWDERL@DTEENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 30 | 0.41 | UNKNOWN | 52000 |  |  |  |  | UNDER GROUND |  | 50 | NATURAL FORCES | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [14 empty] | FROSTHEAVE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050018 | 2005-02-17 17:37 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1925 | 2005-01-18 | 2005 | CAMERON | LE FLORE | OK | 74932 |  | 0+00 | 35.12971 | -94.54257 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | MECHANICAL - EQUIPMENT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105155 | 50014.8142 | 54993.2881 | 91030 | 36013.0219 | 14125 | 18980.2662 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 50 | 747570 | 2005-01-18 | 750 | 1000 | NO | NO | NO | NO | YES | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | GATE VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 4 | 0.16 | GR | 35000 | ERW | GATE VALVE | WKM |  | OTHER | BELLHOLE | 42 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | VALVE THREADS | [9 empty] | ON JANUARY 18, ON LINE OT-19 TIE IN TO LINE O, COMPANY EMPLOYEES HAD SHUT A GATE VALVE ON OT-19 AND BLOWN THE LINE DOWN. THE EMPLOYEES WORKED AT THE END OF LINE OT-19, DOWNSTREAM OF THE VALVE, DURING THE DAY. AFTER COMPLETING THE WORK AT THE END OF THE LINE, THE EMPLOYEES RETURNED TO THE GATE VALVE LOCATION AND WERE IN THE PROCESS OF REMOVING THE CLAPPER FROM A CHECK VALVE THAT WAS LOCATED FIVE FEET DOWN STREAM OF THE GATE VALVE. AN EMPLOYEE HAD LOOSENED SIX OF THE EIGHT BOLTS AND REMOVED TWO OF THE BOLTS. AS THE EMPLOYEES LOOSEN THE REMAINING TWO TIGHTEN BOLTS PRESSURE IN THE LINE BLOWOUT THE O-RING BLOWING DIRT INTO TWO OF THE EMPLOYEES¿ EYES. COMPANY EMPLOYEES RESPONDED TO MAKE THE LOCATION SAFE WITHIN 45 MINUTES. TWO EMPLOYEES WITH THE DIRT THEIR EYES WERE TAKEN TO A HOSPITAL TO HAVE THEIR EYES CHECKED AND IRRIGATED. THEY WERE BOTH RELEASED WITHOUT INJURIES. THE GATE VALVE AND CHECK VALVE WERE REMOVED AND REPLACE WITH A BALL VALVE. THE OLD GATE VALVE WAS FOUND TO BE DEFECTIVE, HAVING RUST GALLING AT THE BOTTOM OF THE STEM THREADS THAT HAD PREVENTED IT COMPLETE CLOSURE AND ALLOW LINE PRESSURE TO BE PRESENT AT THE CHECK VALVE WHILE THE EMPLOYEES WERE TRYING TO REMOVE THE CLAPPER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050019 | 2005-02-17 | ORIGINAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1223 | 2005-01-12 | 2005 | OVERLAND PARK | JOHNSON | KS | 66106 | 2.42 | SERIES 120, 155+46 | 39.041816 | -94.6728 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45600 | 27337.9454 | 59757.3563 | 1600 | 632.9873 | 44000 | 59124.369 | 0 | 0 | YES | NO | NO | NO | 0 |  | 13 | 52 | 746991 | 2005-01-12 | 190 | 200 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR, SR PIPELINE SAFETY SPEC | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 30 | 0.28 | API 5LX | 42000 | EW | N/A | A O SMITH | 1956 | UNDER GROUND |  | 204 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1963 | NO | [57 empty] | COATING WAS DIS-BONDED IN AN AREA FROM 4:00 TO 7:00, APPROXIMATELY 1' IN WIDTH CAUSING SHIELDING OF THE CURRENT FROM GETTING TO THE PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050020 | 2005-02-17 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1645 | 2005-01-24 | 2005 | AGUSTA | BUTLER | KS | 67010 | 1.04 | SERIES 100 54+94 | 37.6792633885 | -96.9664809564 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143910 | 87029.556 | 193376.9986 | 0 | 0 | 138910 | 186658.3203 | 5000 | 6718.6783 | NO | NO | NO | NO | 0 |  | 0 | 0 | 748136 | 2005-01-24 | 253 | 270 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR, SR PIPELINE SAFETY SPEC | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 6.62 | 0.19 | API | 35000 | ERW |  | U S S CHEMICAL | 1975 | UNDER GROUND |  | 77 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1975 | NO | [57 empty] | WHILE PERFORMING HIGHWAY CROSSING PATROL OF 400/77 HIGHWAY ON LINE AK, SSCGP EMPLOYEES CHECKED THE VENT MARKER ON NORTH SIDE OF HIGHWAY WITH A PRAGMATICS LEAK DETECTOR. AT THAT TIME A LEAK WAS DETECTED. ONCE CONFIRMED THE OPERATOR CALLED THE DISTRICT MANAGER TO LOCATION FOR VERIFICATION. UPON VERIFICATION THE DISTRICT MANAGER CALLED GAS CONTROL AND OTHER COMPANY OFFICIALS OF THE SITUATION. AT THAT POINT IN TIME THE SSCGP OPERATOR'S CONTINUED THEIR INVESTIGATION AND DISCOVERED THAT THE LEAK AREA WAS CONFINED TO THE CASING UNDER THE ROAD CROSSING AND NO FARTHER AWAY THAN FIVE FEET FROM THE NORTH END OF THE CASING. CENTRAL REGION OPS WAS ADVISED BECAUSE HIGHWAY 400 WAS INVOLVED AND THEY ADVISED MONITORING THE LEAK AS A PRECAUTION. TEST HOLES WERE ESTABLISHED AND WERE CHECKED THREE TIMES PER DAY AS ADVISED BY THE OPS. ON JANUARY 25TH THE DAY WAS SPENT FILLING OUT PAPERWORK AND CALLING IN ONE CALLS TO ESTABLISH WHERE THE OTHER UTILITIES WERE IN THE AREA. ALSO, ON THIS DAY, UNDER THE ADVISE OF THE OPS, WE WERE ASKED TO LOWER THE LINE PRESSURE FROM 253# TO 200#. THIS FUNCTION WAS PERFORMED. ON JANUARY 26TH SSCGP EMPLOYEES SHOWED UP ON SITE TO PERFORM EXCAVATION TO SEE IF THE LEAK COULD BE FOUND. UPON EXCAVATION A LEAK WAS FOUND OUTSIDE OF THE END OF THE CASING ON THE NORTH SIDE OF THE HIGHWAY. SSCGP EMPLOYEES INSTALLED A MECHANICAL SPLIT REPAIR SLEEVE AND STOPPED THE LEAK. AT THE TIME THE LEAK WAS THOUGHT TO BE CONTAINED AND SSCGP EMPLOYEES WOULD COME BACK WHEN WEATHER PERMITTED AND REPLACE THE PIPE. UPON COMPLETION OF BACKFILLING OF THE LEAK AREA THE DISTRICT MANAGER ASKED THE OPERATOR TO CHECK THE CASING VENT ONCE AGAIN FOR LEAKAGE. AT THE TIME IT WAS THOUGHT THAT MAYBE THE SATURATED SOIL WAS STILL SETTING OFF THE LEAK DETECTOR. THE DISTRICT MANAGER ADVISED THE OPERATOR TO RELEASE NITROGEN IN THE VENT MARKER IN HOPES THAT THIS WOULD NEUTRALIZE THE SOIL OR CONTENTS OF THE CASING THAT MIGHT BE SATURATED WITH NATURAL GAS. THE OPERATORS DID SO AND WAITED APPROXIMATELY 20 MINUTES. USING THE PRAGMATICS THE CASING VENT WAS CHECKED ONCE AGAIN. GAS LEAKAGE WAS DETECTED. LINE PRESSURE WAS LEFT AT 200# AND MONITORING FOR LEAKAGE WAS CONTINUED. ON JANUARY 25TH SSCGP EMPLOYEES MET WITH CONTRACT EMPLOYEES AND IMMEDIATELY STARTED THE PROCESS FOR THE REPLACEMENT OF THE 400/77 HIGHWAY CROSSING. WORKED CONTINUED THROUGH FEBRUARY 1ST UPON COMPLETION OF REPLACEMENT OF PIPE. FOR THE DURATION OF THIS PROJECT SSCGP EMPLOYEES MONITORED THE LEAK AS REQUESTED BY THE OPS. THE OPERATING PRESSURE OF 253# WAS RE-ESTABLISHED ON LINE AK FEBRUARY 2ND.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050021 | 2005-03-01 11:16 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1440 | 2005-02-15 | 2005 |  |  | LA |  | 523M-102+2.68 |  | 28 *42.03' | 91*02.48' | OFFSHORE |  | SHIP SHOAL | 157 |  | YES | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650000 | 385629.6313 | 826022.2487 | 50000 | 19780.8535 | 600000 | 806241.3951 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 750159 | 2005-02-15 | 1100 | 1200 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | SUB-SEA TIE-IN | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 26 | 0.56 | API | 60000 | DSAW |  |  |  | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | 'DASPIT' REPAIR CLAMP | [8 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | A SMALL LEAK WAS DISCOVERED IN SHIP SHOAL BLOCK 157, ON THE TGP 26 IN. LINE 523M-100. THE LEAK WAS APPARENTLY DUE TO A DEFECT IN A PREVIOUSLY INSTALLED DASPIT REPAIR CLAMP. THE LEAK IS IN A SEAM, AT THE 8:00 POSITION. AFTER THE LINE WAS SHUT-IN, THE DAMAGED REPAIR CLAMP WAS REMOVED. A NEW REPAIR CLAMP WAS INSTALLED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050022 | 2005-02-28 | ORIGINAL FINAL | 18536 |  | SOUTHWEST GAS CORPORATION | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | CLARK | NV | 89150-0002 | 831 | 2005-01-26 | 2005 | LAS VEGAS | CLARK | NV | 89118 |  |  | 36.0715752 | -115.213233 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76706 | 43388.1216 | 84004.0264 | 20112 | 7956.6505 | 56594 | 76047.3759 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 36 | 748324 | 2005-01-26 | 270 | 300 | NO | NO | YES | NO | NO | NO | KENLEY ANDERSON, SPECIALIST/COMPLIANCE | 7023652180 | KENLEY.ANDERSON@SWGAS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 8.62 | 0.19 | API5L | 35000 | ELECTRIC RESISTANCE WELD | NA | REPUBLIC STEEL | 1955 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 1 | 25 | 2005 | ONE-CALL SYSTEM | NO | [40 empty] | WHILE MOVING DIRT WITH A BULLDOZER FOR ROAD IMPROVEMENTS, AN OPERATOR FOR VT CONSTRUCTION STRUCK AND DAMAGED AN 8-INCH STEEL 300 PSIG TRANSMISSION LINE. THE CONTRACTOR CALLED THE "USA ONE CALL" SYSTEM FOR RE-MARKS. THE CONTRACTOR DID NOT WAIT THE REQUIRED TWO WORKING DAYS BEFORE BEGINNING TO EXCAVATE. THE TRANSMISSION LINE WAS MARKED WITH THE REQUIRED LINE MARKERS. THERE WERE 35,850 THERMS OF GAS LOST. THERE WAS NO IGNITION OF GAS, INJURIES OR FATALITIES RESULTING FROM THE INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050023 | 2005-03-07 15:53 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP. | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 1520 | 2005-02-07 | 2005 | HERCULANEUM | JEFFERSON | MO | 63048 | MILE POST 2 | 83+37 | 38.25677 | -90.38308 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK DUE TO A STRESS CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 58983.4297 | 124892.38 | 10000 | 3956.1707 | 90000 | 120936.2093 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 749638 | 2005-02-09 | 564 | 680 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT, SR. MANAGER DOT COMPLIANCE PROGRAMS | 3184293606 | JOHNNY.CAVITT@ENABLEMIDSTREAM.COM | TRANSMISSION | OTHER | CRACK ON 4 | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 4 | [7 empty] | UNDER GROUND |  | 48 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | LEAK ON LINE A-86, NEAR JOACHIM CREEK, REPORTED TO OUR FIELD PERSONNEL AND SYSTEM CONTROL ON 2/07/2005. OUR FIELD PERSONNEL RESPONDED IMMEDIATELY TO THE LEAK LOCATION. PRESSURE ON THE LINE WAS LOWERED AND THE SITE WAS MANNED 24 HOURS A DAY. THE FIRST ESTIMATE OF REPAIR WAS TO SLEEVE THE LEAK, HOWEVER UPON EXCAVATION OF THE LEAK A CRACK IN A 4" 45 DEGREE ELBOW WAS FOUND AND IT WAS DETERMINED A SECTION OF PIPE WOULD HAVE TO BE REPLACED. DUE TO THE INCREASING COST OF THE REPAIR THE LEAK WAS REPORTED TO NRC ON 2/09/2005. THE CRACK IS BELIEVED TO BE CAUSED BY EARTH MOVEMENT ALONG THE CREEK BANK. THE FAILED ELBOW WAS SUBMITTED FOR METALLURGIST ANALYSIS. THE METALLURGIST REPORTED THAT THE CRACK WAS DUE TO STRESS AND WAS CONSISTANT WITH A FRACTURE WHICH WOULD HAVE OCCURRED DUE TO EARTH MOVEMENT. A COPY OF THE METALLURGIST REPORT WAS SENT TO THE OPS CENTRAL REGION OFFICE. UPDATED BY PHMSA ON 12/16/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050024 | 2005-03-10 16:06 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINES - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1845 | 2005-02-11 | 2005 | HOUMA | TERREBONNE | LA | 70363 | 127.27 | 6719+91 | 29 18.623 | 91 08.939 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714000 | 407329.8533 | 803935.8117 | 164000 | 64881.1995 | 550000 | 739054.6122 | 0 | 0 | NO | NO | NO | NO | 0 |  | 40 | 10 | 749888 | 2005-02-12 | 650 | 1169 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 30 | 0.41 | API 5LX | 60000 | DSAW | ANSI 600 | US STEEL | 1964 | UNDER WATER |  | 192 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1965 | NO | [57 empty] | A POSSIBLE LEAK WAS REPORTED TO WGP PERSONNEL FROM TERREBONNE PARISH WATER PATROL WHO CALLED THE NRC (#749856) AT APPROXIMATELY 1846 HOURS ON 2/11/05. WGP PERSONNEL SEARCHED FOR THE LEAK IN THE AREA OF A SHEEN IN THE VICINITY OF WGP PIPELINES AT FOUR LEAGUE BAY. THE LEAK, IN THE FORM OF BUBBLES, WAS CONFIRMED AS ORIGINATING NEAR WGP-TRANSCO SELA LINE B AT 9:25 AM ON 2/12/05. WGP GAS CONTROL NOTIFIED THE NRC (#749888) AT 10:45 AM ON 2/12/05. UT READINGS LATER REVEALED AN ISOLATED PINHOLE AT THE 6:00 POSITION IN A GIRTH WELD CAUSED BY INTERNAL CORROSION. DIVERS INSTALLED A CLAMP. THE CLAMP WAS PRESSURE TESTED AND THE LINE RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20050025 | 2005-03-14 12:32 | ORIGINAL | 30716 |  | NEUMIN PRODUCTION CO | 103 FANNIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 | 1000 | 2005-03-07 | 2005 |  | CALHOUN | TX |  |  |  | 28.343 | 96.740 | OFFSHORE |  | SAN ANTONIO BAY | 99 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 751975 | 2005-03-07 | 400 | 1000 | NO | YES | NO | NO | NO | NO | ROBERT C. SERRATA | 3619878914 | ROBERTS@FTPC.FPCUSA.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2002 | 3 | 0.25 | GRADE 13 |  | SMLS |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | MICROBIOLOGICAL |  | YES | 2002 | NO
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050026 | 2005-03-10 | ORIGINAL | 18532 |  | TEXAS GAS SERVICE COMPANY | 1301 S MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TRAVIS | TX | 78746 | 324 | 2005-02-05 | 2005 | ALTON | HIDALGO | TX | 78572 |  |  | 26.2167 | 98.33250 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50151 | 23394.5545 | 23311.6538 | 46490 | 18392.2376 | 3661 | 4919.4162 | 0 | 0 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 3 | 16 | 749508 | 2005-02-05 | 380 | 550 | NO | NO | YES | NO | NO | NO | FRANCES VALDEZ, SAFETY/TRAINING SPECIALIST | 9564443930 | MVALDEZ@TXGAS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 8 | 0.19 | UNK |  |  |  | UNK |  | UNDER GROUND |  | 42 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | LANDOWNER |  | NO |  |  |  |  | NO | [40 empty] | LANDOWNER WAS BUILDING A POND AND HIT 8" HIGH PRESSURE TRANSMISSION LINE WITH FRONT LOADER.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050027 | 2005-03-14 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 1130 | 2005-02-14 | 2005 | SEMINOLE | GAINES | TX | 79360 | 57.84 TXM15501 (M840B) |  | 32.52692 | -102.377 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121300 | 56054.0787 | 53013.3792 | 116000 | 45891.5802 | 5300 | 7121.799 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 750018 | 2005-02-14 | 750 | 800 | YES | NO | NO | NO | NO | NO | JOHN A GORMLEY, SR PIPELINE SAFETY SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1954 | [8 empty] | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | THREADS | [7 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | AT APPROXIMATELY 11:30 A.M. ON FEBRUARY 14, 2005, A NORTHERN NATURAL GAS EMPLOYEE WAS IN THE PROCESS OF REMOVING A THIRD PARTY GAS MEASUREMENT METER FROM AN ABANDONED METER RUN WHEN THE METER FELL AND THE WEIGHT OF THE METER BENT A 1-INCH RISER ON NORTHERN NATURAL GAS 30-INCH RISER ON NORTHERN GAS 30-INCH TXM15501 (M840B) PIPELINE. THE 1-INCH RISER CRACKED RESULTING IN THE RELEASE OF HIGH-PRESSURE SWEET NATURAL GAS. TWENTLY MILES OF 30" PIPELINE HAD TO BE BLOWN DOWN TO SAFELY REPAIR THE RISER.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050028 | 2005-03-21 10:19 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 830 | 2005-03-04 | 2005 |  |  |  |  | 524C-601+ 5.00 |  | 28*59.36' | 90*15.45' | OFFSHORE |  | SOUTH TIMBALIER | 21 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950000 | 544681.2144 | 1086925.158 | 200000 | 79123.4141 | 750000 | 1007801.7439 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 751629 | 2005-03-04 | 980 | 1138 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | 12 IN. END CONNECTOR | STEEL |  | NO | NO | NO | PIPELINE |  | 2004 | 12.75 | 0.38 | API | 52000 | UNKNOWN |  | NATIONAL TUBE | 1973 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | 12-INCH OIL STATES END CONNECTOR | [8 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 12 | 22 | 2004 | WATER |  | 8 | 2160 | [12 empty] | A LEAK WAS DISCOVERED ON THE 12 IN. TGP 524C-600 LINE IN SOUTH TIMBALIER BLOCK 21. APPARENTLY, A PREVIOUSLY-INSTALLED END CONNECTION FITTING, FOLLOWING HURRICANE IVAN REPAIRS, BECAME SEPARATED FROM THE PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050029 | 2005-03-21 14:55 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 743 | 2005-03-08 | 2005 |  |  |  |  | 509A-401+ 1.01 |  | 28*28.47' | 92*37.62' | OFFSHORE |  | EAST CAMERON | 271 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600000 | 1435872.0688 | 2626184.204 | 915000 | 361989.6194 | 1685000 | 2264194.5847 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 752069 | 2005-03-08 | 1137 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 16 | 0.38 | API | 52000 | UNKNOWN |  | US STEEL | 1974 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | ELECTROCHEMICAL ATTACK AND MICROBIOLOGICAL | YES | 1974 | NO | [57 empty] | A LEAK WAS REPORTED IN EAST CAMERON BLK. 271, ON THE 16 IN. TGP 509A-400 LINE. THE LEAK WAS SUBSEQUENTLY LOCATED APPROXIMATELY 1 MILE SOUTHEAST OF THE EAST CAMERON BLOCK 254 PLATFORM. THE CAUSE OF THE LEAK WAS DETERMINED TO BE DUE TO INTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050030 | 2005-03-18 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFT ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 822 | 2005-02-21 | 2005 | GORMAN | LOS ANGELES | CA |  | 134.68 |  | 34 37 32.30N | 118 42 27.15 W | ONSHORE | 1 |  |  |  | NO | YES | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 238171.057 | 513791.2987 | 25000 | 9890.4268 | 375000 | 503900.872 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 8 | 750664 | 2005-02-21 | 248 | 317 | NO | NO | NO | NO | YES | NO | W JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1931 | 26 | 0.25 |  | 3 |  |  | WESTERN PIPE AND STEEL | 1931 | UNDER GROUND |  | 60 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | MUDSLIDE | [52 empty] | ON FEBRUARY 21, 2005, A 26" TRANSMISSION LINE WAS SEVERED WHEN A MAJOR LANDSLIDE OCCURRED IN THE IN AN AREA OF THE ANGELES NATIONAL FOREST. THIS PARTICULAR SECTION OF PIPELINE, WHICH ORIGINALLY HAD APPROXIMATELY 5 FEET OF COVER, HAD NOT BEEN SUBJECT TO PREVIOUS LANDSLIDES. GAS WAS CONTROLLED BY CLOSING 2 LINES VALVES. DAMAGED PIPING WAS CAPPED, AND IS CURRENTLY AWAITING RE-ROUTING. THIS INCIDENT BECAME REPORTABLE AT 14:00 WHEN DAMAGE ESTIMATES, INCLUDING GAS LOSS EXCEEDED $50,000. THERE WAS NO IGNITION AND NO DAMAGE TO PUBLIC OR PERSONAL PROPERTY. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050031 | 2005-04-01 11:36 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 715 | 2005-03-14 | 2005 |  |  |  |  | 5.24 |  | 28*46'24.4 | 91*43'39.77 | OFFSHORE |  | EUGENE ISLAND | 175 |  | YES | NO | INTERSTATE | OTHER | LEAKING SEAL ON SWIVEL JOINT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 43118.9032 | 86558.3956 | 15000 | 5934.2561 | 60000 | 80624.1395 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 752619 | 2005-03-14 | 920 | 1300 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 10 | 0.34 | API | 46000 | ERW |  | UNKNOWN | 1967 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | SWIVEL JOINT SEAL | [6 empty] | MATERIAL DEFECT |  | NO | YES | 12 | 6 | 1967 | WATER |  | 24 | 2800 | [12 empty] | WHILE PERFORMING MAINTENANCE AT THE SUB-SEA TIE-IN ASSEMBLY ON ANR'S 10-INCH 736-32 PIPELINE IN EUGENE ISLAND BLOCK 175, THE DIVER DISCOVERED A LEAKING JOINT. A SMALL LEAK IN A CHIKSAN SWIVEL JOINT WAS FOUND.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050032 | 2005-04-01 15:24 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1730 | 2005-03-12 | 2005 |  |  |  |  | MP 526-1A+ 0.01 |  | 29*18'18 | 89*44'44 | OFFSHORE |  |  |  | LA | NO | NO | INTERSTATE | OTHER | LEAKING COLLAR FOR VALVE BODY DRAIN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 53017.1944 | 86967.6364 | 50000 | 19780.8535 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 15 | 752538 | 2005-03-12 | 900 | 1000 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | COLLAR ON VALVE BODY DRAIN | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 30 | 0.63 | API | 52000 |  | GATE | GROVE | 1970 | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | DURING MAINTENANCE OPERATIONS AT THE MAINLINE VALVE NO. 526-1A SITE, ON TENNESSEE GAS PIPELINE CO'S LINE 500-1, A LEAK WAS DISCOVERED IN THE COLLAR FOR THE VALVE BODY DRAIN. THE VALVE IS A 30-INCH GROVE GATE VALVE. THE VALVE ASSEMBLY WILL NEED TO BE REPLACED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050033 | 2005-04-07 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 2208 | 2005-04-06 | 2005 | JACKSON | JACKSON | MN | 56143 | 5.666 / MNB87001 AYA06 | 299+16 | 43.5586 | -94.9392 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103287 | 62462.8014 | 138790.425 | 0 | 0 | 103287 | 138790.425 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 |  |  |  | 495 | YES | NO | NO | NO | NO | NO | JOHN A GORMLEY - SR. CORROSION SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1939 | 6 | 0.28 | 5L | 35000 | SEAMLESS | PLUG | ROCKWELL 2049 | 1992 | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 8 |  |  | THE INCIDENT OCCURRED AT THE COMPLETION OF A CONSTRUCTION PROJECT TO MOVE THE WORTHINGTON 6" (MNB87001) BLOCK VALVE AYA06 OUTSIDE OF A ROAD RIGHT-OF-WAY. THE WORTHINGTON BRANCH LINE HAD BEEN BLOWN DOWN UPSTREAM OF THIS VALVE TO A STOPPLE FITTING DOWNSTREAM DURING THE CONSTRUCTION PROJECT. THE PIPELINE WAS BEING PURGED ON THE DAY OF THE INCIDENT FROM THE TAKE-OFF VALVE TO THIS BLOCK VALVE. THEN THE PIPELINE WAS PURGED FROM THIS BLOCK VALVE TO THE STOPPLE FITTING DOWNSTREAM. DURING THE PURGING PROCESS THE NORTHERN EMPLOYEE APPROACHED THE VALVE FROM TWO DIFFERENT DIRECTIONS. THE VALVE HAD NOT BEEN COMPLETELY BACKFILLED SO THE VALVE OPERATOR AND INDICATOR WAS OVER HIS HEAD. WHEN THE PIPELINE PURGING WAS COMPLETED THE NORTHERN EMPLOYEE INADVERTENTLY CLOSED THE BLOCK VALVE AYA06 THINKING THAT HE WAS OPENING IT AND LEFT FOR THE DAY. LATER THAT SAME EVENING AQUILA (THE LOCAL DISTRIBUTION COMPANY) CONTACTED NORTHERN TO REPORT A LOSS OF GAS SERVICE TO THE TOWN OF JACKSON, MN. APPROXIMATELY 1500 CUSTOMERS WERE WITHOUT NATURAL GAS. NORTHERN OPENED THE BLOCK VALVE AYA06 AND PURGED THE 4.5 MILES OF WORTHINGTON 6" BRANCH LINE AND 1600' OF JACKSON (MNB87201) BRANCH LINE. AQUILA BEGAN RE-LIGHTING CUSTOMERS THE MORNING OF APRIL 7. THERE WAS NO NATURAL GAS LEAK AND NO KNOWN THREAT TO PUBLIC SAFETY. JACKSON HAD FAIR SKIES WITH A HIGH TEMPERATURE ON APRIL 6 OF 54°F AND A LOW OF 39°F. UPDATED BY PHMSA ON 12/3/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050034 | 2005-04-08 16:37 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 910 | 2005-03-18 | 2005 |  |  |  |  | MP 527A-701+0.1 |  | 28*49'50.09 | 89*24'21.91 | OFFSHORE |  | SOUTH PASS | 77 |  | YES | NO | INTERSTATE | OTHER | PIPELINE DAMAGED BY VESSEL STRIKING RISER BELOW . | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600000 | 952684.2281 | 2055165.1949 | 100000 | 39561.707 | 1500000 | 2015603.4878 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 753036 | 2005-03-18 | 700 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 26 | 0.75 | API | 60000 |  |  | UNKNOWN |  | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A LEAK WAS REPORTED BY CHEVRON TEXACO PERSONNEL AT THE SOUTH PASS BLOCK 77 PLATFORM, ON THE TGP 26-INCH LINE NO. 527A-700. PIPE WAS DAMAGED BY A MARINE VESSEL OPERATING IN THE AREA NEAR THE PIELINE RISER. VESSEL APPARENTLY STRUCK THE RISER BELOW THE WATER LINE, AND CAUSED THE PIPELINE TO LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050036 | 2005-03-11 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 935 | 2005-02-28 | 2005 | PIRU | VENTURA | CA |  | 35.1 |  | 34 22 50.78N | 118 44 15.26 W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 1205770.8735 | 2663768.3524 | 25000 | 9890.4268 | 1975000 | 2653877.9257 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 30 | 751292 | 2005-02-28 | 643 | 773 | NO | YES | NO | NO | NO | NO | W JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO |  |  | 1971 | 34 | 0.38 | [5 empty] | 1971 | UNDER GROUND |  | 60 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | MUDSLIDE | [52 empty] | ON FEBRUARY 28, 2005 A 34" TRANSMISSION LINE WAS SEVERED WHEN A MAJOR LANDSLIDE OCCURRED IN THEIN AN UNPOPULATED AREA OF THE FOOTHILLS SURROUNDING PIRU. THIS PARTICULAR SECTION OF PIPELINE, WHICH ORIGINALLY HAD APPROXIMATELY 5 FEET OF COVER, HAD NOT BEEN SUBJECT TO PREVIOUS LANDSLIDES. GAS WAS CONTROLLED BY CLOSING 2 LINE VALVES. DAMAGED PIPING WAS CAPPED, AND IS CURRENTLY AWAITING RE-ROUNTING. THIS INCIDENT BECAME REPORTABLE WHEN DAMAGE ESTIMATES, INCLUDING GAS LOSS EXCEEDED $50,000. THERE WAS IGNITION, BUT NO RESULTING DAMAGE TO PUBLIC OR PERSONAL PROPERTY. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050037 | 2006-01-10 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC. | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1415 | 2005-02-24 | 2005 | FAIRWAY | JOHNSON | KS | 66205 | 1+3213 | 100/852 | 39.0284076526 | -94.6257960161 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451164 | 272393.9096 | 603400.7989 | 3000 | 1186.8512 | 448164 | 602213.9477 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 751287 | 2005-02-28 | 190 | 200 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR, SR. PIPELINE SAFETY SPEC. | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 20 | 0.25 | API | 46000 | FLASH WELD |  | A.O. SMITH | 1956 | ABOVE GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1958 | YES | 40 | 0 | [55 empty] | PIPELINE WAS PRESSURE TESTED IN 2004 CAUSING THE PIPELINE TO FAIL IN THE CORRODED AREA.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050038 | 2005-04-18 09:31 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CORPORATION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1200 | 2005-03-22 | 2005 | [6 empty] | 28 27 18.04180N | 91 40 31.11293W | OFFSHORE |  | EUGENE ISLAND | 264 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175400 | 90188.0283 | 134716.6049 | 106500 | 42133.218 | 68900 | 92583.3869 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 753424 | 2005-03-22 | 850 | 1250 | NO | YES | NO | NO | NO | NO | DAVID D. ANDERSON | 7242232766 | DDANDERSON@NISOURCE.COM | GATHERING | OTHER | GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 20 | 0.44 | 5L | 52000 | SEAMLESS |  | US STEEL | 1974 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL | MICROBIOLOGICAL |  | YES | 1974 | NO | [57 empty] | THE LEAK WAS DISCOVERED AT 2:45 PM ON MARCH 22, 2005. THE LINE WAS SHUT AND PRESSURE LOWERED UNTIL REPAIRS COULD BE MADE. A REPAIR SLEEVE WAS INSTALLED ON MARCH 29, 2005 AND THE LINE PLACED BACK IN SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050039 | 2005-04-20 11:31 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE COMPANY OF AMERICA | 500 DALLAS STREET #100 | HOUSTON | HARRIS | TX | 77002 | 1745 | 2005-03-30 | 2005 | NAPLES | MORRIS | TX |  | 197 | 10378+90 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 45559.4002 | 39561.707 | 100000 | 39561.707 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 754307 | 2005-03-30 |  |  | YES | NO | NO | NO | NO | NO | REBECCA FIELDS | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 30 | 0.31 | X70 |  | DOUBLE SUBMERGED ARC WELD |  |  |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | NO |  |  |  |  | YES |  | YES | ACCURATE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050040 | 2005-04-20 17:14 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1330 | 2005-03-23 | 2005 |  |  | LA |  | 526A-2401+3.50 |  | 28*57 | 89*18 | OFFSHORE |  | SOUTH PASS | 39 | LA | NO | NO | INTERSTATE | OTHER | A 1.5 IN. CRACK WAS FOUND AT 6 OCLOCK PIPE POSITIO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600000 | 952684.2281 | 2055165.1949 | 100000 | 39561.707 | 1500000 | 2015603.4878 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 | 753552 | 2005-03-23 | 880 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2001 | 12.75 | 0.5 | API | 42000 | SEAMLESS |  | UNKNOWN | 2001 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | A LEAK WAS REPORTED ON THE 12-INCH TGP LINE NO. 526A-2400, IN SOUTH PASS BLOCK 39, STATE WATERS. THE LEAK WAS REPORTEDLY IN AN AREA THAT WAS PREVIOUSLY REPAIRED WITH A REPAIR CLAMP IN NOVEMBER, 2001. FURTHER INVESTIGATION WILL CONTINUE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050041 | 2005-04-21 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC. | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302 | 1115 | 2005-03-28 | 2005 |  | FAIRFIELD | OH | 43125 | BETWEEN VLAVE 304 & 305 | 4298+38 | 39.829269 | 82.797859 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | THIRD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 80521.8546 | 136782.9906 | 68322 | 27029.3495 | 81678 | 109753.6411 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 754249 | 2005-03-30 | 830 | 850 | YES | NO | NO | NO | NO | NO | MARTIN C. SCHWOEBLE | 7244687726 | MARTIN_C_SCHWOEBLE@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 26 | 256 | [6 empty] | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | HOE BUCKET SCRAPED PIPE | [10 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | ON SATURDAY MARCH 26, 2005, AT APPROXIMATELY 11:15 AM, WHILE EXCAVATING FOR A NEW WATERLINE, A BACKHOE OPERATED BY A THIRD PARTY CONTRACTOR, DUG INTO AND DAMAGED DTI¿S INTERSTATE NATURAL GAS TRANSMISSION PIPELINE TL 400. THE DAMAGED PIPE WAS REMOVED (26¿, .256 WALL, X-60, LENGTH 62¿) AND REPLACED WITH .312 WALL, X-65. (THERE WAS NO LEAK OR ESCAPE OF GAS, NO FATALITIES AND NO EVACUATION OF PEOPLE.)
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20050042 | 2005-04-21 | SUPPLEMENTAL FINAL | 4900 |  | KINDER MORGAN TEJAS PIPELINE | 500 DALLAS STREET SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 915 | 2005-03-15 | 2005 | NACOGDOCHES | NACOGDOCHES | TX | 75964 |  |  | 31 47 25 | 94 4534 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 10 | 752771 | 2005-03-15 | 0 | 1001 | NO | YES | NO | NO | NO | NO | REBECCA VOSS FIELDS, SENIOR COMPLIANCE ENGINEER | 7133699418 | REBECCA_FIELDS@KINDERMORGAN.COM | TRANSMISSION | OTHER | PIG LAUNCHER | STEEL |  | NO | NO | NO | OTHER | PIG LAUNCHER | 1966 | 20 | 0.34 | X-60 | 60000 | NA | M&J GATE VALVE |  | 1966 | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 2
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050043 | 2005-04-29 09:10 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 530 | 2005-04-04 | 2005 | SENECA ROCKS | PENDLETON | WV | 26884 | SENECA COMPRESSOR STATION |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493200 | 224698.9619 | 195118.3391 | 493200 | 195118.3391 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 15 | 754698 | 2005-04-04 | 700 | 1000 | NO | NO | YES | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION |  |  |  |  | NO | NO | NO | COMPRESSOR |  | 1953 | [8 empty] | OTHER | COMPRESSOR STATION |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | COMPRESSOR ESD SYSTEM | [10 empty] | COMPRESSOR STATION WAS NOT MANNED DURING THE TIME OF THE INCIDENT. THE STATION ESD SYSTEM IS A PRESSURIZED SYSTEM USING BOTH COMPRESSED GAS AND PIPELINE PRESSURE TO DRIVE THE VALVE ACTUATORS. DURING HIGH WINDS, THE STATION LOST ONE PHASE OF COMMERCIAL ELECTRICAL POWER. DURING THE LOSS OF POWER, THERE WAS A SLOW LEAK ON THE COMPRESSED AIR SYSTEM. WHEN THE AIR PRESSURE FELL BELOW 75 PSI, THE ESD VENT VALVES POWERED BY PIPELINE GAS ACTIVATED. THERE WAS NOT ENOUGH REMAINING PRESSURE TO CLOSE THE FIRE VALVES. ALL THE FIRE VALVES WERE MANUALLY CLOSED APPROXIMATELY 2 HOURS AFTER THE ESD SYSTEM ACTIVATED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050045 | 2005-04-25 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1529 | 2005-03-21 | 2005 | COLUMBIA | CALDWELL | LA | 71418 | 126.66/GV #61 | 4+10 | 32 -7.353' | 92 -5.225' | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CIRCUMFERENTIAL CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 48007.1011 | 105128.5562 | 2500 | 989.0427 | 77500 | 104139.5135 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 3 | 753434 | 2005-03-22 | 750 | 900 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENERGY.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 24 | 0.5 | API 5LX | 45000 | SMLS | N/A | NATIONAL TUBE | 1950 | UNDER GROUND |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | A CORPS OF ENGINEER WORKBOAT CREW DISCOVERED THE LEAK ON THE OUACHITA RIVER BANK. A MEMBER OF THAT CORPS OF ENGINEER WORKBOAT CREW CONTACTED TRUNKLINE GAS COMPANY'S GAS CONTROL, USING THE EMERGENCY CONTACT INFORMATION FROM THE TRUNKLINE GAS COMPANY LINE MARKER AND "DO NOT DREDGE" SIGN. TRUNKLINE GAS COMPANY'S GAS CONTROLLER CONTACTED FIELD PERSONNEL AT TRUNKLINE GAS COMPANY'S EPPS LOCATION WHO COORDINATED A RESPONSE WITH TRUNKLINE GAS COMPANY'S POLLOCK LOCATION. THE EPPS AND POLLOCK PERSONNEL PROCEEDED TO THE ISOLATION VALVES, THEN ISOLATED AND DEPRESSURIZED THE LINE SEGMENT. CAUSE IS STILL UNDER INVESTIGATION. THE INVESTIGATION IS BEING HAMPERED BY WET CONDITIONS ON A STEEP SLOPE AND SINCE THE LINE IS NOT CRITICAL TO CURRENT OPERATIONS, IT CAN BE LEFT OUT OF SERVICE UNTIL CONDITIONS IMPROVE. 5-31-05 INVESTIGATION REVEALED THAT THE LAND MOVEMENT ON THE STEEP SLOPE HAD CAUSED A BUCKLE, WHICH SUBSEQUENTLY DEVELOPED A CRACK IN THE BUCKLE. SINCE THE LINE IS NOT CRITICAL TO CURRENT OPERATIONS, IT WILL BE LEFT OUT OF SERVICE. IT SHOULD BE NOTED THAT THE RUGGED TERRAIN AT THE INCIDENT LOCATION HAD A LARGE EFFECT ON THE OPERATOR DAMAGE COST. SPECIFICALLY, INGRESS TO THE SITE WITH THE EXCAVATION EQUIPMENT AND DIFFICULTY IN PERFORMING THE ACTUAL EXCAVATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050046 | 2005-04-27 | ORIGINAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1228 | 2005-04-11 | 2005 |  |  |  |  | N/A | N/A | 28.506833' | 90.285333' | OFFSHORE |  | SOUTH TIMBALIER | 179 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69130 | 38475.7087 | 71720.958 | 22330 | 8834.1292 | 46800 | 62886.8288 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 10 | 755551 | 2005-04-12 | 1125 | 1312 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 12 | 0.38 | API 5LX | 52000 | SMLS | N/A | YOUNGSTOWN SHEET AND TUBE | 1969 | ABOVE GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1972 | NO | [57 empty] | LEAK WAS DISCOVERED BY PRODUCER. REPAIR WAS MADE BY INSTALLATION OF A BOLT ON LEAK CLAMP. REPAIR WAS COMPLETED AND LINE WAS PUT BACK IN SERVICE ON 4/17/2005.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050047 | 2005-05-06 14:02 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1630 | 2005-04-13 | 2005 |  |  | LA |  |  |  | 28.41345 | 91.69358 | OFFSHORE |  | EUGENE ISLAND | 271 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315000 | 173343.2873 | 314243.0948 | 115000 | 45495.9631 | 200000 | 268747.1317 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 755683 | 2005-04-13 | 850 | 1250 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 20 | 0.44 | API5LX-52 | 52000 | SEAMLESS |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1975 | NO | [57 empty] | LEAK DISCOVERED BY MMS DURING ROUTINE OFFSHORE FLIGHT ON 4/13/05. LEAK WAS CONFIRMED ON SAME DATE. LEAK WAS DETERMINED TO BE AN INTERNAL, PIN HOLE LEAK, LOCATED AT APPROXIMATELY 6:00 POSITION. LEAK WAS REPAIRED WITH A 20¿ X 15.25¿ DASPIT SEA CLAMP. REPAIR WAS COMPLETED ON 4/18/05.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050048 | 2005-05-09 16:56 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1350 | 2005-04-13 | 2005 | HIRAM | QUITMAN | MS |  | MP 61-1+3.34 |  | 34.161797 | -90.188802 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 34874.6978 | 46655.5667 | 50000 | 19780.8535 | 20000 | 26874.7132 | 0 | 0 | NO | NO | NO | YES | 0 | COMPANY POLICY | 3 | 0 | 755675 | 2005-04-13 | 700 | 750 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1944 | 24 | 0.28 | API | 45000 | UNKNOWN |  | NATIONAL TUBE | 1944 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 5 | 20 | 1983 | WATER |  | 8 | 1072 | [12 empty] | A GAS LEAK WAS DISCOVERED ON TGP'S 100-1 LINE AT MP 61-1+ 3.34, AFTER BEING CONTACTED BY LANDOWNER. THE LEAK WAS APPARENTLY DUE TO A PINHOLE LEAK IN A WELD, AT THE 6 O'CLOCK PIPE POSITION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050049 | 2005-05-11 15:01 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP. | 525 MILAM STREET | SHREVEPORT | CADDO | LA | 71101 | 532 | 2005-04-12 | 2005 | PINE BLUFF | JEFFERSON | AR | 71603 | 95.5 | 403+94 | 34.07130 | 91.95197 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222012 | 101939.6517 | 92868.143 | 216700 | 85730.2191 | 5312 | 7137.9238 | 0 | 0 | NO | NO | NO | YES | 4 | PRECAUTIONARY | 1 | 30 | 755502 | 2005-04-12 | 438 | 450 | NO | NO | NO | NO | YES | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 22 | 0.31 | UNKNOWN | 30000 | FURNACE LAP | NA. | AO SMITH | 1929 | UNDER GROUND |  | 52 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | NO |  | NO | [57 empty] | ON APRIL 12, 2005 AT APPROXIMATELY 05:11 THE MRT GAS CONTROLLER RECEIVED A LOW PRESSURE SCADA ALARM ON OUR ML-1 PIPELINE. THE CONTROLLER REQUESTED A LOCAL FIELD PERSON TO RESPONSE TO AND INVESTIGATES THE AREA. AT APPROXIMATELY 6:11 THE FIELD PERSON, WHO WAS STILL IN TRANSIT, RECEIVED A CELL PHONE CALL FROM A LOCAL RESIDENT WHO REPORTED WHAT THEY THOUGHT THERE WAS A BLOW OUT AROUND MP 95 OR 96. THE MRT FIELD PERSON CALLS GAS CONTROL REQUESTING HELP TO ISOLATE THE SUSPECTED AREA AND INITIATED OUR EMERGENCY RESPONSE PLAN. THE SUSPECTED AREA WAS ISOLATED BY 06:55, AND FIELD PERSONNEL REPORTED TO GAS CONTROL THE EXACT LOCATION OF THE RUPTURE AT APPROXIMATELY 07:15, WITH NO FIRE AND NO INJURIES. THE LINCOLN COUNTY SHERIFF DEPARTMENT EVACUATED 4 PERSONS FROM A LOCAL DEER CAMP THAT WAS IN THE AREA OF THE RUPTURE. THE AREA WAS MONITORED AND THE PIPELINE WAS ALLOWED TO BLOW DOWN. AREA WAS DEEMED SAFE, AND ALL ISOLATION VALVES WERE LOCKED AND TAGGED OUT. THE RUPTURE SECTION OF PIPE WAS TRANSPORTED TO THE LOCAL TEAM PERSONNEL OFFICE. THE PIPE WAS INSPECTED BY MRT CORROSION MANAGER AND HE DETERMINED THAT THE RUPTURE WAS DUE TO MICROBIOLOGICALLY INFLUENCED CORROSION (MIC).
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20050050 | 2005-05-12 14:30 | ORIGINAL | 31130 |  | DEFS AUSTIN GATHERING, LP DUKE ENERGY FIELD SERVICES | P. O. BOX 89 | WARDA | FAYETTE | TX | 78960 | 830 | 2005-04-23 | 2005 | GIDDINGS | LEE | TX | 78942 |  |  | 30.16 | -96.94 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500 | 2684.0855 | 5809.7808 | 250 | 98.9043 | 4250 | 5710.8765 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 756609 | 2005-04-23 | 16 | 100 | YES | NO | NO | NO | NO | NO | CINDY LOPEZ | 3615848518 | CALOPEZ@DUKE-ENERGY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 10 | 0.24 | X-42 | 2160 | SEAMLESS |  |  |  | UNDER GROUND |  | 40 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1978 | NO | [57 empty] | A 1/8" INTERNAL CORROSION PINHOLE IN THE 10" SUCTION LINE (LINE GS-1) ALLOWED CONDENSATE TO LEAK OUT OF THE PIPE AND ONTO THE GROUND. THE CONDENSATE RAN INTO A STORMWATER DRAINAGE DITCH WHICH WAS NOT RUNNING WITH WATER, HOWEVER, THERE WAS APPROXIMATELY 15 GALLONS OF WATER POOLED UP IN WHICH THE CONDENSATE RAN INTO.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050051 | 2005-05-10 | ORIGINAL FINAL | 15938 |  | PUBLIC SERVICE OF NORTH CAROLINA INCORPORATED (DBA PSNC ENERGY) | 800 GASTON ROAD | GASTONIA | GASTON | NC | 28056 | 1145 | 2005-04-06 | 2005 | MORRISVILLE | WAKE | NC |  | N/A | N/A | N 35.84553 | W -78.87514 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE |  |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36515 | 18383.3762 | 25553.1666 | 24800 | 9811.3033 | 11715 | 15741.8632 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 35 | 754987 | 2005-04-06 | 650 | 1070 | NO | YES | NO | NO | NO | NO | KENNETH G GRIFFIN, MANAGER - OPERATIONS | 9199183023 | KGRIFFIN@SCANA.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2004 | 16 | 0.38 | API 5L | 52000 | ELECTRIC RESISTANCE WELD | N/A | MAVERICK | 2004 | UNDER GROUND |  | 28 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | LANE CONSTRUCTION WAS CONTRACTED TO PERFORM GRADING SERVICES FOR THE CONSTRUCTION OF THE US540 LOOP HIGHWAY. THE CONTRACTOR WAS PREPARING THE SUBGRADE OF THE HIGHWAY USING A LARGE BULLDOZER WITH A ROCK-RIPPING BLADE WHEN IT HIT THE SIXTEEN-INCH TRANSMISSION LINE. THE CONTRACTOR DID NOT HAVE A LOCATE TICKET FOR THE GAS MAIN, ALTHOUGH THE LINE WAS CLEARLY MARKED BY PIPELINE MARKERS AND A TRANSMISSION LOCATOR WAS ONSITE THE PREVIOUS DAY. THE PIPE, AS OF APRIL 7, 2005 IS 19" DEEP AT THE CENTERLINE OF US540 AND IS 34" DEEP ON THE WEST SIDE OF THE US540 AND IS 34" DEEP ON THE WEST SIDE OT THE US540 CONSTRUCTION. AN INVESTIGATION BY LANE CONSTRUCTION AND THE NCDOT IS UNDERWAY TO DETERMINE WHY THEY WERE GRADING AT THE ELEVATION. THE T-21 RELOCATION PERFORMED IN 2004 WAS APPROVED BY THE NCDOT AT THE TIME OF THE RELOCATION AND WAS EXPECTED TO BE 8' DEEP AT THE END OF CONSTRUCTION.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20050052 | 2005-05-16 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 127 | 2005-04-16 | 2005 | SAINT JAMES | SAINT JAMES | LA | 70723 | MP 66.22 | 3496+42 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RUPTURE DISK FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 3350 | 1563.5289 | 1562.3468 | 3100 | 1226.4129 | 250 | 335.9339 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 5 | 755964 | 2005-04-16 | 750 | 995 | NO | NO | NO | NO | YES | NO | JOHNNY LOPEZ, PIPELINE SPECIALIST I | 7132152995 | JOHNNYLOPEZ@WILLIAMS.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | VALVE YARD SCRUBBER |  | 3 | [7 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FORCE FROM SANDBLASTING CAUSED RUPTURE DISK TO RUPTURE. |  | SAND BLASTING CREW WAS SANDBLASTING SCRUBBER WHEN RUPTURE DISK RUPTURED. FORCE FROM ESCAPING GAS KNOCKED CREW MEMBER TO GROUND, WHERE HE WAS INJURED. CREW MEMBER REQUIRED ONE NIGHT STAY IN HOSPITAL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050053 | 2005-05-17 | SUPPLEMENTAL FINAL | 31880 |  | CROSSTEX MISSISSIPPI PIPELINE LP | 1000 SPRINGSRIDGE ROAD | CLINTON | HINDS | MS | 39056 | 1415 | 2005-04-18 | 2005 | WARREN | WARREN | MS |  | N/A | N/A | 32.52731N | 90.76409W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | WRINKLE/BEND CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 455594.0023 | 395617.0704 | 1000000 | 395617.0704 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 756143 | 2005-04-18 | 780 | 960 | YES | NO | NO | NO | NO | NO | KEVIN BEVILLE | 2149793748 | KEVIN.BEVILLE@SOUTHCROSSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1987 | 6 | 0.16 |  | 2000 |  |  | INFORMATION NOT AVAILABLE |  | UNDER GROUND |  | 144 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | WRINKLE BEND | [11 empty] | MATERIAL DEFECT |  | NO | YES | 11 | 18 | 1987 | WATER |  | 12 | 1615 | [12 empty] | AREA GROUND SHIFT DUE TO HEAVY RAINS AND FORCES CAUSING PIPELINE TO WRINKLE AND BEND WHICH RESULTED IN A SMALL CRACK TO THE PIPE (APPROXIMATELY 1 INCH OPENING). UPDATED BY PHMSA ON 12/4/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050054 | 2005-11-03 | ORIGINAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 300 S ST PAUL SUITE 8-122 | DALLAS | DALLAS | TX | 75201 | 1330 | 2004-10-02 | 2004 | KATY | FORT BEND | TX | 77493 | 564+04 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE |  |  | PUNCTURE | 2 | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 47518.797 | 41263.1579 | 80000 | 41263.1579 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 |  | 2004-10-02 | 825 | 1200 | YES | NO | NO | NO | NO | NO | ELLEN WEAVER, MANAGER REGULATORY AND COMPLIANCE | 2148753930 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 18 | 0.38 | 5LX | 56000 | EW SMLS |  |  |  | UNDER GROUND |  | 54 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | WHILE EXCAVATING TO MAKE A TIE-IN, AN ATMOS CONTRACTOR STRUCK A 2-INCH TAP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050055 | 2005-03-20 | SUPPLEMENTAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 300 S ST PAUL SUITE 8-122 | DALLAS | DALLAS | TX | 75201 | 1030 | 2005-02-22 | 2005 | TYLER | SMITH | TX | 75703 |  |  | 32 17 345 | 95 20 926 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126000 | 71425.4973 | 138970.8982 | 32000 | 12659.7463 | 94000 | 126311.1519 | 0 | 0 | YES | NO | NO | YES | 29 | PRECAUTIONARY | 22 | 0 |  | 2005-02-22 | 800 | 1000 | NO | YES | NO | NO | NO | NO | MIKE ARCHER - COMPLIANCE MONITORING | 2142062879 | MICHAEL.ARCHER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 14 | 0.26 | N 45 | 45000 |  |  |  |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | A LANDOWNER CLEARING LAND STRUCK A FOURTEEN INCH TRANSMISSION LINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050056 | 2005-03-14 | ORIGINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 300 S ST PAUL SUITE 8-122 | DALLAS | DALLAS | TX | 75201 | 1000 | 2005-01-01 | 2005 | SPRINGTOWN | PARKER | TX | 76080 |  |  | 32 59 4.43N | 9740 56.9W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE OPENED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10700 | 4874.8558 | 4233.1027 | 10700 | 4233.1027 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 |  | 2005-01-01 | 400 | 500 | NO | YES | NO | NO | NO | NO | ELLEN WEAVER, MANAGER REGULATORY AND COMPLIANCE | 2148753930 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | OTHER | COMMUNICATION LOSS TO RTU | STEEL |  | NO | NO | NO | OTHER | RTU | [9 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | ATMOS GAS CONTROL LOST COMMUNICATION WITH THE RTU THAT CONTROLS THE GAS FLOW FROM THE SPRINGTOWN PROCESSING PLANT. A TECHNICIAN WAS DISPATCHED IMMEDIATELY AND WHILE ENROUTE, FOUR RELIEF VALVES BEGAN TO OPERATE IN AN APPROPRIATE FASHION TO PREVENT OVERPRESSURIZATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050057 | 2005-03-18 | ORIGINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 300 S ST PAUL SUITE 8-122 | DALLAS | DALLAS | TX | 75201 | 1500 | 2005-01-27 | 2005 | HENDERSON | RUSK | TX | 75602 |  | APPROX 4430+25 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88000 | 40539.7399 | 37658.658 | 85000 | 33627.451 | 3000 | 4031.207 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 |  | 2005-01-27 | 785 | 1200 | NO | YES | NO | NO | NO | NO | ELLEN WEAVER, MANAGER REGULATORY AND COMPLIANCE | 2148753930 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 14 | 0.26 | GRADE N-45 | 45000 | ERW |  |  |  | UNDER GROUND |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A NON-ATMOS EXCAVATOR CLEARING VEGETATION GOT A BULLDOZER STUCK. A SECOND BULLDOZER WAS ATTEMPTING TO FREE THE FIRST BULLDOZER WHEN ITS TRACK SUNK DOWN TO THE PIPELINE AND PUNCTURED IT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050058 | 2005-05-23 15:51 | SUPPLEMENTAL FINAL | 26330 |  | ENOGEX INC. | 515 CENTRAL PARK DRIVE, SUITE 600, PO BOX 24300 | OKLAHOMA CITY | OKLAHOMA | OK | 73124 | 130 | 2005-04-24 | 2005 | CENTRAHOMA | COAL | OK | 74534 | MP 7 |  | N34 36' 31.74 | W96 21' 18.94 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 717542 | 336602.964 | 345499.5721 | 652542 | 258156.7543 | 65000 | 87342.8178 | 0 | 0 | NO | NO | NO | YES | 40 | PRECAUTIONARY | 2 | 45 | 756655 | 2005-04-24 | 960 | 973 | YES | NO | NO | NO | NO | NO | TED LILLY | 4055576804 | LILLYTC@OGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 30 | 0.31 | X65 | 65000 | SUBMERGED ARC WELDED (SAW) | N/A | KAISER | 1974 | UNDER GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | DISBONDED COATING | YES | 1975 | NO | [57 empty] | AN INTERNAL INVESTIGATION HAS IDENTIFIED THE CAUSE OF THE FAILURE TO BE THE RESULT OF EXTERNAL CORROSION IN A SMALL AREA OF THE PIPE FOR WHICH THE COATING HAD BECOME DISBONDED. THE FAILED SECTION OF PIPE WAS REPLACED AND THE AREA UPSTREAM AND DOWNSTREAM OF THE FAILURE WERE THOROUGHLY INSPECTED AND FOUND TO BE IN GOOD CONDITION. THIS LINE ALSO HAS AN EFFECTIVE CATHODIC PROTECTION SYSTEM.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050059 | 2005-05-26 17:43 | SUPPLEMENTAL FINAL | 31246 |  | COLUMBIA NATURAL RESOURCES, LLC | 900 PENNSYLVANIA AVENUE | CHARLESTON | KANAWHA | WV | 25302 | 700 | 2005-04-30 | 2005 | INEZ | MARTIN | KY | 41224 |  |  | 37.85104 | -82.52114 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147335 | 89070.9932 | 197789.6695 | 200 | 79.1234 | 42135 | 56618.302 | 105000 | 141092.2441 | NO | NO | YES | YES | 20 | PRECAUTIONARY | 7 | 39 | 757307 | 2005-04-30 | 76 | 78 | NO | NO | NO | NO | YES | NO | ROBERT L. PRICE | 3043535074 | BOB.PRICE@CHK.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 8 | 0.28 | API |  | FURNACE LAP WELD |  | UNKNOWN | 1947 | UNDER GROUND |  | 150 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | OTHER | DIFFERENTIAL O2 CELL CORROSION | NO |  | NO | [57 empty] | INCIDENT OCCURRED AT 0700 HOURS ON APRIL 30, 2005 DURING FLASH FLOODING IN AREA OF OPERATOR'S PIPELINE. OPERATOR NOTIFIED OF EXPLOSION AND FIRE AT 1235 ON APRIL 30, 2005 BY LOCAL DISTRIBUTION COMPANY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050060 | 2005-05-31 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1710 | 2004-11-09 | 2004 | [6 empty] | N 28 7.6' | W96 39.8 | OFFSHORE |  | MATAGRODA | 628 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241000 | 148525.3859 | 284189.3119 | 57000 | 29400 | 184000 | 254789.3119 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 |  |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7138401980 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 |  |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1977 | NO | [57 empty] | 3 SMALL LEAKS IN 6:00 POSITION AND SMALL PINHOLE LEAKS UNDER THE EXISTING FLANGE OF TWO RISERS. REPORT FINALIZED WITH MINOR SUPPLEMENTAL DATA ENTERED. NO CHANGE IN COST OR ANY OTHER CRITICAL INFORMATION
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050061 | 2005-06-02 16:47 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1350 | 2005-05-05 | 2005 | HOT SPRINGS | GARLAND | AR |  | B-10 | 707+50 | 34.5081329 | -92.9212112 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FLANGE GASKET FAILED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50001 | 24367.9201 | 29873.9715 | 39356 | 15569.9054 | 10645 | 14304.0661 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 757820 | 2005-05-05 | 870 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | BLOCK VALVE FLANGE GASKET | OTHER | GARLOCK GASKET | NO | NO | NO | OTHER | FLANGE GASKET | 2003 | 8 | [7 empty] | ABOVE GROUND |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | LINE BT-1AS WAS BEING RETURNED TO SERVICE WHEN COMPANY PERSONNEL NOTICED A FLANGE GASKET BEGAN TO LEAK. DUE TO THE NATURAL OF THE RELEASE THE COMPANY'S EMERGENCY RESPONSE PLAN WAS ACTIVATED. THE AREA WAS ISOLATE AND THE AFFECT PIPE SEGMENT WAS BLOWN DOWN. THE LOCATION WAS MONITORED OVERNIGHT AND ABOUT 30 TO FORTY CUSTOMERS WERE RELIT THE NEXT DAY DURING NORMAL DAYLIGHT WORKING HOURS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050062 | 2005-06-03 13:34 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP. | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1130 | 2004-12-06 | 2004 | GRANITE CITY | MADISON | IL | 62040 | MP-28 | 149447 | 38.7033 | 90.2073 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166886 | 103681.518 | 221532.8509 | 11000 | 5673.6842 | 155886 | 215859.1667 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 760490 | 2005-05-31 | 180 | 200 | NO | NO | NO | NO | YES | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 16 | 0.31 | UNKNOWN | 24000 | UNKNOWN |  | UNKNOW |  | UNDER GROUND |  | 216 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | WRINKLE BEND | [11 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 7 | 13 | 1976 | WATER |  | 8 | 330 | [12 empty] | WE HAD REPORTS OF BUBBLES ON DECEMBER 6, 2004, HOWEVER THE LOCATION OF THE BUBBLES WERE OVER 100 FEET FROM OUR ALTON PIPE LOCATION AND GAS SENSORS DID NOT DETECT GAS. AIR SAMPLES WERE TAKEN TO A LAB WHO DETERMINED THAT NATURAL GAS WAS PRESENT. WE WERE NOT SURE IF THIS WAS COMING FROM OUR PIPELINE HOWEVER THE LINE WAS ISOLATED AND MONITORED. METHODS WERE DISCUSSED WITH THE CUSTOMER/PROPERTY OWNER INCLUDING REPAIR IN-PLACE, BY-PASS AND RE-ROUTE. THE CUSTOMER ASKED FOR REPAIR IN-PLACE BUT THEY HAD TO REMOVER A LARGE AMOUNT OF METAL SLAG THAT HAD PLACE ABOVE THE PIPELINE. IT WAS NOT UNTIL MAY 3, 2005 THAT THE PIPELINE WAS EXCAVATED AND THE LEAK CONFIRMED TO BE ON OUR PIPELINE. A VETICAL CRACK IN THE PIPE RAN FROM THE 6 O'CLOCK TO THE 12 O'CLOCK POSITION. THE CRACK WAS IN A WRINKLE BEND THAT ALSO RAN FROM THE 6 O'CLOCK TO 12 O'CLOCK POSITION. THE LINE WAS REPAIRED AND PLACED BACK IN SERVICE MAY 13, 2005.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050063 | 2005-06-06 15:37 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE COMPANY | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1735 | 2005-05-10 | 2005 | CLINTON | CUSTER | OK |  | N/A |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 907124.8279 | 2015603.4878 | 0 | 0 | 1500000 | 2015603.4878 | 0 | 0 | NO | NO | NO | YES | 1 | PRECAUTIONARY | 4 | 30 | 758317 | 2005-05-10 |  |  | NO | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | N/A | STEEL |  | NO | NO | NO | COMPRESSOR | [6 empty] | N/A | N/A | N/A |  | OTHER | THIRD-PARTY FACILITY (UNDERGROUND) |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FAILURE OF A THIRD-PARTY GATHERING FACILITY IN CLOSE PROXIMITY TO ANR CUSTER COMPRESSOR STATION FACILITIES. |  | THE FAILURE OF THE THIRD-PARTY'S FACILITY RESULTED IN A NON-JURISDITIONAL GAS RELEASE AND FIRE, WHICH CAUSED DAMAGE TO ANR'S FACILITIES. DUE TO THE ADJACENT PROXIMITY OF ANR'S FACILITIES TO THE THIRD PARTY RELEASE, AND MEDIA COVERAGE OF THE SITE, ANR IS SUBMITTING THIS REPORT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050064 | 2005-06-02 | SUPPLEMENTAL FINAL | 2748 |  | CONSUMERS ENERGY | 1945 W PARNALL ROAD | JACKSON | JACKSON | MI | 49201 | 2220 | 2005-05-01 | 2005 | ORION | OAKLAND | MI | 48611 | SQUIRREL ROAD | 1210+49 | 42.7139 | 83.2195 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1400000 | 772071.8979 | 1407170.6279 | 500000 | 197808.5352 | 900000 | 1209362.0927 | 0 | 0 | YES | NO | NO | YES | 650 | THREAT TO THE PUBLIC | 1 | 28 | 757387 | 2005-05-01 | 692 | 790 | NO | YES | NO | NO | NO | NO | ALAN M. CHICHESTER - GAS REGULATORY SERVICES ENGINEER | 9897915841 | ALAN.CHICHESTER@CMSENERGY.COM | TRANSMISSION | OTHER | SADDLE TEE CONNECTION, PIPE ADJACENT TO WELD | STEEL |  | NO | NO | NO | OTHER | VALVE SITE | 1951 | 22 | 0.28 | API 5L X-52 | 1328 | ERW |  | YOUNGSTOWN SHEET & TUBE COMPANY | 1951 | UNDER GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE INCIDENT WAS THE RESULT OF EXCESSIVE STRESS PLACED ON THE SADDLE FITTING DURING CONSTRUCTION OF A LAUNCHER/RECEIVER INSTALLATION. |  | DUE TO REQUIREMENTS IN 49-CFR-192 SUBPART O - PIPELINE INTEGRITY, WORK WAS UNDERWAY TO ADD PERMANENT INTERNAL INSPECTION DEVICE LAUNCHERS/RECEIVERS AT THE SQUIRREL ROAD VALVE SITE. THE OUTAGE BEGAN ON TUESDAY APRIL 26, 2005, WHEN THE LINE WAS ISOLATED AND REMOVED FROM SERVICE. FACILITY INSTALLATION WAS ESSENTIALLY COMPLETED ON FRIDAY 29, 2005 AND THE LINE WAS RETURNED TO SERVICE ON SATURDAY APRIL 30, 2005. THE LINE WAS OPERATING AT APPROXIMATELY 692 PSIG, (790 MAOP). CONSUMERS ENERGY'S GAS CONTROL RECEIVED NOTIFICATION OF BLOWING GAS AT 2220 HOURS, MAY 1, 2005. CREWS WERE DISPATCHED AND THE EMERGENCY WAS MITIGRATED BY 2348 HOURS, MAY 1, 2005. A WELDED SADDLE TEE CONNECTION BETWEEN A 22-INCH LINE AND A 12-INCH LINE SEPARATED. THERE WERE NO INJURIES BUT THE VALVE SITE ITSELF EXPERIENCED DAMAGE. DAMAGED MATERIALS ARE BEING REPLACED TO ALLOW THE FACILITY TO BE RETURNED TO SERVICE. THE CAUSE OF THE FAILUE WAS DUE TO EXCESSIVE STRESS BEING PLACED ON THE SADDLE FITTING DURING LAUNCHER/RECEIVER CONSTRUCTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050065 | 2005-06-13 10:58 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE COMPANY OF AMERICA | 500 DALLAS STREET #1000 | HOUSTON | HARRIS | TX | 77002 | 202 | 2005-05-13 | 2005 | MARSHALL | HARRISON | TX | 75672 | 438 | 23069+15.7 | 32 23 51 | 94 26 09 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 8 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87500000 | 52647134.3717 | 115870256.6651 | 1800000 | 712110.7266 | 700000 | 940614.961 | 85000000 | 114217530.9775 | NO | YES | NO | YES | 40 | PRECAUTIONARY | 3 | 30 | 758574 | 2005-05-13 | 824 | 858 | NO | NO | YES | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 36 | 0.33 | 5LX65 | 65000 | FLASH WELD |  | AO SMITH | 1967 | UNDER GROUND |  | 60 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | SCC | STRESS CORROSION CRACKING |  | YES | 1967 | NO | [57 empty] | PIPE SECTION FAILED FROM NEAR NEUTRAL / LOW PH STRESS CORROSION CRACKING (SCC)
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050066 | 2005-06-14 | ORIGINAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION LP | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 900 | 2005-05-31 | 2005 | WIND RIDGE | GREENE | PA | 15380 | MILE POST 731.06 | 38600+22 | 39.8942 | 80.4353 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK CAUSED BY TRACKHOE HITTING PIPE NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 63783.1603 | 55386.3899 | 140000 | 55386.3899 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 35 | 760452 | 2005-05-31 | 858 | 1000 | NO | NO | NO | NO | YES | NO | DWAYNE TESCHENDORF, PRINCIPAL ENGINEER | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | OTHER | 2-INCH PIPE NIPPLE & THREADOLET | STEEL |  | NO | NO | NO | PIPELINE | [10 empty] | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | A COMPANY CONTRACTOR WAS UNCOVERING TEXAS EASTERN 30-INCH LINE 10 WHEN THE TRACKHOE OPERATOR KNOCKED A 2-INCH PIPE NIPPLE AND THREADOLET OFF THE 30-INCH PIPELINE RESULTING IN A NATURAL GAS LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050067 | 2005-06-14 | ORIGINAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION LP | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 930 | 2005-05-17 | 2005 | BEDFORD | BEDFORD | PA | 15522 | MILE POST 1230.60 |  | 39.9307 | 78.5861 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204100 | 122817.9125 | 270369.1617 | 4100 | 1622.03 | 200000 | 268747.1317 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 10 | 759001 | 2005-05-17 | 817 | 1000 | NO | YES | NO | NO | NO | NO | DWAYNE TESCHENDORF, PRINCIPAL ENGINEER | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION |  |  |  |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | COMPANY CONTRACTOR DAMAGED ESD SYSTEM INADVERTENTLY ACTIVATING ESD SYSTEM |  | A CONTRACTOR WORKING FOR THE PIPELINE COMPANY DAMAGED THE ESD SYSTEM WHILE CONDUCTING UNRELATED WORK CAUSING THE ESD SYSTEM TO ACTIVATE. THE NATURAL GAS RELEASED BY THE ESD ACTIVATION WAS IGNITED BY THE CONTRACTOR'S WATER PUMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050068 | 2005-06-24 10:35 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 2317 | 2005-05-26 | 2005 | DELHI | RICHLAND | LA | 71232 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FAILURE OF COMPRESSOR ENGINE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15002650 | 9072455.6031 | 20157083.2636 | 2650 | 1048.3852 | 15000000 | 20156034.8784 | 0 | 0 | NO | NO | YES | NO | 0 |  | 1 | 45 | 760116 | 2005-05-27 | 646 | 1008 | YES | NO | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | TURBINE COMPRESSOR ENGINE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1971 | [8 empty] | INSIDE/UNDER BUILDING |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FIRST STAGE REACTION TURBINE FAILED LEADING TO AN OUT-OF-BALANCE ROTOR. THIS LEAD TO CATASTROPHIC FAILURE OF THE REACTION TURBINE. |  | UNIT HAD GONE DOWN ON ALARM. COMPANY RESPONDER CLEARNED ALARMS, AND STARTED UNIT. UNIT WENT THROUGH WARM UP, AND WENT ON LINE TO MAINTAIN LINE PRESSURE. COMPANY PERSON PLACED UNIT IN AUTOMATIC START MODE, AND WAS LEAVING BUILDING WHEN THE UNIT POWER TURBINE FAILED. TURBINE FAILURE RESULTED IN DAMAGE TO UNIT AND ADJOINING UNIT. FAILED UNIT CAUGHT FIRE. COMPANY PERSON HIT ESD FOR APPROPRIATE ENGINE BLOCKS. INVESTIGATION REVEALED A SEGMENT OF THE FIRST STAGE REACTION TURBINE DISK BROKE AWAY CAUSING THE ROTOR TO BECOME SEVERALLY OUT OF BALANCE. THIS SITUATION RESULTED IN THE COMPLETE CATASTROPHIC FAILURE OF THE REACTION TURBINE. THE INITIAL CAUSE OF THE ROTOR DISK FAILURE WAS SHOWN TO BE DUE TO A LOW CYCLE FATIGUE CRACK RESULTING OVER SEVERAL CYCLES. THIS CRACK WAS INITIATED BY THE FAILURE OF ONE OF THE LOWER SEAL RING SEGMENTS, WHICH CAME UNFASTENED AND RUBBED AGAINST THE ROTOR DISK. THE ROOT CAUSE OF THIS FAILURE HAS BEEN DETERMINED TO BE THE RELEASE OF ONE OF THE LOWER SEAL RING SEGMENTS FROM ITS FASTENERS. NO DEFINITIVE REASON CAN BE DETERMINED FOR THE RELEASE OF THESE FASTENERS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050069 | 2005-06-24 11:00 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 910 | 2005-06-18 | 2005 | [6 empty] | 9142.59 | 2820.78 | OFFSHORE |  | EUGENE ISLAND | 292B | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 90712.4828 | 201560.3488 | 0 | 0 | 150000 | 201560.3488 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 762577 | 2005-06-18 |  | 1250 | NO | NO | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 18 | 0.41 |  | 52000 |  |  |  | 1971 | OTHER | RISER IN UNDERWATER CASING |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | INITIAL EXAMINATION DETERMINED LEAK IS ON 18" RISER INSIDE A FILLED CASING ADJACENT TO PLATFORM. |  | LEAK IN RISER ADAJACENT TO EUGENE ISLAND PLATFORM 292B WAS CONFIRMED ON 6/18/05. INITIAL EXAMINATION DETERMINED LEAK IS ON 18" RISER INSIDE A FILLED CASING ADJACENT TO PLATFORM. REPAIR BY REPLACING PIPE SECTION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050070 | 2005-06-24 13:19 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1330 | 2005-05-31 | 2005 | TRINIDAD | LAS ANIMAS | CO |  | MP 151A+11.5 |  | N 37.14239 | W 104.65458 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 31850.9484 | 39936.8884 | 50000 | 19780.8535 | 15000 | 20156.0349 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 |  | 760493 | 2005-05-31 | 1200 | 1308 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1994 | 10 | 0.19 | API | 52000 | ERW |  | CALIF.STEEL IN. | 1994 | UNDER GROUND |  | 57 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | A THIRD PARY EXCAVATOR WAS INSTALLING A PLATIC GAS LINE THAT CROSSED COLORADO INTERSTATE GAS' (CIG) RIGHT-OF WAY. THE CONTRACTOR DID NOT FILE A UTILITY LOCATE NOTICE. CIG WAS NOT AWARE OF THE EXCAVATION. THE EXCAVATOR STRUCK AND PUNCTURED CIG'S 10-INCH 151A PIPELINE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050072 | 2005-06-30 19:04 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LP | 2707 NORTH LOOP WEST | HOUSTON | HARRIS | TX | 77382 |  | 2005-06-30 | 2005 | [8 empty] | OFFSHORE |  | HIA | 283 |  | YES | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 108705.8235 | 240924.3 | 1000 | 395.6171 | 179000 | 240528.6829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 76058 | 2005-05-31 | 850 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7138032494 | JMCDONALD@EPROD.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | [5 empty] | 12 INCH VALVE |  |  | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | YES | 7 | 1 | 1981 | WATER |  | 24 | 2160 | [12 empty] | AFTER 25 YEARS OF OPERATION, CONNECTION OF VALVE GREASE FITTING ON VALVE STARTED TO LEAK. SMALL BUBBLES WERE EVIDENT AND LEAK WAS MINOR IN NATURE. COST OF PROJECT HIGH DUE TO NEED FOR DIVERS AND SUPPORTING VESSELS TO MAKE REPAIR. VALVE HAD BEEN TESTED WITH PIPELINE BACK IN 1980 TO A TEST PRESSURE OF 2160 PSIG. DATA OBTAINED FROM MMS RECORDS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050073 | 2005-07-15 15:46 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1130 | 2005-06-24 | 2005 |  | DONA ANA | NM |  | 243+787, 28.5 TO 30 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106000 | 54259.1996 | 79860.153 | 66000 | 26110.7266 | 40000 | 53749.4263 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 763290 | 2005-06-24 | 778 | 837 | YES | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 26 | 0.29 | API | 52000 | EFW |  | A.O. SMITH | 1947 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDER INVESTIGATION | YES | 1970 | NO | [57 empty] | EL PASO NATURAL GAS PERSONNEL WERE IN THE PROCESS OF RUNNING THE INSTRUMENTED PIG ON LINE 1100, IN NEW MEXICO WHEN SEVERAL ANOMALIES IN THE PIPE WERE IDENTIFIED. AFTER EXCAVATION AND FURTHER EXAMINATION, A SMALL LEAK WAS DISCOVERED. EXTERNAL CORROSION IS THE SUSPECTED CAUSE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20050074 | 2005-07-15 15:20 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 2153 | 2005-06-18 | 2005 | CARTHAGE | PANOLA | TX | 75633 | N/A | N/A | 32 08' 22.6 | 094 20' 14.5 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 300380 | 181598.0913 | 403271.0321 | 380 | 150.3345 | 300000 | 403120.6976 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 37 | 762636 | 2005-06-18 | 789 | 1000 | YES | NO | NO | NO | NO | NO | JACK L ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | COMPRESSOR | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1980 | [6 empty] | JOY | 1980 | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | ROOT CAUSE-COMPRESSOR VALVE BROKE FALLING INTO CYLINDER. PISTON DROVE PIECE TO TOP OF CYLINDER RESULTING IN AN OVERSTRESS SITUATION. THE OVERSTRESS SITUATION LEAD TO CRACKING OF TWO CASTY IRON DISTANCE PIECES. GAS ESCAPED PAST THE CYLINDER ROD PACKING AND IGNITED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050075 | 2005-07-18 16:12 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 840 | 2005-07-04 | 2005 | MONTICELLO | JONES | IA | 52310 | 9.557 | 50460 | 42.2948 | -91.2019 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93538 | 53089.227 | 103583.0649 | 23317 | 9224.6032 | 70221 | 94358.4617 | 0 | 0 | NO | NO | NO | NO | 0 |  | 12 | 0 | 764359 | 2005-07-04 | 800 | 960 | NO | NO | NO | YES | NO | NO | JOHN GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 6 | 0.19 | 5LX | 42000 | ERW |  |  |  | UNDER GROUND |  | 39 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | GOUGE | [11 empty] | MATERIAL DEFECT |  | YES | NO
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20050076 | 2005-07-21 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION, LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 1115 | 2005-07-11 | 2005 | WHEATLAND | KNOX | IN | 47597 | 860 |  | 38.6749697 | -87.3683982 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | OUTSIDE PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 11 | 30 | 765109 | 2005-07-11 | 500 | 600 | NO | NO | NO | NO | NO | NO | MICHAEL K NANCE, MANAGER OF GAS CONTROL | 2706886822 | MIKE.K.NANCE@TXGT.COM | TRANSMISSION | OTHER | 1 | STEEL |  | NO | NO | NO | PIPELINE | [13 empty] | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE INDIVIDUAL WHO WAS IN THE AUTOMOBILE COLLISION WAS RELEASED FROM THE LOCAL EMERGENCY CARE FACILITY WITHIN TWO HOURS WITH NO REPORTABLE INJURIES. DAMAGE TO TEXAS GAS FACILITIES WAS LIMITED TO THE IRON PIP BARRIER SURROUNDING THE CUSTOMER FARM TAP (LESS THAN ONE THOUSAND DOLLARS IN VALUE). THE LDC OWNING THE MEASUREMENT FACILITY HAD SERVICE RESTORED TO THE TWO HORSEHOLDS WITHIN 24 HOURS. CORRECTED LAT/LONG DATA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050077 | 2005-07-25 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 2015 | 2005-06-30 | 2005 | LAWRENCE | DOUGLAS | KS | 66044 | 14/1072 | SERIES 130 STATION 681+69 | 38.81818 | -95.241616 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192163 | 103635.9655 | 178285.1378 | 84305 | 33352.4971 | 102858 | 138213.9624 | 5000 | 6718.6783 | NO | NO | NO | YES | 4 | PRECAUTIONARY | 2 | 0 | 764055 | 2005-06-30 | 520 | 450 | NO | NO | YES | NO | NO | YES | DAVID SINCLAIR, SR. PIPELINE SAFETY SPECIALIST | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 20 | 0.31 | UNKNOWN | 24000 | FURNACE LAP WELD |  | SPANG-CHALFONT | 1929 | UNDER GROUND |  | 24 | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 0 |  |  | ON JUNE 30TH AT APPROXIMATELY 7:52PM GAS CONTROL RECEIVED AN ALARM OF AN OVERPRESSURE SITUATION ON THE TOPEKA 20" AT OTTAWA STATION. OPERATIONS PERSONNEL WERE CONTACTED AT 8:05PM AND ARRIVED TO OTTAWA STATION AT 8:09PM AND FOUND LINE PRESSURE ON THE TOPEKA SYSTEM HAD EXCEEDED IT'S MAOP OF 450 PSIG DUE TO A LIGHTENING STORM CAUSING THE WORKING REGULATOR 1137 R TO FAIL OPEN. THE MONITOR REGULATOR 1137 RM FAILED TO OPERATE EXPOSING LINE ES TO A PRESSURE OF 679 PSIG. IT WAS LATER DETERMINED THE MONITOR REGULATOR FAILURE WAS DUE TO PNEUMATIC CONTROLLER'S SUPPLY VALVE BEING SHUT. AT 8:15 THE TOPEKA 20" RUPTURED APPROXIMATELY 3 MILES SOUTH OF LAWRENCE KANSAS. RICHARD HANES ARRIVED ON SITE OF RUPTURE AT 9:09PM, AND REPORTED THAT GAS WAS BLOWING AT MAINLINE PRESSURE AND THERE WAS NO FIRE. AT 9:42PM THE BALDWIN MAIN LINE GATE WAS CLOSED, SHUTTING IN THE RUPTURED SECTION. A CHECK VALVE AT HASKELL BOTTOMS NEAR LAWRENCE PREVENTED LOSS OF PRESSURE ELSEWHERE ON OUR SYSTEM.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050078 | 2005-07-26 12:41 | SUPPLEMENTAL FINAL | 18667 |  | PLAINS EXPLORATION & PRODUCTION COMPANY | 5640 S. FAIRFAX AVE | LOS ANGELES | LOS ANGELES | CA | 90056 | 2100 | 2005-06-28 | 2005 | LOS ANGELES | LOS ANGELES | CA | 90019 | 0.2 MILES |  | 34.0715218 | -118.3766479 | ONSHORE | 4 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 74142.8086 | 146242.078 | 30000 | 11868.5121 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 763780 | 2005-06-28 | 120 | 275 | NO | NO | NO | NO | NO | NO | BOB MARSALEK | 8059348223 | BMARSALEK@PLAINSXP.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 8 | 0.32 | GRADE B | 35000 | SEAMLESS |  |  |  | UNDER PAVEMENT |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1980 | NO | [57 empty] | THE EXTERNAL CORROSION OCCURRED 6" FORM A BUTT WELD WHERE THE EXTERNAL COATING APPLIED IN THE FIELD. THE CORROSION OCCURRED ON PIPE IN CASING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050079 | 2005-07-27 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC COMPANY | PO BOX 770000 MAIL CODE H15E | SAN FRANCISCO | SAN FRANCISCO | CA | 94177-0001 | 1200 | 2005-06-28 | 2005 | SHAFTER | KERN | CA | 93263 | 297.7333 |  | 35.48746 | -119.40336 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204000 | 104873.6471 | 156555.3694 | 124000 | 49056.5167 | 80000 | 107498.8527 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 55 | 763750 | 2005-06-28 | 740 | 757 | NO | NO | YES | NO | NO | NO | CHARLES CHANG, REGULATORY COMPLIANCE - GAS OPERATIONS | 9259744248 | CYC8@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 34 | 0.34 | X52 | 52000 | DSAW |  |  |  | UNDER GROUND |  | 40 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | AGRICULTURAL OPERATIONS | YES | 5 | 9 |  | ONE-CALL SYSTEM | YES | STAKES | YES | ACCURATE | YES | [36 empty] | THE EXCAVATOR, JORDY WISE, WORKING FOR GARNER FARMS, WAS PLOWING/RIPPING A FIELD WITH A D8 TRACTOR WHEN HE STRUCK AND DAMAGED 34 INCH LINE 300B CAUSING GAS TO ESCAPE. THERE WAS A USA ONE-CALL NOTIFICATION TAG FOR THE AREA NAD THE SITE WAS ACCURATELY MARKED BY PG&E WITHIN THE PROPER TIME LIMIT, HOWEVER THE USA TICKET HAD EXPIRED ON JUNE 6, 2005. THE EXCAVATOR WAS AWARE OF THE LOCATION OF THE 34 INCH PIPELINE BUT FAILED TO FOLLOW PROPER PROCEDURE BY HAVING A ACTIVE USA TICKET AND STOPPING EXCAVATING/RIPPING 5 FEET OF THE PIPELINE. UPDATED BY PHMSA ON 12/16/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050080 | 2005-07-29 16:29 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1330 | 2005-07-02 | 2005 | DOWNSVILLE | UNION | LA | 71241 | FM-38 | 310+60 | +32.710247 | -92.407023 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK DUE TO CAR HITTING RE-609 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19233 | 11025.7308 | 21995.6546 | 4059 | 1605.8097 | 15174 | 20389.8449 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 31 | 764221 | 2005-07-02 | 150 | 175 | NO | NO | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | RURAL EXTENION | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1982 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE A STATE HIGHWAY WAS CLOSED BY EMERGENCY RESPONDER PERSONNEL.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050081 | 2005-08-01 11:51 | ORIGINAL | 31130 |  | DUKE ENERGY FIELD SERVICES, LP - EASTRANS LIMITED PARTNERSHIP | 370 17TH STREET, SUITE 2500 | DENVER | DENVER | CO | 80202 | 1615 | 2005-07-11 | 2005 | HENDERSON | RUSK | TX | 75652 |  |  | 32 17 51.121 N | 94 43 51.863 W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91594 | 46890.4706 | 69041.0531 | 56994 | 22547.7993 | 34600 | 46493.2538 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 765146 | 2005-07-11 | 850 | 1264 | YES | NO | NO | NO | NO | NO | CINDY LOPEZ | 3615848518 | CALOPEZ@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.24 | X-60 | 1763 | ERW |  |  |  | UNDER GROUND |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDER REVIEW; UNKNOWN AS OF DATE OF THIS REPORT | YES | 1989 | NO | [57 empty] | THIRD PARTY NOTIFIED DUKE ENERGY FIELD SERVICES - EASTRANS LIMITED PARTNERSHIP ABOUT POSSIBLE LEAK (HISSING SOUND). LINE WAS BLOWN DOWN AND EXPOSED. SMALL INTERNAL CORROSION PINHOLE LEAK WAS DISCOVERED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050082 | 2005-08-02 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFT ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 1134 | 2005-06-29 | 2005 | VENTURA | VENTURA | CA |  | MP #12.34 |  | 34.29293 | 119.14254 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 40840.9331 | 84580.3102 | 10000 | 3956.1707 | 60000 | 80624.1395 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 26 | 763875 | 2005-06-29 | 625 | 780 | NO | NO | NO | NO | YES | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1944 | 18 | 0.31 | X 45 | 50 |  |  |  | 1944 | UNDER GROUND |  | 22 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | FARMING | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | DOT/CPUC REPORTABLE INCIDENT. 11832 DARLING ROAD, VENTURA. ON JUNE 29, 2005 AN 18" NATURAL GAS TRANSMISSION PIPELINE OPERATING AT APPROXIMATELY 625 POUNDS WAS DAMAGED BY A FARMER PERFORMING GRADING WORK. WHILE GRADING FIELDS FOR PLANTING, THE EXCAVATOR STRUCK AND DAMAGED THE MAIN, RESULTING IN FIVE OUTAGES. NO INJURIES OR PUBLIC PROPERTY DAMAGE RESULTED FROM THIS INCIDENT. ALL REPAIRS HAVE BEEN COMPLETED, AND FIVE CUSTOMERS WHO WERE OUT OF GAS HAVE BEEN RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT THE EXCAVATOR DID NOT HAVE A USA TICKET, BUT WAS AWARE OF PIPING DUE TO PERMANENT MARKERS IN THE AREA. THE INCIDENT WAS REPORTED TO DOT UNDER INCIDENT #763875, BASED UPON DAMAGE TO COMPANY FACILITIES EXCEEDING $50K. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050083 | 2005-08-11 12:03 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1757 | 2005-08-10 | 2005 | LAKE ELMO | WASHINGTON | MN | 55042 | 0.160 | 8+44 | 44.9997532 | -92.8721500 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 8027.1571 | 13519.2048 | 7000 | 2769.3195 | 8000 | 10749.8853 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 768657 | 2005-08-10 | 478 | 1050 | NO | YES | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING | [7 empty] | RELIEF | FISHER | 1975 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | A RELIEF VALVE AT THE LAKE ELMO TOWN BORDER STATION (AKA ST PAUL 1R) BEGAN VENTING AT 6 P.M. THE CAUSE OF THE RELIEF VALVE ACTIVATING IS STILL UNDER INVESTIGATION. PIGGING OF THE PIPLINE THAT SERVES THE LAKE ELMO BRANCH LINE, MNM86501-M450B FARMINGTON TO NORTH BRANCH, OCCURRED THE DAY BEFORE. IF THIS WAS A CONTRIBUTING FACTOR, IT HAS NOT BEEN DETERMINED YET. THE NUMBER 1 REGULATOR WAS DISASSEMBLED ON 8/11/05. A 1/4" PORTION OF THE RING SEAL WAS FOUND MISSING AND METAL SHAVINGS WERE FOUND INSIDE THE REGULATOR. A NEW RING SEAT WAS ORDERED AND WAS INSTALLED UPON DELIVERY. THE STATION DOES NOT HAVE INLET STRAINERS ON THE REGULATOR RUNS. MATERIAL WAS PURCHASED AND STRAINERS WERE INSTALLED. THIS INCIDENT DID NOT MEET THE CRITERIA OUTLINED IN 192.5 AND A LETTER TO RESCIND IT WAS SENT ON 9/19/05. 9/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050084 | 2005-08-12 15:10 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE-TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1030 | 2005-07-15 | 2005 | FRAZER | MONTGOMERY | PA | 19403 | 1730.89 | 3080+53 | 40.11136N | 75.45371W | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102000 | 47962.1471 | 49834.1271 | 92000 | 36396.7705 | 10000 | 13437.3566 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 10 | 765657 | 2005-07-15 | 700 | 800 | NO | YES | NO | NO | NO | NO | KEVIN WILSON | 7132152902 | J.KEVIN.WILSON@WILLIAMS.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 2 | [7 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE LEAK WAS THE RESULT OF A FATIGUE CRACK, CAUSED BY VIBRATION DURING THE BLOWDOWN OF OUR PIPELINE.THIS INITIATED AT A METALLURGICAL NOTCH AT THE TOE OF THE BUTT-WELD CONNECTING A 2-INCH VALVE TO A TEE (12-INCH).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050085 | 2005-12-20 | SUPPLEMENTAL FINAL | 8070 |  | INDIANA GAS CO INC | 20 NW FOURTH STREET | EVANSVILLE | VANDERBURGH | IN | 47708-1724 | 1453 | 2005-07-28 | 2005 | BROOKSTON | WHITE | IN | 47923 | N/A | N/A | 40.5936508 | -87.0236893 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 16 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429570 | 243932.3583 | 476476.7051 | 106265 | 42040.248 | 108520 | 145822.1937 | 214785 | 288614.2634 | NO | NO | NO | NO | 0 | [7 empty] | NO | NO | NO | NO | NO | NO | JOHN A SPINKS COMPLIANCE SUPERVISOR | 9374401844 | JASPINKS@VECTREN.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM |  |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | [8 empty] | UNDER GROUND |  | 54 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | FIELD DRAINAGE TILE | NO |  |  |  |  | YES |  |  | ACCURATE | [37 empty] | A CONSTRUCTON CREW WAS EXCAVATING FOR FIELD DRAINING TITLE INSTALLATION WHEN THEIR TRENCHER CONTACTED VECTREN'S 16 INCH GAS TRANSMISSION PIPELINE ALLOWING GAS TO BE RELEASED TO THE ATMOSPHERE. THE TRENCHER WAS PUSHED ON ITS SIDE BY THE FORCE OF THE ESCAPING GAS WITH NOT RESULTING INJURIES. UPDATED BY PHMSA ON 1/7/2016 PER OPERATOR'S MARK UP (PART A, QUESTION 4 - TYPE OF LEAK OR RUPTURE; AND PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050086 | 2005-08-25 14:18 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINES - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1820 | 2005-08-06 | 2005 |  |  |  |  | 8.77 |  | 28 36.780' | 95 13.544 | OFFSHORE |  | GALVESTON | 394 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 80271.571 | 135192.0476 | 70000 | 27693.1949 | 80000 | 107498.8527 | 0 | 0 | NO | NO | NO | NO | 0 |  | 168 | 10 | 768193 | 2005-08-06 | 1060 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12 | 0.31 | API 5L | 52000 | SEAMLESS | ANSI 600 | USS TUBULAR | 1990 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1990 | NO | [57 empty] | THE LEAK WAS DISCOVERED OFFSHORE AT GA 394 AND REPORTED TO WGP GAS CONTROL. DIVERS DISCOVERED A PINHOLE LEAK AT THE 7:00 POSITION. THE LEAK WAS CLAMPED AND THE PIPELINE WAS RETURNED TO SERVICE. THE PIPELINE SEGMENT IS SCHEDULED FOR ABANDONMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050087 | 2005-08-26 11:56 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE-TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 940 | 2005-08-03 | 2005 | SPRING | HARRIS | TX | 77014 | 339.82 | 17942+53 | N30.098204 | W95.301551 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274000 | 156901.2715 | 312244.5737 | 59000 | 23341.4072 | 40000 | 53749.4263 | 175000 | 235153.7402 | NO | YES | NO | NO | 0 |  | 4 | 30 | 767808 | 2005-08-03 | 550 | 780 | NO | NO | NO | NO | YES | NO | J.K. WILSON | 7132152902 | J.KEVIN.WILSON@WILLIAMS.COM | TRANSMISSION | OTHER | IGNITION SOURCE |  |  | NO | NO | NO | PIPELINE | [10 empty] | OTHER | VALVE SITE |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | GAS BEING VENTED TO ATMOSPHERE IGNITED DURING PLANNED BLOWDOWN OPERATIONS |  | THE INCIDENT INVESTIGATION CONCLUDED THAT DURING A PLANNED GAS BLOWDOWN FOR A PIPELINE ASSESSMENT (DIG) THE GAS THAT WAS BEING BLOWN DOWN WAS INADVERTENTLY REDIRECTED BY A PORTABLE SILENCER TOWARDS AN ELECTRICAL IGNITION SOURCE, THUS CREATING IGNITION. THE INVESTIGATION ALSO REVEALED THAT THERE WAS NO DAMAGE TO THE PIPELINE SYSTEM. THE OPERATOR PROPERTY DAMAGE/LOSS (COMPANY TRUCK AND HEAVY EQUIPMENT) AMOUNT IN DOLLARS MET THE PHMSA REPORTING CRITERIA, THEREFORE AN INCIDENT REPORT WAS INITIATED AND SUBMITTED TO PHMSA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050088 | 2005-08-29 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION INC. | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302 | 1640 | 2005-07-30 | 2005 | LOST CREEK | HARRISON | WV | 26385 |  |  | N39 8' 45.1" | W80 21' 8.4" | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 541000 | 246923.8229 | 216873.1908 | 538000 | 212841.9839 | 3000 | 4031.207 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 767384 | 2005-07-03 | 969 | 1050 | NO | YES | NO | NO | NO | NO | SHAWN A. MILLER | 3046273404 | SHAWN_A_MILLER@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1976 | 20 | 0.28 | API 5L | 52000 | SEAMLESS |  |  |  | UNDER GROUND |  | 60 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | ON SATURDAY, 7-30-05 @ APPROXIMATELY 4:30 TO 4:40 PM LINE TL-414, A LOST CREEK STORAGE FIELD MAIN LINE, FAILED WHILE OPERATING IN STORAGE INJECTION SERVICE. THE PIPELINE WAS OPERATING AT A PRESSSURE OF ABOUT 969 PSIG, BASED ON A MECURY ER METER APPROXIMATLEY 100 YARDS FROM THE FAILURE SITE. LINE TL-414 IS A 1050 PSI MAOP PIPELINE THAT LEAVES LIGHTBURN STATION AS A 30" PIPELINE AND DECREASES IN DIAMETER AS IT MOVES OUT INTO THE STORAGE FIELD. THE PIPELINE IS 20" IN DIAMETER AT THE SITE OF THE FAILURE AND REDUCES TO 16" APPROXIMATELY 400' ON THE FIELD SIDE OF THE FAILURE. ONCE NOTIFIED OF THE PIPELINE FAILURE OPERATIONS PERSONNEL WERE DISPATCHED TO CLOSE ISOLATION VALVES ON BOTH ENDS OF THE 20" PIPELINE SECTION AS WELL AS VALVES ON THREE BRANCH LINES THAT TIE IN TO TL-414 WITHIN THE DAMAGED SECTION OF PIPELINE. THE FIRST OF THESE VALVES WAS CLOSED AT APPROXIMATLEY 5:05 PM, TWENTY FIVE TO THIRTY FIVE MINUTES AFTER THE FAILURE OCCURRED. THE FINAL VALVE REQUIRED TO TOTALY ISOLATE THE SEGMENT OF DAMAGED LINE WAS CLOSED AT 5:57 PM. AS A RESULT OF THE FAILURE A SIGNIFICANT HOLE WAS BLOWN IN THE GROUND SURROUNDING THE PIPLINE ENDS BY THE ESCAPING GAS. A SEGMENT OF PIPE APPROXIMATELY 4 TO 5 FEET IN LEGTH WAS FOUND AFTER THE FAILURE ABOUT 234 FEET FROM THE LINE IN A WOODED AND BRUSHY AREA ADJACENT TO THE RIGHT OF WAY. THE FAILURE OCCURRED IN AN AREA THAT HAS BEEN PRONE TO GROUND MOVEMENT (SLIPS) FOR SEVERAL YEARS. SEVERAL ATTEMPTS HAVE BEEN MADE TO REPAIR SLIPS IN THE AREA WITH SOME LIMITED SUCCESS, HOWEVER WHEN THE MOST RECENT SLIP WAS IDENTIFIED IN LATE 2004 PLANS WERE MADE TO RELOCATE LINE TL-414 TO ANOTHER LOCATION IN AN ATTEMPT TO ELIMINATE THE RECURRING PROBLEM. WORK WAS SCHEDULED TO START ON THE RELOCATION PROJECT IN AUGUST 22, 2005.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050089 | 2005-09-01 09:40 | ORIGINAL FINAL | 1007 |  | KINDER MORGAN INTERSTATE GAS TRANSMISSON | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1510 | 2005-06-22 | 2005 | FRANKLIN | FRANKLIN | NE | 68838 |  | 1835 + 32 | 040 09 01 | -098 53 13 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178000 | 83780.5383 | 87485.9731 | 160000 | 63298.7313 | 17000 | 22843.5062 | 1000 | 1343.7357 | NO | NO | NO | NO | 0 |  |  |  | 763094 | 2005-06-22 | 542 | 720 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.25 | 5LX | 35000 |  |  |  |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | NO | [40 empty] | PRIVATE CONTRACTOR WAS LEVELING A FIELD FOR AGRICULTURAL PURPOSES AND WAS WORKING UNDER THE DIRECTION OF THE LANDOWNER. CONTRACTOR DID NOT MAKE A ONE-CALL AND DUG INTO KMIGT PIPELINE CAUSING AN UNSCHEDULED RELEASE AT THE POINT OF CONTACT. NO INJURIES WERE RECORDED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050090 | 2005-09-08 14:47 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 931 | 2005-08-18 | 2005 | SANDYVILLE | JACKSON | WV | 25275 |  | 6+53 | 38.87972 | 81.69583 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90440 | 54627.951 | 121110.2808 | 440 | 174.0715 | 90000 | 120936.2093 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 769694 | 2005-08-19 | 1650 | 1700 | NO | YES | NO | NO | NO | NO | STEVEN BURNLEY | 6077210112 | SBURNLEY@NISOURCE.COM | TRANSMISSION | OTHER | DRIP | STEEL |  | NO | NO | NO | OTHER | STORAGE WELL LINE | 1998 | 12 | 0.5 | API 5L | 65000 | SMLS |  | UNKNOWN | 1997 | UNDER GROUND |  | 96 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | CO2 CORROSION PRODUCT INDICATION | YES | 1998 | NO | [57 empty] | A LEAK WAS FOUND ON LINE X59 W7338 IN THE RIPLEY STORAGE FIELD. UPON SUBSEQUENT EXCAVATION THE LEAK WAS IDENTIFIED TO BE ON THE 12-INCH BARREL OF AN UNDERSLUNG DRIP ADJACENT TO THE STORAGE WELL. THE DRIP WAS FOUND TO BE PART FILLED WITH SOLIDS. ANALYSIS OF THE INTERNAL CORROSION CHARACTERISTICS WILL REQUIRE DESTRUCTIVE TECHNIQUES AND THERFORE REPAIR COSTS WILL EXCEED $50K. ANALYSIS YIELDS NO BACTERIAL ACTIVITY AND PRESENCE OF IRON RICH CALCIUM CARBONATE SUGGESTING CO2. CHEMICAL TREATMENTS WERE MODIFIED SHORTLY BEFORE THE EVENT CONSISTENT WITH CO2 IC PREVENTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050091 | 2005-09-08 17:15 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1030 | 2005-08-12 | 2005 |  | PLAQUEMINES | LA |  |  |  | 29*23'11 | 89*22'47 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 58983.4297 | 124892.38 | 10000 | 3956.1707 | 90000 | 120936.2093 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 768836 | 2005-08-12 | 895 | 1100 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 12.75 | 0.31 | API | 46000 | UNKNOWN |  |  | 1957 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1957 | NO | [57 empty] | A LEAK WAS DISCOVERED ON SNG'S 12-INCH BASTIAN BAY LINE, NEAR THE OLGA SUCTION PLATFORM. THE PINHOLE LEAK WAS APPARENTLY THE RESULT OF INTERNAL CORROSION. THE LEAK WAS REPAIRED BY INSTALLING A CLAMP. HOWEVER, THIS PIPELINE, INCLUDING THE SECTION CONTAINING THE LEAK REPAIR HAS BEEN ABANDONED AND IS NO LONGER IN SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050092 | 2005-09-09 09:59 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORPORATION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 245 | 2005-08-24 | 2005 | WASHINGTON | WASHINGTON | PA | 15301 |  | 2145+43 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116200 | 68899.7025 | 147419.3925 | 9200 | 3639.677 | 107000 | 143779.7155 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 45 | 770225 | 2005-08-24 | 465 | 600 | NO | YES | NO | NO | NO | NO | DAVID D. ANDERSON | 7242232766 | DDANDERSON@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 20 | 0.38 | API 5L | 35000 | SEAMLESS |  | NATIONAL TUBE | 1946 | UNDER GROUND |  | 70 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1958 | NO | [57 empty] | THE LEAK WAS DISCOVERED DURING A ROUTINE INSPECTION AT A RAILROAD CASING VENT. THE SECTION OF PIPELINE WAS BLOWN DOWN IMMEDIATELY, AND A PLAN PUT IN PLACE TO REPLACE THE PIPE. EXCAVATION OF THE LEAK AREA REVEALED A LARGE EXTERNAL PIT NEAR THE END OF THE CASING. THE PIPE HAS BEEN REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050093 | 2005-09-12 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFT ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 1530 | 2005-08-13 | 2005 | MORENO VALLEY | RIVERSIDE | CA |  | 154.49 |  | 33.9112N | 117.0632W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 26101.7613 | 28395.769 | 48000 | 18989.6194 | 7000 | 9406.1496 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 768977 | 2005-08-13 | 800 | 687 | NO | YES | NO | NO | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 36 | 0.31 | X-60 | 1040 |  |  |  | 1970 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | VANDALISM | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [65 empty] | SEPTEMBER 12, 2005 CPUC/DOT REPORTABLE INCIDENT JACKRABBIT TRAIL, MORENO VALLEY NARRATIVE ON AUGUST 13, 2005, A 36" TRANSMISSION LINE WAS PUNCTURED BY GUNFIRE FROM UNKNOWN VANDALS. OF FIVE SHOTS THAT STRUCK THE ABOVE-GROUND PIPING, ONE CAUSED A 3/4" PUNCTURE, REQUIRING BLOWDOWN ON THE DAMAGED SECTION FOR REPAIR. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THE PIPING WAS REPAIRED AND PUT BACK INTO SERVICE. NO CUSTOMERS WERE PUT OUT OF SERVICE DUE TO THE DAMAGE OR RESULTING REPAIRS. THIS INCIDENT BECAME REPORTABLE TO THE DOT AND CPUC AT APPROXIMATELY 17:30 WHEN GAS LOSS AND REPAIR ESTIMATES EXCEEDED $50K. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050094 | 2005-09-25 22:57 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1835 | 2005-08-28 | 2005 |  |  |  |  | 523M-102 + 2.68 |  | 28 *41.80' | -91*02.83' | OFFSHORE |  | SHIP SHOAL | 157 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9737000 | 5664715.8084 | 11661776.2251 | 1500000 | 593425.6055 | 8237000 | 11068350.6196 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 770658 | 2005-08-28 | 900 | 1200 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.49 | API | 60000 |  |  | UNKNOWN |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | DURING HURRICANE KATRINA, A SIGNIFICANT PRESSURE DROP WAS NOTICED ON THE SHIP SHOAL BLOCK 198 LINE TO COCODRIE. A LEAK WAS DISCOVERED IN SHIP SHOAL BLOCK 157, AT A SUB-SEA TIE-IN TO A PRODUCER-OWNED PIPELINE. THE DAMAGE HAS BEEN REPAIRED AND THE PIPELINE PLACED BACK INTO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050095 | 2005-09-25 23:24 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 815 | 2005-08-29 | 2005 |  |  |  |  | 524J-201+9.83 |  |  |  | OFFSHORE |  | SOUTH TIMBALIER | 37 |  | YES | NO | INTERSTATE | OTHER | STORM DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 32515.4643 | 69164.8683 | 5000 | 1978.0854 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 770694 | 2005-08-29 | 715 | 1125 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8.63 | 0.5 | API | 35000 | SEAMLESS |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | A SIGNIFICANT PRESSURE DROP WAS NOTICED ON TWO TGP METERS. A LEAK WAS DISCOVERED IN SOUTH TIMBALIER BLOCK 37. TGP'S 524J-200 PIPELINE SUSTAINED EXTERNAL DAMAGE TO THE PIPE'S SURFACE MOST LIKELY DUE TO DEBRIS DRIVEN BY CURRENTS FROM HURRICANE KATRINA. THE DAMAGED SECTION WAS REMOVED AND REPLACED FOR THE LINE TO BE PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050096 | 2005-09-25 23:52 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1350 | 2005-08-30 | 2005 | PORT SULPHUR | PLAQUEMINES | LA | 70083 | MP527-101+ |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR STATION HEAVILY DAMAGED BY KATRINA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65005000 | 39311020.5125 | 87344795.8917 | 5000 | 1978.0854 | 65000000 | 87342817.8063 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 770885 | 2005-08-30 |  |  | NO | NO | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | MULTIPLE DAMAGES TO COMPRESSOR STATION | STEEL |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | TENNESSEE GAS PIPELINE COMPRESSOR STATION 527 IN PLAQUEMINES PARISH WAS FOUND UNDER WATER, WITH MULTIPLE LEAKS DETECTED. THE OFFICE AND SEVERAL OTHER BUILDINGS WERE WASHED AWAY OR WERE UNDER WATER. EXTENSIVE DAMAGES CAUSED BY HURRICANE KATRINA HAVE BEEN REPAIRED (COMPRESSOR STATION REFURBISHED) AND FACILITY HAS BEEN PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050097 | 2005-09-26 00:10 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1745 | 2005-08-30 | 2005 |  |  |  |  | MP524C-601 + 0.00 |  | 29. 056417' | -90.250477 | OFFSHORE |  | BAY MARCHAND | 5 |  | YES | NO | INTERSTATE | OTHER | TWO RISERS MISSING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2665826 | 1607098.7493 | 3550006.2213 | 33919 | 13418.9354 | 2631907 | 3536587.2859 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 770945 | 2005-08-30 | 900 | 1138 | NO | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM7 | TRANSMISSION | OTHER | UNKNOWN AT THIS TIME | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 | 0.5 | API | 35000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | TWO 12-INCH RISERS (LINE NO.S 524C-600 & 524C-900) WERE DISCOVERED MISSING AT THE BAY MARCHAND BLOCK 5 PLATFORM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050098 | 2005-09-26 00:34 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1545 | 2005-08-31 | 2005 |  |  |  |  | MP 526A-203A + 0.00 |  | 29*27'86 | -89*23'33 | OFFSHORE |  | MAIN PASS | 32 |  | YES | NO | INTERSTATE | OTHER | 8 INCH RISER MISSING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 32515.4643 | 69164.8683 | 5000 | 1978.0854 | 50000 | 67186.7829 | 0 | 0 | NO | YES | NO | NO | 0 |  | 3 |  | 771099 | 2005-08-31 | 990 | 992 | NO | NO | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | RISER | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8.63 | 0.32 | API | 42000 | SEAMLESS |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | A 4-INCH RISER (LINE NO.526A-200) WAS DISCOVERED MISSING AT THE MAIN PASS BLOCK 32 PLATFORM. PIPELINE WAS ABANDONED BY SALE TO ANOTHER PARTY. TGP NO LONGER OPERATES THIS LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050099 | 2005-09-26 14:58 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1830 | 2005-08-30 | 2005 | CHALMETTE | ST BERNARD | LA | 77043 | 2.16 |  | 29 58.27 | 89 57.09 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | TAP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162319 | 74026.1408 | 64690.2265 | 161819 | 64018.3587 | 500 | 671.8678 | 0 | 0 | NO | NO | NO | NO | 0 |  | 28 | 0 | 770966 | 2005-08-30 | 348 | 442 | NO | NO | NO | NO | NO | NO | JEFFREY B. MCMAINE | 2706886361 | JEFF.MCMAINE@BWPMLP.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  |  | 1 |  | UKNOWN |  | SEAMLESS | N/A | UNKNOWN |  | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA TIDAL SURGE | [51 empty] | TIDEL SURGE FROM HURRICANE KATRINA CAUSED A 1/2" AND 1" NIPPLE TO PULL AWAY (STRIPPED THREADS) FROM THE PIPING AT A REGULATOR STATION. WAS UNDER WATER AND NOT ACCESSABLE ACCOUNTED FOR THE ELASPED TIME TO MAKE SAFE. 5/15/2013 UPDATE: UNCHECKED PART A, QUESTION 5.D TO REFLECT THAT THE INCIDENT DIDN'T OCCUR IN AN HCA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050100 | 2005-09-26 15:17 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1550 | 2005-08-30 | 2005 | POINTE A LA HACHE | PLAQUEMINES | LA |  | 29.06 |  | 29 35.107 | 89 48.217 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | TAP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277889 | 126679.1396 | 110411.6914 | 277389 | 109739.8235 | 500 | 671.8678 | 0 | 0 | NO | NO | NO | NO | 0 |  | 532 | 0 | 771102 | 2005-08-30 | 720 | 982 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9857789035 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | TAP TEE AND TUBING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  |  | 0.25 |  | UNKNOWN |  | UNKNOWN |  |  |  | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA TIDAL SURGE | [51 empty] | TIDAL SURGE FROM HURRICANE KATRINA CAUSED A 1/4" NIPPPLE TO PULL OFF AND A 1/4" PIPING TEE TO CRACK AND 3/8" TUBING TO BREAK. BEING UNDERWATER RESULTED IN LENGTHLY ELAPSED TIME TO AREA MADE SAFE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050101 | 2005-09-26 15:33 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1100 | 2005-09-09 | 2005 |  |  | LA |  | 11.77 | 621+84 | 28 59' 07 | 90 09' 41 | OFFSHORE |  | SOUTH TIMBALIER | 26 |  | YES | YES | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2200000 | 1325626.4938 | 2925559.138 | 32337 | 12793.0692 | 2167663 | 2912766.0688 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 38 | 771931 | 2005-09-09 | 1100 | 1235 | YES | NO | NO | NO | NO | NO | JACK L. ADAMS | 9857789035 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12 | 0.5 |  | 42000 | SEAMLESS |  |  | 1968 | UNDER WATER |  | 600 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON 9/9/2005 PLATFORM OPERATOR RETURNED TO THE PLATFORM AFTER HURRICANE KATRINA AND INFORMED GULF SOUTH THAT FPL 2 HAD NO PRESSURE. DIVERS INVESTIGATED THE SUBSEA PIPELINE AND IDENTIFIED A BREAK APPROXIMATELY 100 FEET FROM THE PLATFORM. THE 12" PLATFORM RISER ALSO RECEIVED DAMAGE. EVIDENCE SUGGESTS THAT A VESSEL WAS ADRIFT DUING THE STORM EITHER DRAGGING AN ANCHOR OR THE LEG OF A LIFT BOAT CAUSING THE SEPARATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050102 | 2005-09-26 16:14 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1320 | 2005-09-04 | 2005 | ALGIERS | ORLEANS | LA |  | 0.00 |  | 29 55.423 | 89 58.867' | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | TAP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187752 | 85613.2631 | 74751.9555 | 187252 | 74080.0877 | 500 | 671.8678 | 0 | 0 | NO | NO | NO | NO | 0 |  | 175 |  |  |  | 77 | 480 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9857789035 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  |  | 0.5 | [7 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | WINDS DURING HURRICANE KATRINA BLEW METER BUILDING AWAY BREAKING 4 1/2" TAPS THAT CONNECTED TO THE ORIFICE METER FLANGE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050103 | 2005-09-26 17:04 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINES - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1530 | 2005-08-30 | 2005 |  |  |  |  | MP 15.99 | 843+99 | X= 2,107,434 | Y= 21,094 | OFFSHORE |  | SHIP SHOAL | 145 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2530000 | 1525542.5332 | 3371207.6585 | 30000 | 11868.5121 | 2500000 | 3359339.1464 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 770940 | 2005-08-30 | 1000 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 10 | 0.37 | GRADE B | 35000 | SEAMLESS | ANSI 600 | YOUNGSTOWN | 1963 | UNDER WATER |  | 48 | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | ON TUESDAY, AUGUST 30, 2005 AROUND 3:30 PM, FOLLOWING HURRICANE KATRINA, THE PIPELINE SEGMENT WAS FOUND DEPRESSURIZED FROM GAUGE OBSERVATIONS AT SS 87 AND SS169 PLATFORMS. FURTHER INVESTIGATION FROM FLY-OVER REVEALED BUBBLES IN THE VICINITY OF SS 145. THE NRC WAS NOTIFIED AND CASE # 770940 WAS ASSIGNED. ON FRIDAY, SEPTEMBER 2, 2005 DIVERS WERE DISPATCHED AND DISCOVERED THE PIPELINE HAD BEEN SEVERED BENEATH THE TENNESSEE GAS PIPLINE 36¿ CROSSING. SUBSEQUENTLY, REPAIRS HAVE BEEN SCHEDULED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050104 | 2005-09-27 11:20 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1545 | 2005-08-31 | 2005 |  | PLAQUEMINES | LA |  |  |  | 29.386014 | -89.380013 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | 1-INCH NIPPLE AND VALVE DAMAGED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 32515.4643 | 69164.8683 | 5000 | 1978.0854 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 771100 | 2005-08-31 | 1100 | 1150 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | 1-INCH NIPPLE AND VALVE | STEEL |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | A LEAK WAS DISCOVERED ON THE VALVE PLATFORM AT THE OLGA COMPRESSOR STATION. THE LEAK WAS BELIEVED TO BE RELATED TO THE HURRICANE DAMAGE. THE 1" NIPPLE HAS SINCE BEEN REPAIRED AND PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050105 | 2005-09-27 11:36 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1815 | 2005-08-31 | 2005 |  |  |  |  | MP 0+00 |  | 29.224718 | -88.552297 | OFFSHORE |  | MAIN PASS | 306 |  | YES | NO | INTERSTATE | OTHER | 18-INCH RISER&PIPELINE DAMAGED AT THE NOBLE PLAT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 294917.1485 | 624461.8999 | 50000 | 19780.8535 | 450000 | 604681.0464 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 771125 | 2005-08-31 | 1150 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | 18-INCH RISER & PIPELINE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 18 | 0.5 | API | 52000 |  |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | 18-INCH RISER AND PIPELINE DAMAGED AT THE NOBLE PLATFORM, MAIN PASS BLOCK 306, DURING HURRICANE KATRINA. THE PLATFORM WAS DAMAGED BEYON REPAIR BUT SOUTHERN NATURAL GAS (SNG) COMPANY INSTALLED A SUBSEA TIE-IN & BLOCK VALVE, RESTORING THE 18" PIPELINE TO SERVICE. OTHER PIPELINES TIED INTO THIS SUBSEA ASSEMBLY AS WELL BUT THE PRODUCTION HAS DIMINISHED TO THE POINT THAT THE MAIN PASS 306 PIPELINE IS PLANNED FOR ABANDOMENT IN 2010.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050106 | 2005-09-27 16:05 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1710 | 2005-09-01 | 2005 | [6 empty] | 29*16'16 | -88*42'43 | OFFSHORE |  | MAIN PASS | 298 |  | YES | NO | INTERSTATE | OTHER | 12-INCH FLANGE ON RISER LEAKED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 32515.4643 | 69164.8683 | 5000 | 1978.0854 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 771240 | 2005-09-01 | 1100 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 12.75 | 0.5 | API | 52000 |  |  |  | 1970 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | FOLLOWING AN INSPECTION AFTER THE STORM, A FLANGE ON THE PIPELINE RISER WAS DISCOVERED LEAKING AT THE MAIN PASS BLOCK 298 PLATFORM. THE PLATFORM ALSO SUSTAINED DAMAGE. INITIALLY, THE LEAKING FLANGE WAS ISOLATED TO STOP THE LEAK. LATER, THE MAIN PASS 298 PLATFORM WAS REMOVED DUE TO DAMAGE SUSTAINED DURING HURRICANE KATRINA. A SUBSEA TIE-IN ASSEMBLY WAS INSTALLED AND ALL PIPELINES PREVIOUSLY CONNECTED AT THE PLATFORM WERE CONNECTED AT THE NEW SSTI AND RETURNED TO FLOW.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050107 | 2005-09-29 15:26 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 2050 | 2005-09-03 | 2005 |  | PLAQUEMINES | LA |  | 527A-102 + 10.00 |  | 29.172576 | -89.418711 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | STORM DAMAGE TO EXISTING SIDE VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 34793.4343 | 71142.9536 | 10000 | 3956.1707 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 |  | 771397 | 2005-09-03 | 1100 | 1273 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | IN FABRICATED ASSEMBLY | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.38 | API | 60000 |  |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | A LEAK WAS DISCOVERED ON THE 527A-100 LINE, NEAR SIDE VALVE 527A-103. LEAK WAS DETERMINED TO BE CAUSED BY DAMAGE TO THE ASSEMBLY FROM HURRICANE KATRINA. THE DAMAGED ASSEMBLY HAS BEEN REMOVED AND REPLACED WITH THE AFFECED PIPELINE BEING PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050108 | 2005-09-29 17:30 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 757 | 2005-08-30 | 2005 |  | HUGHES | OK | 74825 | ALLEN ST. AD-EAST | 2975+99 | 34.52003 | 96.21195 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | 2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254000 | 117212.4354 | 109967.9218 | 244000 | 96530.5652 | 10000 | 13437.3566 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 770838 | 2005-08-30 | 620 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | 2" TOR NIPPLE | 1973 | 30 | 0.33 | API 5L X-65 | 65000 | DSAW |  | REPUBLIC | 1973 | OPEN DITCH |  | 36 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | CONTRACTOR WAS MOVING PIPE AND RIGGING FAILED RELEASING PIPE THAT STRUCK THE 2" TOR NIPPLE ON PIPE IN OPEN DIG CAUSING RELEASE. |  | A CONTRACTOR WAS MOVING PIPE AND THE RIGGING FAILED RELEASING PIPE THAT STRUCK THE 2" TOR NIPPLE ON PIPE IN AN OPEN DIG CAUSING RELEASE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050109 | 2005-09-30 18:38 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1920 | 2005-09-04 | 2005 |  |  |  |  | MP 527A-901 +8.06 |  | 28*47' 41.533 | -89* 10' 36.216 | OFFSHORE |  | MISISSIPPI CANYON | 148 |  | YES | NO | INTERSTATE | OTHER | CONTROL LINE ON PLATFORM FOUND LEAKING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 34793.4343 | 71142.9536 | 10000 | 3956.1707 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 771505 | 2005-09-04 | 1200 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | CONTROL LINE ON PLATFORM PIPING | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.63 | API | 60000 |  |  | KAISER |  | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | LEAK WAS DISCOVERED ON THE VASTAR PLATFORM AT MISSISSIPPI CANYON BLOCK 148, ON THE CONTROL PIPING FOR THE PLATFORM. THE TGP PIPELINE INVOLVED WAS THE 527A-900 LINE. THE TUBING COMPRISING THE CONTROL PIPING WAS BROKEN DURING THE ONSLAUGHT OF HURRICANE KATRINA. THE TUBING HAS BEEN REPAIRED (BY REPLACEMENT WITH NEW TUBING) AND THE PIPELINE HAS BEEN RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050110 | 2005-08-10 | ORIGINAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFT ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 1900 | 2005-07-13 | 2005 | NEWBERRY SPRINGS | SAN BERNADINO | CA |  | NEW BERRY SPRINGS COMP. S |  | 34.8163 | -116.6102 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725000 | 334034.5487 | 310525.3407 | 700000 | 276931.9493 | 25000 | 33593.3915 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 765454 | 2005-07-13 | 230 | 250 | NO | YES | NO | NO | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | OTHER | AIR LINE | OTHER | BRAIDED NYLON REINFORCEMENT | NO | NO | NO | COMPRESSOR |  | 2004 | 1.5 | [7 empty] | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | AIR HOSE | [10 empty] | NEWBERRY STATION IVESTIGATION REPORT DOT/CPUC REPORTABLE 7/13/2005 SEQUENCE OF EVENTS AT APPROXIMATELY 6:00 PM, GAS CONTROL REPORTED THAT STARTING AIR PRESSURE AT NEWBERRY STATION WAS LOW, SETTING INTO MOTION RESPONSE AND INVESTIGATION. THE AIR DRYER WAS ISOLATED AND AIR PRESSURE BUILT BACK UP, AND THE GAS VENT VALVES CLOSED. THE AIR SYSTEMS PRESSURE DROPPED DUE TO THE AIR LINE HOSE FAILURE, BUT THE AIR COMPRESSURE CONTINEUED TO SUPPLY AIR, ULTIMATELY HOLDING A PRESSURE OF 35# IN TEH AIR SYTEM. ONCE THE AIR DRYER WAS ISOLATED, AIR PRESSURE BUILT BACK UP AND THE GAS VENT VALVES CLOSED. MAINTAINING THE 35# EQUILIBRIUM RESULTED IN A PRESSURE LOW ENOUGH TO TRIP THE GAS VENTING VALVES (65# DESIGNED SET POINT) TO ATMPOSPHERE BUT NOT LOWE ENOUGH TO CLOSE THE BLOCK VALVLES (30# DESIGNED SET POINT) WHICH WOULD HAVE ISOLATED TRANSMISSION LINES 235 AND 3000 FROM THE STATION. UPON DISCOVERY OF THE HOSE FAILURE, THE AIR DRYER WAS BYPASSED AND REMOVED FROM SERVICE. STATION PERSONNEL REMAINED AT THE STATION THROUGH THE NIGHT OT MONITOR OPERATIONS. THE STATION WAS PLACED BACK ONLINE AT APPROXIMATELY 8:45 PM. DUE TO QUICK ACTION BY GAS OPERATIONS TO MAINTAIN THE GAS SYSTEM AND BY PUTTING STORAGE ON WITHDRAWAL, THERE WAS NO LOSS OF SERVICE OR CUSTOMER IMPACT. NOTE: THE VENTING OF GAS TO ATMOSPHERE WAS NOT THE RESULT OF ANY MALFUCTION OF THE ESD SYSTEM NOR A TRIGGER OF THE ESD SYSTEM. DURING THIS INCIDENT, THE ESD SYSTEM COULD HAVE BEEN ACTUATED BY A NUMBER OF SAFETY-TRIGGERED CONDITIONS, AND THIS WOULD HAVE RESULTED IN A COMPLETE ISOLATION AND BLOW-DOWN OF THE STATION. IMMEDIATE MITIGATION EFFORTS UNTIL COMPLETEION OF COMPREHENSIVE ENGINEERING ANALYSIS, THE AIR DRYER WILL REMAIN OUT OF SERVICE. A NITROGEN SUPPLY SYSTEM TO PROVIDE BACK-UP PRESSURE TO THE ESD SYSTEM NOT INSTALLED ON FRIDAY JULY 15, 2005. THE SYTEM IS SET TO PROVIDE CONSTANT 80# OF NITROGEN FEED TO THE ESD SYSTEM, SHOULD THE EXISTING SYSTEM PRESSURE DROP BELOW 80#. THE NITROGEN FEED IS SUPPLIED THROUGH A CHECK VALVE AND ORIFICE SO AS TO NOT IMPACT OR AFFECT NORMAL OPERATION OF THE ESD SYSTEM, IF ACTUATED. ON GOING ENGINEERING REVIEW OF CURRENT AIR SYSTEMS AT NEW BETTER STATION (STARTING AIR, UTILITY AIR, AND INSTRUMENT AIR), AND WILL IMPLEMENT ANY MODIFICATIONS IDENTIFIED FROM ENGINEERING REVIEW DEEMED NECESSARY. PLEASE CONTACT JEFF KOSKIE AT (213) 244-3283 IF YOU HAVE ANY QUESTIONS OR NEED ADDITIONAL INFORMATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050111 | 2005-10-03 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1200 | 2005-08-29 | 2005 | [6 empty] | 28-34.15 | 90-24.53 | OFFSHORE |  | SOUTH TIMBALIER | 161 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 604123.4306 | 1339753.5605 | 4200 | 1661.5917 | 995800 | 1338091.9688 | 0 | 0 | NO | NO | NO | NO | 0 |  | 24 | 20 | 771176 | 2005-09-01 | 922 | 1206 | NO | YES | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENERGY.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | JONES & LAUGHLIN | 1968 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | HURRICANE KATRINA CAUSED THE APACHE ST161A PLATFORM TO TOPPLE, WHICH RESULETED IN DAMAGE TO TRUNKLINE GAS COMPANY'S 12 INCH PIPELINE. THE PIPELINE HAS BEEN ISOLATED AND MADE SAFE. DIVERS HAVE NOT BEEN AVAILABLE TO INVESTIGATE THE FAILURE. APACHE, THE OWNER & OPERATOR OF THE TOPPLED PLATFORM, DOES NOT CURRENTLY PLAN TO REPOLACE THEIR PLATFORM. A DIFFERENT PRODUCER HAS APPROACHED TRUNKLINE ABOUT CONNECTING TO THE SEVERED LINE. FINAL DISPOSITION OF THE LINE WILL BE DEPENDENT UPON WHETHER THIS PRODUCER FOLLOWS THROUGH WITH THIS CONNECTION OR EXERCISES SOME OTHER OPTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050112 | 2005-10-03 14:58 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1230 | 2005-09-14 | 2005 |  |  | LA |  |  |  | 2827.43N | 9140.55W | OFFSHORE |  | EUGENE ISLAND | 264 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 60474.9885 | 134373.5659 | 0 | 0 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 772458 | 2005-09-14 |  |  | YES | NO | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | [7 empty] | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | UNKNOWN | [10 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | LEAK DISCOVERED DURING ROUTINE MMS PATROL. DUE TO HURRICANE KATRINA, NO REPAIR DATE HAS BEEN SCHEDULED. LINE HAS BEEN ABANDONED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050113 | 2005-10-03 23:34 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1925 | 2005-09-04 | 2005 |  | PLAQUEMINES | LA |  | MP 526A-601+0.00 |  | 29.091739 | -89.282690 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | 1/2-INCH VALVE DAMAGED AT VALVE 526A-601 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224040 | 133996.6055 | 291569.3511 | 10000 | 3956.1707 | 214040 | 287613.1804 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 771506 |  | 1000 | 1133 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1988 | 10.75 | 0.37 | API | 42000 |  |  |  |  | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE KATRINA | [51 empty] | 1/2-INCH VALVE FOUND DAMAGED AND LEAKING AT MLV 526A-601 , NEAR SV 526A-103. THE VALVE WAS REPLACED AND THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050114 | 2005-10-04 22:37 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 850 | 2005-09-05 | 2005 | [6 empty] | 29* 06' 00 | -88* 43' 43 | OFFSHORE |  | SOUTH PASS | 62 |  | YES | NO | INTERSTATE | OTHER | 20-INCH & 14-INCH RISERS DAMAGED AT PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 53017.1944 | 86967.6364 | 50000 | 19780.8535 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 |  | 771521 | 2005-09-05 | 1100 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | 20-INCH, 14-INCH RISERS | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.5 | API | 52000 |  |  |  |  | OTHER | UNDER INVESTIGATION |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM DAMAGE-HURRICANE KATRINA | [51 empty] | SOUTH PASS BLOCK 62 PLATFORM TOPPLED, WITH TWO SNG RISERS (20-INCH, 14-INCH) DAMAGED WITH PLATFORM. THE AFFECTED PIPELINES WERE LATER REPAIRED AND TIED IN SUBSEA, BEING PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050115 | 2005-10-04 23:15 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1400 | 2005-09-05 | 2005 |  |  |  |  | MP 523M-201 + 0.00 |  |  |  | OFFSHORE |  | SHIP SHOAL | 144 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3817476 | 2293702.5847 | 5034866.7681 | 100000 | 39561.707 | 3717476 | 4995305.061 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 771534 | 2005-09-05 | 1000 | 1200 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | DAMAGED AND BENT AT SIDE VALVE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.41 | API | 60000 | SEAMLESS |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM DAMAGE -- HURRICANE KATRINA | [51 empty] | 20-INCH PIPELINE DAMAGED AND BENT AT S.V. LOCATION IN SHIP SHOAL BLOCK 144. SIDE VALVE ASSEMBLY TORN OFF 26-INCH MAIN LINE (NEAR MP 523M-101 + 40.59). CROSS-OVER BETWEEN 26-INCH AND 36-INCH LINES BENT, DAMAGED. THIS PIPELINE HAS SINCE BEEN ABANDONED.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050117 | 2005-10-06 10:56 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 |  | 2005-09-08 | 2005 | [6 empty] | 28 51 55.037 | 89 16 41.02 | OFFSHORE |  | VIOSCA KNOLL | 817 |  | YES | NO | INTERSTATE | OTHER | FOUND PIPELINE BROKEN DUE TO MUD SLIDE. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34685356 | 20927191.0878 | 46297914.9087 | 327000 | 129366.782 | 34358356 | 46168548.1267 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 771837 | 2005-09-08 | 901 | 1500 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPORD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 20 | 0.5 | API 5L | 65000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | OTHER | HURRICANE KATRINA | [53 empty] | HURRICANE KATRINA'S PATH CROSSED OVER ENTERPRISE PRODUCTS OPERATING L.P. VIOSCA KNOLL 817 PLATFORM CAUSING DAMAGE TO THE PLATFORM AND DEPARTING PIPELINES. STRUCTURE REPAIRS TO THE PLATFORM HAVE BEEN COMPLETED. A PORTION OF THE PIPELINE FACILITIES HAVE BEEN REPAIRED TO BRING PRODUCTION TO VIOSCA KNOLL 817 PLATFORM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050118 | 2005-10-05 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1700 | 2005-09-05 | 2005 |  |  |  |  | MP 523Q-301 +0.00 |  | 28*47'19.93 | -90 *57' .0.94 | OFFSHORE |  | SHIP SHOAL | 120 |  | YES | NO | INTERSTATE | OTHER | STORM DAMAGE TO SUBSEA TIE-IN ASSEMBLY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 53017.1944 | 86967.6364 | 50000 | 19780.8535 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 771545 | 2005-09-05 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | 0.41 |  | 52000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM DAMAGE - HURRICANE | [51 empty] | A LEAK WAS DISCOVERED ON THE TGP LINE 523Q-300, IN SHIP SHOAL BLOCK 120. THE LEAK WAS CAUSED BY HURRICANE DAMAGE TO THE SUBSEA TIE-IN ASSEMBLY. THE DAMAGE WAS REPAIRED AND THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050120 | 2005-10-06 22:39 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1330 | 2005-09-08 | 2005 |  |  |  |  | MP 0+00 |  |  |  | OFFSHORE |  | WEST DELTA | 133 |  | YES | NO | INTERSTATE | OTHER | 12-INCH RISER DAMAGED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 106034.3888 | 173935.2729 | 100000 | 39561.707 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 771840 | 2005-09-08 | 1050 | 1300 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | RISER PIPING | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 | 0.5 | API | 52000 |  |  |  |  | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM DAMAGE-HURRICANE KATRINA | [51 empty] | VASTAR RESOURCES PLATFORM IN WEST DELTA BLOCK 133 WAS FOUND TOPPLED FOLLOWING HURRICANE KATRINA. SOUTHERN NATURAL GAS 12-INCH PIPELINE RISER ON THE WEST DELTA BLOCK 133-105 HURTES LINE WAS DAMAGED. THE PRODUCER'S PLATFORM WAS NOT RESTORED AND SNG'S PIPELINE WAS ABANDONED FROM WHERE THE PLATFORM HAD STOOD OVER TO A DOWNSTREAM TIE-IN IN WEST DELTA BLOCK 105, BEING DISCONNECTED FROM THIS DOWNSTREAM TIE-IN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050121 | 2005-10-06 23:05 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1705 | 2005-09-08 | 2005 |  |  |  |  | MP 0+0.0 |  |  |  | OFFSHORE |  | BRETON SOUND | 34 |  | YES | NO | INTERSTATE | OTHER | 6-INCH RISER DAMGED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 53017.1944 | 86967.6364 | 50000 | 19780.8535 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 771856 | 2005-09-08 | 1000 | 1150 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | RISER PIPE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6.63 | 0.31 | API | 35000 |  |  |  |  | OTHER | RISER ON PLATFORM |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM DAMAGE-HURRICANE KATRINA | [51 empty] | THE BRETON SOUND BLOCK 34 PLATFORM WAS FOUND DAMAGED BEYOND REPAIR IN THE AFTERMATH OF HURRICANE KATRINA, ALONG WITH THE SNG 6-INCH BRETON SOUND BLOCK 32 PIPELINE (MAINLY THE RISER ON THE PLATFORM). SNG INSTALLED A SUBSEA BLOCK VALVE AT THE END OF THE BRETON SOUND BLOCK 34 PIPELINE, ALLOWING THE LINE TO BE PLACED BACK INTO SERVICE WITH OTHER EXISTING PRODUCING CUSTOMERS HAVING COME BACK ON LINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050122 | 2005-10-10 08:49 | SUPPLEMENTAL FINAL | 30688 |  | CONSUMERS ENERGY | 1945 W. PARNALL RD | JACKSON | JACKSON | MI | 49201 | 652 | 2005-09-11 | 2005 | FLINT | GENESEE | MI | 48559 |  |  | 43.0764 | 83.6544 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 28827.199 | 33218.2101 | 50000 | 19780.8535 | 10000 | 13437.3566 | 0 | 0 | NO | NO | NO | YES | 100 | PRECAUTIONARY | 2 | 51 | 772093 | 2005-09-11 | 220 | 375 | NO | YES | NO | NO | NO | NO | JOAQUIN J AFFONSO JR | 5177881835 | JJAFFONSO@CMSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 10.75 | 0.25 | 5L-API5L | 35000 | ERW |  |  | 1961 | ABOVE GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | ATMOSPHERIC | NO |  | NO | [57 empty] | ROOT CAUSE ANALYSIS DETERMINED THAT THE PIPE COATING WAS DAMAGED NEAR THE TOP OF THE PIPE DUE TO PIPE MOVEMENT AND ITS PROXIMITY TO THE BRIDGE. MOISTURE AND CORROSIVE MATERIALS FR0M THE BRIDGE DECK ENTERED THE SPACE BETWEEN THE PIPE COATING AND THE PIPE WALL ACCELERATING ATMOSPHERIC CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050123 | 2005-10-10 17:12 | SUPPLEMENTAL FINAL | 2731 |  | CHEVRON PIPE LINE COMPANY | 4800 FOURNACE PLACE | BELLAIRE | HARRIS | TX | 77401 | 1700 | 2005-09-11 | 2005 | [8 empty] | OFFSHORE |  | CHANDELEUR SOUND | 7 | LA | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2245911 | 1351366.5238 | 2974381.6241 | 45911 | 18163.1753 | 2200000 | 2956218.4488 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 772135 | 2005-09-11 | 950 | 1440 | YES | NO | NO | NO | NO | NO | HENRY L. LEGER | 3376548915 | HENRYLEGER@CHEVRON.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 12 | 312 | API 5L | 46000 | ERW | N/A | J&L STEEL CORPORATION | 1964 | UNDER WATER |  | 36 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | THE CHANDELEUR NATURAL GAS PIPELINE SYSTEM IN THE GULF OF MEXICO WAS IMPACTED BY HURRICANE KATRINA. COMMUNICATIONS WERE LOST ON AUGUST 29, 2005 DUE TO HURRICANE KATRINA. COMMUNICATIONS WERE RE-ESTABLISHED ON SEPTEMBER 11, 2005 AND INDICATED A LOW PRESSURE OF 17-PSIG ON THE PIPELINE; AT THAT TIME THE TELEPHONIC NOTIFICATION WAS MADE TO THE NRC. SUBSEQUENTLY, SIDE SCAN SONAR INDICATED CRATERS ON THE SEA-FLOOR ALONG THE PIPELINE WHICH MAY HAVE BEEN CREATED BY HIGH PRESSURE GAS REALEASES. DIVERS WERE THEN SENT DOWN AND CONFIRMED THAT A PHYSICAL SEPERATION OF THE PIPELINE HAD OCCURED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050124 | 2005-10-11 12:47 | SUPPLEMENTAL FINAL | 18273 |  | SHELL PIPELINE COMPANY LP | 777 WALKER STREET | HOUSTON | HARRIS | TX | 77002 |  | 2005-10-02 | 2005 | [6 empty] | 27.9007 | 92.0008 | OFFSHORE |  | GARDEN BANKS | 84 |  | YES | NO | INTERSTATE | OTHER | HURRICANE RITA - SEPARATED LINE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15150000 | 9124671.7911 | 20120565.5801 | 250000 | 98904.2676 | 14900000 | 20021661.3125 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  |  | 2005-10-03 | 1280 | 2160 | NO | NO | NO | NO | NO | NO | RICHARD KLASEN | 7132411064 | RICHARD.KLASEN@SHELL.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 | 0.56 |  | 52000 | SEAMLESS |  | NKK | 1994 | UNDER WATER |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | HURRICANE RITA WAS THE CAUSE. THE PIPELINE WAS SEPARATED AT THE TIE-IN LOCATION WHERE THE AUGER 12" LINE WAS ROUTED INTO GB 128A PLATFORM. LOCATION 27.54.02.08N 92.00.03.00W 10-3-2005 AN INITIAL NOTIFICATION WAS MADE TO THE MMS. AT 7500 FEET UPSTREAM THE PIPELINE WAS KINKED FROM A DRILLING RIG (THERALD MARTIN)CROSSING THE PATH OF THE PIPELINE. A PIPE REPLACEMENT WAS MADE AT BOTH LOCATIONS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050125 | 2005-10-12 11:01 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1840 | 2005-09-25 | 2005 | [6 empty] | 28.4235 | -91.9569 | OFFSHORE |  | SOUTH MARSH ISLAND | 108 |  | YES | NO | INTERSTATE | OTHER | UNKNOWN AT THIS TIME | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7350000 | 4429996.0684 | 9781645.2316 | 100000 | 39561.707 | 7250000 | 9742083.5246 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773725 | 2005-09-25 | 1100 | 1250 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 24 |  |  | 52000 | DSAW |  | U.S. STEEL | 1968 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE | [51 empty] | 24-INCH PIPELINE RISER ON ANR LINE 749 DESTROYED, ALONG WITH SOUTH MARSH ISLAND BLOCK 108 PLATFORM, FOLLOWING HURRICANE RITA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050126 | 2005-10-12 12:18 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1100 | 2005-09-25 | 2005 |  |  |  |  | MP 524G-101 + |  |  |  | OFFSHORE |  | BAY MARCHAND | 5 |  | YES | NO | INTERSTATE | OTHER | RISER AND CONNECTING PIPING DAMAGED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1807302 | 1090470.0009 | 2412672.223 | 16732 | 6619.4648 | 1790570 | 2406052.7581 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773664 | 2005-09-25 | 1100 | 1235 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | RISER AT PLATFORM | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.38 |  | 42000 |  |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | GAS BUBBLES REPORTED IN BAY MARCHAND BLOCK 5 , NEAR TGP LINE NO. 523G-100 FROM BAY MARCHAND TO LEEVILLE. LINE WAS ISOLATED AND BLOWN DOWN. INVESTIGATION REVEALED THAT THE 16-INCH RISER PIPE NEEDED TO BE REPLACED. THE PIPELINE ITSELF WAS FOUND DISPLACED ON THE SEA FLOOR. UPON RISER REPLACEMENT AND DETERMINATION THAT THE PIPE STRESSES WERE ACCEPTABLE, THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050127 | 2005-10-11 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE COPMANY | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1325 | 2005-09-11 | 2005 |  |  |  |  | MP 523M-101A + |  | 28.4750 | -90.5803 | OFFSHORE |  | SHIP SHOAL | 135 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 185560.1803 | 304386.7276 | 175000 | 69232.9873 | 175000 | 235153.7402 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 772112 | 2005-09-11 | 1000 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 26 | 0.5 |  | 52000 | SMLS |  |  | 1974 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | DAMAGE DUE TO HURRICANE | [51 empty] | MULTIPLE LEAKS OCCURRED ON TGP 26-INCH LINE 523M-100 IN SHIP SHOAL BLOCKS 119, 135, AND 144, GULF OF MEXICO. DAMAGED SECTIONS WERE REMOVED AND REPLACED WITH NEW PIPE AND END CONNECTORS. THE PIPELINE HAS BEEN RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050128 | 2005-10-13 09:03 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1630 | 2005-09-29 | 2005 | DODGE CENTER | DODGE | MN | 55927 | 0.799 | 4217 | 44.0374 | -92.8562 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56052 | 33897.4406 | 75319.0711 | 0 | 0 | 56052 | 75319.0711 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 |  |  | 62 | 988 | NO | YES | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2005 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | TURBINE METER | [10 empty] | A ROOTS 5M TURBINE METER FAILED WHEN A LOCAL COMPANY MAY HAVE BEEN TESTING EQUIPMENT AND PULLING AN ABNORMALLY LARGE LOAD. THE METER OVERSPUN AND SEIZED. THIS PREVENTED GAS FROM FLOWING THROUGH THE METER AND THE TOWN OF DODGE CENTER EVENTUALLY RAN OUT OF NATURAL GAS. DODGE CENTER, MN HAS A POPULATION OF 2486 PEOPLE AND THERE ARE 1100 CUSTOMERS. THE TOWN WAS RELIT THE SAME EVENING WITH ASSISTANCE FROM THE LOCAL DISTRIBUTION COMPANY. THE FINAL INVESTIGATION SHOWED THAT DEBRIS HAD ENTERED THE METER. SAND AND WELD SLAG WAS FOUND INSIDE THE BODY OF THE METER. THE DEBRIS HAD ETCHED A GROOVE IN THE METER BODY UNTIL IT WAS BETWEEN THE TURBINE BLADE AND THE BODY ENOUGH TO CAUSE THE METER TO SEIZE. A TEE STRAINER WAS INSTALLED UPSTREAM OF THE METER TO PREVENT REOCCURRANCE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050129 | 2005-10-14 10:25 | SUPPLEMENTAL FINAL | 1007 |  | KINDER MORGAN INTERSTATE GAS TRANSMISSION | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 930 | 2005-09-27 | 2005 | HILL CITY | GRAHAM | KS |  |  | 15941+16 | 39.5418789 | -99.8662046 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 34774.3001 | 31015.0159 | 75000 | 29671.2803 | 0 | 0 | 1000 | 1343.7357 | NO | NO | NO | NO | 0 |  | 0 | 30 | 774013 | 2005-09-27 | 650 | 956 | YES | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | SLEEVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1976 | 22 | 0.28 | X-52 | 52000 | FLASH WELD |  |  |  | UNDER GROUND |  | 24 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | SLEEVE | [8 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | A PIPE SLEEVE INSTALLED IN 1976 DEVELOPED A PIN-HOLE LEAK WHICH KILLED VEGETATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050130 | 2005-10-14 12:48 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET 1000 | HOUSTON | HARRIS | TX | 77002 | 1637 | 2005-09-26 | 2005 | BEAUMONT | LIBERTY | TX |  |  |  | 2950179 | 9330367 | ONSHORE |  |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112000 | 51026.5283 | 44309.1119 | 112000 | 44309.1119 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773906 | 2005-09-26 |  |  | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1990 | [8 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | RELIEF VALVE OPENED DUE TO HURRICAN RITA AND SUDDEN LOSS OF DOWN STREAM CUSTOMERS. GAS VENTED UNTIL OPERATIONS PERSONNEL WERE ALLOWED BACK INTO AREA BY DISASTER RECOVERY TEAM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050131 | 2005-10-14 14:34 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1455 | 2005-09-26 | 2005 | CAMERON | CAMERON | LA |  |  |  | 2947393 | 9330367 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50001 | 22780.1557 | 19781.2491 | 50001 | 19781.2491 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 20 |  | 773881 | 2005-09-26 |  |  | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA | [51 empty] | FLOATING DEBRIS FROM HURRICANE RITA WASHED INTO THE PLANT SITE AND BROKE POWER GAS CONNECTION TO VALVE OPERATORS. MAINTENANCE PERSONNEL WERE UNABLE TO ACCESS LOCATION DURING HURRICANE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050132 | 2005-10-14 16:51 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1730 | 2005-09-17 | 2005 |  | PLAQUEMINES | LA |  | 0.73 |  | 29*8'8 | -89*18'18 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK ON 1-IN. BYPASS AT METER STATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56750 | 33312.7538 | 69857.1982 | 6750 | 2670.4152 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 772864 | 2005-09-17 | 1000 | 1100 | NO | NO | YES | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | 1-INCH BY-PASS LINE AT METER STATION | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1958 | 6.63 | 0.19 |  | 35000 |  |  |  | 1958 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | LEAK DISCOVERED ON 6-IN. SNG PIPELINE DUE TO DAMAGE AT THE WEST BAY RECEIVING STATION, ON A 1-INCH BY-PASS LOCATED ON A MARSH PLATFORM. INITIAL REPAIR WAS THE ISOLATION AND REMOVAL OF THE 1" BY-PASS. SINCE THEN, THIS METER STATION WAS REPLACED WITH A NEWLY BUILT STATION WHICH IS FLOWING GAS AT THIS TIME.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050133 | 2005-10-21 15:45 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 200 | 2005-09-24 | 2005 | CAMERON | CAMERON | LA | 70631 | MP 7.22 | 381+41 | 29.80148 | 093.34052 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | 1/2" FITTING KNOCKED OFF SEPARATOR | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94456 | 43048.5027 | 37463.2179 | 94356 | 37328.8443 | 100 | 134.3736 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774342 | 2005-09-29 | 280 | 805 | NO | NO | NO | NO | YES | NO | JACK L. ADAMS | 9857789035 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | 1/2 FITTING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1951 | [8 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | 1/2" FITTING KNOCKED OFF SEPERATOR BY DEBRIS FROM HIGH WINDS/WATER SURGE ENCOUNTERED DURING HURRICANE RITA
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050134 | 2005-10-21 16:22 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1400 | 2005-09-25 | 2005 | [6 empty] | 29.08703 | 091.69764 | OFFSHORE |  | EUGENE ISLAND | 95-F |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2591810 | 1561020.3861 | 3442175.4476 | 42750 | 16912.6298 | 2549060 | 3425262.8178 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773684 | 2005-09-25 | 895 | 1400 | NO | YES | NO | NO | NO | NO | JACK L. ADAMS | 9859851006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 10 | 0.5 |  | 42000 |  |  |  |  | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A SUBSEA TAP ASSEMBLY WAS STRUCK, DAMAGED AND SEPERATED FROM THE MAIN LINE POSSIBLY BY AN ANCHOR OF A DRIFTING VESSEL DURING HURICANE RITA. ALL PRODUCTION WAS SHUT-IN FOR THE STORM. THE AREA WAS MADE SAFE AS SOON AS THE PIPELINE BLEW DOWN FROM THE DAMAGE. REPAIR WAS MADE AND PUT BACK IN-SERVICE ON MARCH 1, 2006.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050135 | 2005-10-21 16:37 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1400 | 2005-10-21 | 2005 |  |  |  |  | MP 1.28 |  | 29.24508 | 091.66686 | OFFSHORE |  | EUGENE ISLAND | 43 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1800000 | 1082173.3795 | 2378192.1158 | 42750 | 16912.6298 | 1757250 | 2361279.486 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773684 | 2005-09-25 | 895 | 1200 | NO | YES | NO | NO | NO | NO | JACK L. ADAMS | 9857789035 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | TAP CONNECTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 14 | 0.5 |  | 42000 | SEAMLESS | N/A |  |  | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | PLATFORMS WERE SHUTDOWN AND PIPELINES SHUTIN PRIOR TO THE ARRIVAL OF HURRICANE RITA. UPON ACCESS ON 9/25/2005 AFTER THE HURRICANE PASSED, PRESSURE ON THE SHUTIN SYSTEM WAS DISCOVERED TO BE ZERO. A 4" SUBSEA TAP ASSEMBLY WAS STRUCK, DAMAGED AND COMPLETELY SEPARATED FROM THE 14" MAINLINE POSSIBLY BY AN ANCHOR OF A DRIFTING VESSEL DURING HURICANE RITA. BASED UPON RECORDED PRESSURES DATA FROM THE PLATFORM, IT IS ESTIMATED THAT THE INCIDENT OCCURRED APPROXIMATELY 1115 HOURS 9/22/2005.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050136 | 2005-10-21 | SUPPLEMENTAL FINAL | 18646 |  | ENBRIDGE OFFSHORE (GAS TRANSMISSION) L.L.C. | 1100 LOUISIANA SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 500 | 2005-09-24 | 2005 | CAMERON | CAMERON | LA | 70631 | MP 17 | STATION 701 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | BROKEN FITTING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 30318.7578 | 42699.396 | 40000 | 15824.6828 | 20000 | 26874.7132 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 774409 | 2005-09-29 | 850 | 1200 | YES | NO | NO | NO | NO | NO | MARC CURRY | 7133536369 | MARC.CURRY@ENBRIDGE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | SLUG CATCHER | [9 empty] | ABOVE GROUND |  | 0 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | FLOTATION | [52 empty] | HIGH WATERS FROM HURRICANE RITA STORM SURGE DAMAGED A LIQUID LEVEL INDICATOR THREADED INTO A 1" NIPPLE WELDED TO A SLUG CATCHER CAUSING THE RELEASE OF GAS TO ATMOSPHERE. THE HIGH WATERS ALSO CAUSED A SECTION OF THE SLUG CATCHER TO MOVE FROM IT ORIGINAL POSITION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050137 | 2005-10-24 18:24 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1840 | 2005-09-25 | 2005 | [6 empty] | 28.1638 | -91.3698 | OFFSHORE |  | EUGENE ISLAND | 346 | LA | YES | NO | INTERSTATE | OTHER | UNKNOWN- DAMAGE BEING ASSESSED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129600 | 63459.9968 | 79336.2825 | 100000 | 39561.707 | 29600 | 39774.5755 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773724 | 2005-09-25 |  | 1480 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.44 | API | 60000 |  |  |  | 2000 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | A GAS LEAK WAS DISCOVERED ON ANR LINE 697, IN EUGENE ISLAND BLOCK 346. THE PIPELINE WAS BLOWN DOWN TO ASSESS THE DAMAGE. A FLANGE ON THE ABOVE WATER PIPING WAS LATER REPLACED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050138 | 2005-10-25 10:40 | SUPPLEMENTAL FINAL | 4900 |  | KINDER MORGAN TEJAS PIPELINE | 500 DALLAS STREET SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 715 | 2005-10-25 | 2005 | TEXAS CITY | GALVESTON | TX |  |  |  | 292158 | 945626 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142605 | 64969.9827 | 56416.9723 | 142605 | 56416.9723 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 52 | 777340 | 2005-10-25 | 200 |  | NO | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | PRESSURE REGULATOR DEVELOPED A LEAK WHEN DOWNSTREAM CUSTOMER SUDDENLY CUT RECEIPT, PRESSURE BUILT UP AND ACTIVATED THE SECONDARY DEVICE (RELIEF VALVE) VENTING GAS TO ATMOSPHERE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050139 | 2005-10-25 10:05 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS WILLIAMS - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1220 | 2005-09-27 | 2005 |  |  |  |  | MP 23.85 |  | 28 19' 52.079 | 91 12 17.318 | OFFSHORE |  | SHIP SHOAL | 269 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5150000 | 3092088.5267 | 6778020.8533 | 150000 | 59342.5606 | 5000000 | 6718678.2928 | 0 | 0 | NO | NO | NO | NO | 0 |  | 77 | 5 | 774035 | 2005-09-27 | 750 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.5 | API 5LX | 52000 | SEAMLESS | ANSI 600 | US STEEL | 1969 | UNDER WATER |  | 36 | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | DURING POST HURRICANE RITA DAMAGE ASSESSMENTS, MARITECH'S SS 269A PLATFORM WAS DISCOVERED TO BE MISSING AND ASSUMED COLLAPSED ON LOCATION. THE 20" DEPARTING PIPELINE FROM SS 269A TO SS 214 HELD PRESSURE VIA A SUBSEA CHECK VALVE DOWNSTREAM OF THE PIPELINE DAMAGE. TRANSCO ALSO HAD A 10" PIPELINE FROM SS 322 AND A 16" PIPELINE FROM SS 269B BOARDING THE SS 269A PLATFORM, WHICH WERE ALSO DAMAGED DURING THE SAME EVENT. INVESTIGATION AND REPAIR SOLUTIONS ARE CURRENTLY UNDERWAY WITH START UP DATE PENDING CONTRACTOR AND EQUIPMENT AVAILABILITY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050140 | 2005-10-25 13:59 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1430 | 2005-09-26 | 2005 |  |  |  |  | 523M-105 + 34.96 | 184575 | 28.5851 | -92.4449 | OFFSHORE |  | VERMILION | 245B |  | YES | NO | INTERSTATE | OTHER | DAMAGE DUE TO HURRICANE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9050000 | 5398408.5202 | 11686748.4159 | 500000 | 197808.5352 | 8550000 | 11488939.8807 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 773870 | 2005-09-26 | 1000 | 1250 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | SUBSEA TIE-IN ASSEMBLY | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 30 | 0.6 | API | 60000 | DSAW |  |  | 1974 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | THE TGP 523M-100 PIPELINE'S SUBSEA TIE-IN FOR LINE 523M-2500 WAS DAMAGED SEVERELY DURING HURRICANE RITA, RESULTING IN A GAS RELEASE. THE SUBSEA TIE-IN WAS REPLACED WITH A NEW ASSEMBLY AND THE PIPELINES WERE PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050141 | 2005-10-25 17:43 | SUPPLEMENTAL FINAL | 31485 |  | ENBRIDGE OFFSHORE (GAS GATHERING) L.L.C. | 1100 LOUISIANA, SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 0 | 2005-09-24 | 2005 | [6 empty] | 28DEG19MIN | 91DEG54.5MIN | OFFSHORE |  | SOUTH MARSH ISLAND | 128 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151000 | 91168.0768 | 201955.9659 | 1000 | 395.6171 | 150000 | 201560.3488 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 1 |  |  | 1250 | 1440 | NO | YES | NO | NO | NO | NO | SCOTT R. PETERSON | 7138212176 | SCOTT.PETERSON@ENBRIDGE.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1996 | 12 | 0.38 | [6 empty] | OTHER | ON A BRIDGE BETWEEN TWO OFFSHORE PLATFORMS |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA | [51 empty] | HURRICANE RITA
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050142 | 2005-10-27 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1415 | 2005-09-27 | 2005 | [6 empty] | 29.5271 | -93.8186 | OFFSHORE |  | SABINE PASS | 18 |  | YES | NO | INTERSTATE | OTHER | FITTINGS ON PIG RECEIVER LEAKING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 106034.3888 | 173935.2729 | 100000 | 39561.707 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774073 | 2005-09-27 | 1200 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | FITTINGS ON PIG RECEIVER | STEEL |  | NO | NO | NO | PIPELINE |  |  | 24 | 0.5 |  | 60000 |  |  |  |  | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE-RELATED DAMAGE | [51 empty] | CONDENSATE AND NATURAL GAS WAS DISCOVERED LEAKING FROM FITTINGS ON PIG RECEIVER. AS SOON AS CONDITIONS ALLOWED FOR SAFE WORK TO PROCEED, ALL MATERIALS WERE INSPECTED AND THE FITTINGS WERE TIGHTENED, CAUSING THE LEAK TO STOP. PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050143 | 2005-10-28 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1230 | 2005-09-27 | 2005 | [6 empty] | 28.3546 | -91.5740 | OFFSHORE |  | SOUTH MARSH ISLAND | 76 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 106034.3888 | 173935.2729 | 100000 | 39561.707 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774037 | 2005-09-27 | 1000 | 1250 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | SEPARATION AT PLATFORM | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.38 |  | 42000 |  |  |  |  | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE-RELATED DAMAGE | [51 empty] | A LEAK WAS REPORTED NEAR TGP'S 12-INCH PIPELINE IN SOUTH MARSH ISLAND BLOCK 76. APPARENTLY, THE PRODUCTION PLATFORM TO WHICH PIPELINE CONNECTED WAS TOPPLED AND DESTROYED DURING HURRICANE RITA. THE TOPPLING CAUSED SEPARATION OF TGP'S CONNECTING LINE. PIPELINE HAS NEVER BEEN REPAIRED OR RECOMMISSIONED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050144 | 2005-10-28 13:25 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1330 | 2005-09-28 | 2005 |  |  |  |  | 523M-6201+5.0 |  | 28 *34.74' | -91*64.20' | OFFSHORE |  | EUGENE ISLAND | 294 |  | YES | NO | INTERSTATE | OTHER | 6-INCH RISER DAMGED WITH PRODUCER PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1580000 | 925673.6421 | 1933478.6229 | 200000 | 79123.4141 | 1380000 | 1854355.2088 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774225 | 2005-09-28 | 1000 | 1250 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | DAMAGE TO RISER PIPE | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 6.63 | 0.43 | API | 35000 | SEAMLESS |  |  | 1982 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA DAMAGE | [51 empty] | 6-INCH PIPELINE RISER DAMAGED ALONG WITH PRODUCER'S PLATFORM AT EUGENE ISLAND BLOCK 294A. THE PIPELINE HAS SINCE BEEN ABANDONED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050145 | 2005-10-28 16:36 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1410 | 2005-09-29 | 2005 | ROCK SPRINGS | SWEETWATER | WY |  | 0280 + 15776 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK ON BURIED FLANGE INSULATION SET | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234500 | 114294.5877 | 140178.1324 | 184500 | 72991.3495 | 50000 | 67186.7829 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774402 | 2005-09-29 | 683 | 850 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 24 | 0.28 |  | 52000 |  |  |  | 1973 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | BURIED FLANGE INSULATION SET FOUND LEAKING | [6 empty] | MATERIAL DEFECT |  | NO | YES | 9 | 30 | 1973 | WATER |  | 8 | 1153 | [12 empty] | A MINOR LEAK WAS DISCOVERED ON THE 5B LINE, AT THE BLOCK GATE 28.1. THE LEAK WAS DETRMINED TO BE LOCATED ON THE BURIED FLANGE INSULATION SET.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050146 | 2005-11-01 08:06 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 |  | 2005-10-03 | 2005 | CHANTILLY | FAIRFAX | VA |  | 1590.41 | 10750+20 | 38.881 | 77.418 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161427 | 76528.2907 | 82825.6486 | 141427 | 55950.9354 | 20000 | 26874.7132 | 0 | 0 | YES | NO | NO | YES | 858 | PRECAUTIONARY | 2 | 5 | 774823 | 2005-10-03 | 545 | 780 | NO | YES | NO | NO | NO | NO | JOHNNY LOPEZ - PIPELINE SPECIALIST I | 7132152995 | JOHNNY.LOPEZ@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 36 | 0.47 |  | 52000 | LONG |  |  |  | OPEN DITCH |  |  | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | WILLIAMS CONSTRUCTIO'S CONTRACTOR STRUCK MAINLINE "C" WITH TRACK HOE, WHILE EXCAVATING FOR AN ANOMALY INVESTIGATION. THERE WAS GAS RELEASED, BUT NO FIRES, OR INJURIES WERE REPORTED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050147 | 2005-11-01 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1300 | 2005-10-03 | 2005 | [5 empty] | 507A-2302 + | 29.6520 | -93.1218 | OFFSHORE |  | WEST CAMERON | 66A |  | YES | NO | INTERSTATE | OTHER | LEAK ON PRODUCER PLATFORM -METER TUBE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219000 | 114690.6748 | 181451.9972 | 119000 | 47078.4314 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774825 | 2005-10-03 | 900 | 999 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | METER TUBE | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 20 | 0.5 |  | 42000 |  |  |  | 1970 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA DAMAGE | [51 empty] | WEST CAMERON BLOCK 66A PRODUCER PLATFORM SUSTAINED DAMAGE TO PLATFORM PIPING DURING STORM. THE PLATFORM HAS BEEN REPAIRED AND MADE SAFE SO THAT PIPELINE HAS BEEN PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050148 | 2005-11-02 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1645 | 2005-09-27 | 2005 |  | CAMERON | LA |  | 507F-104 + |  | 29* 45' 46 | -92* 57' 57 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | 1/2-INCH VALVE BROKEN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 83254.6886 | 154154.4194 | 50000 | 19780.8535 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774103 | 2005-09-27 | 1000 | 1247 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | 1/2-INCH VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 26 | 0.5 | API | 52000 |  |  |  | 1971 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | DEBRIS FROM HURRICANE STRUCK A 1/2-INCH VALVE ON THE 26-INCH LINE, CAUSING DAMAGE AND A SUBSEQUENT LEAK. DAMAGE HAS BEEN REPAIRED AND PIPELINE PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050149 | 2005-11-02 18:04 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1300 | 2005-10-06 | 2005 |  |  |  |  | MP 20.12 |  | 29 40' 46.3 | 93 20' 49.7 | OFFSHORE |  | WEST CAMERON | 40 |  | YES | NO | INTERSTATE | OTHER | 6 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2113000 | 1260981.8928 | 2732176.0461 | 113000 | 44704.729 | 2000000 | 2687471.3171 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 775234 | 2005-10-06 | 865 | 1168 | NO | NO | YES | NO | NO | NO | CHRIS MASON | 8015846725 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 16 | 0.5 | API 5L | 35000 | ERW | ANSI 600 | LONE STAR STEEL | 1958 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A 6" TAP VALVE TO AN ABANDONED PIPELINE WAS SEVERED BY EXTERNAL FORCES (SUSPECTED ANCHOR, CABLE, OR DRIFTING RIG) DURING HURRICANE RITA. THE 16" PIPELINE CONNECTED TO THE 6" TAP LOST ALL PRESSURE AND IS SCHEDULED FOR REPAIR.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050150 | 2005-11-03 10:59 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1100 | 2005-10-05 | 2005 |  |  |  |  | 509A-501 + |  | 28.4189 | -92.6285 | OFFSHORE |  | EAST CAMERON | 272 |  | YES | NO | INTERSTATE | OTHER | 16-IN. RISER TOPPLED WITH PRODUCER PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 675000 | 382103.893 | 741100.8166 | 175000 | 69232.9873 | 500000 | 671867.8293 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 775071 | 2005-10-05 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | HURRICANE DAMAGE | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 16 | 0.5 | API | 52000 |  |  |  | 1974 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | PRODUCER PLATFORM AT EAST CAMERON BLOCK 272A WAS DAMAGED DURING STORM, ALONG WITH TGP 16-IN. LINE NO. 509A-500. PIPELINE WAS REPAIRED AFTER HURRICANE RITA AND PLACED BACK INTO SERVICE AT A NEW END CONNECTION. THE PIPELINE IS BACK OUT OF SERVICE DUE TO EXTRANEOUS DAMAGE TO OTHER FACILITIES DURING HURRICANE IKE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050151 | 2005-11-03 11:23 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1100 | 2005-10-05 | 2005 |  |  |  |  | 523M-7401 + 1.02 |  | 28.5258 | -92.4612 | OFFSHORE |  | VERMILION | 245 |  | YES | NO | INTERSTATE | OTHER | 8-IN. RISER TOPPLED ALONG WITH PRODUCER'S PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 675000 | 382103.893 | 741100.8166 | 175000 | 69232.9873 | 500000 | 671867.8293 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 775075 | 2005-10-05 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | RISER | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 8.63 | 0.5 | API | 35000 |  |  |  | 1990 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | TGP 8-IN. RISER DAMAGED WHEN PRODUCER'S VERMILION BLOCK 245F PLATFORM WAS DESTROYED. THE PLATFORM WAS NOT REBUILT AND THE TGP PIPELINE WAS SUBSEQUENTLY ABANDONED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050152 | 2005-11-08 07:45 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 335 | 2005-10-25 | 2005 | CENTERVILLE | SAINT MARY | LA |  | MP 66.5 / VS 1207 | 3511+20 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265223 | 121206.8978 | 107297.0427 | 262723 | 103937.7036 | 2500 | 3359.3391 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 10 | 777327 | 2005-10-25 | 815 | 894 | NO | YES | NO | NO | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | OTHER | RELIEF VALVE | 2002 | [5 empty] | PILOT OPERATED RELIEF VALVE | AXELSON TYPE HF |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | RELIEF VALVE ACTUATED BELOW THE ESTABLISHED SET POINT OF THE RELIEF VALVE. OVER TIME, VIBRATION LOWERED THE SET POINT OF THE RELIEF VALVE. THE RELIEF VALVE ACTUATED AND ESCAPING GAS CAUSED ADDITIONAL VIBRATION, FURTHER REDUCING THE SET POINT. THE CONTINUALLY FALLING SET POINT DID NOT ALLOW THE VALVE TO RESEAT ON ITS OWN. THE JAM NUT ON THE RELIEF DEVICE HAS BEEN SECURED WITH A STAINLESS STEEL TIE WIRE TO HELP PREVENT REOCCURRENCE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050153 | 2005-10-26 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC COMPANY | PO BOX 770000 MAIL CODE H15E | SAN FRANCISCO | SAN FRANCISCO | CA | 94177-0001 | 1155 | 2005-09-28 | 2005 | FOLSOM | SACRAMENTO | CA | 95630 | 16.36 |  | 38.64509 | -121.11201 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | CIRCUMFERENTIAL WELD | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 72569.9862 | 161248.279 | 0 | 0 | 120000 | 161248.279 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 | 30 | 774377 | 2005-09-29 | 85 | 500 | NO | NO | YES | NO | NO | NO | LARRY DENISTON - REGULATORY COMPLIANCE | 9259744313 | LCD1@PGE.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 10 | 0.22 | X42 | 42000 | ERW |  |  | 1986 | UNDER PAVEMENT |  | 42 | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | A SYSTEM MALFUNCTION ON A LNG TRAILER AND LNG VAPORIZER RESULTED IN THE RELEASE OF UN-VAPORIZED LNG INTO THE FOLSOM DFM. THE RAPID COOLING AND CONTRACTION OF THE 10" STEEL PIPELINE CAUSED A GIRTH WELD ON THE PIPELINE TO CRACK AND THE SUBSEQUENT LEAK. A MALFUNCTION HAS BEEN ATTRIBUTED TO A MIS-WIRING OF THE TEMPERATURE THERMOCOUPLE WHICH HAS LEAD TO AN INCORRECT INPUT TO THE HEAT EXCHANGE CONTROLLER. UPDATED BY PHMSA ON 12/16/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050154 | 2005-11-11 12:06 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 2727 NORTH LOOP WEST | HOUSTON | HARRIS | TX | 77382 | 1500 | 2005-10-11 | 2005 | [6 empty] | 29 10' 4" | 88 27' 21" | OFFSHORE |  | SOUTH PASS | 55 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32948184 | 19909975.9922 | 44175539.3622 | 103479 | 40938.0588 | 32844705 | 44134601.3034 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 775743 | 2005-10-11 | 1060 | 2220 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPORD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2003 | 12 | 0.5 | API 5L | 65000 | ERW |  |  |  | UNDER WATER |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | OTHER | HURRICANE KATRINA | [53 empty] | HURRICANE KATRINA'S PATH CROSSED OVER TENNESSEE GAS PIPELINE FACILITY SOUTH PASS 55 AND ENTERPRISE'S 12" GAS PIPELINE. ENTERPRISE PRODUCTS OPERATING L.P. GAS PIPELINE WAS BROKEN DUE TO SUBSEA MUD SLIDES. PIPELINE REPAIRS WILL RESTORE SERVICE TO PRE HURRICANE KATRINA STATUS.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050155 | 2005-11-11 12:24 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1500 | 2005-09-28 | 2005 | [6 empty] | 28 3' 49" | 91 29' 10" | OFFSHORE |  | GREEN CANYON | 237 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61000000 | 36846786.1071 | 81694817.0187 | 288000 | 113937.7163 | 60712000 | 81580879.3024 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 774245 | 2005-09-28 | 1080 | 2160 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPORD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.55 | API 5L | 65000 | ERW |  |  |  | UNDER WATER |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | OTHER | HURRICANE RITA | [53 empty] | HURRICANE RITA'S PATH CROSSED OVER CHEVRON GREEN CANYON 237 TLP FACILITY DESTOYING THE FACILITY. ENTERPRISE PRODUCTS OPERATING L.P. GAS PIPELINE WAS RIPPED FROM THE FACILITY AND IS LAYING ON THE GULF SEA FLOOR. THE PIPELINE HAS BEEN ISOLATED SUBSEA AND INSPECTED WITH ROV. THE GAS PIPELINE MAY BE RECOMMISSIONED FOR SERVICE TO A NEW PRODUCER AT THE END OF 2008. NOTE: PAGE 1 5-C-OPERATOR DAMAGE EQUALS $60,712,000 AND TOTAL EQUALS $61,000,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050156 | 2005-11-11 14:48 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE COMPANY | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 830 | 2005-10-14 | 2005 |  |  |  |  | 1 | 359+23 | 28*58'59 | -91*50' 51 | OFFSHORE |  | EUGENE ISLAND | 133 |  | YES | NO | INTERSTATE | OTHER | PIPE SEPARATED SUB-SEA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1550000 | 929904.528 | 2035384.3414 | 50000 | 19780.8535 | 1500000 | 2015603.4878 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 776070 | 2005-10-14 | 1200 | 1300 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12.75 | 0.38 |  | 46000 |  |  | UNKNOWN | 1968 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM-RELATED DAMAGE -- HURRICANE RITA | [51 empty] | ANR PIPELINE 12-INCH LINE NO. 747 WAS SEVERED IN EUGENE ISLAND BLOCK 133, DURING HURRICANE RITA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050157 | 2005-11-11 14:59 | SUPPLEMENTAL FINAL | 2731 |  | CHEVRON PIPE LINE COMANY | 4800 FOURNACE PLACE | BELLAIRE | HARRIS | TX | 77401 | 1437 | 2005-10-16 | 2005 | [6 empty] | 30-5-24 | 88-10-17 | OFFSHORE |  | MOBILE | 864 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255000 | 154211.2207 | 342652.5929 | 0 | 0 | 255000 | 342652.5929 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 776328 | 2005-10-16 | 993 | 1440 | YES | NO | NO | NO | NO | NO | HENRY L. LEGER | 3376548915 | HENRYLEGER@CHEVRON.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 12 | 375 | API 5L X42 | 42000 | SEAMLESS | N/A |  |  | UNDER WATER |  | 36 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | OTHER | SEA BOTTOM MOVEMENT | [53 empty] | THE SUBJECT 12-INCH PIPELINE IS PART OF THE CHANDELEUR NATURAL GAS PIPELINE SYSTEM LOCATED IN THE GULF OF MEXICO WHICH WAS IMPACTED BY HURRICANE KATRINA. AT THE TIME THE LEAK WAS DISCOVERED, THE SUBJECT SEGMENT WAS ISOLATED AND OUT OF SERVICE BECAUSE OF STORM IMPACTED UPSTREAM SEGMENTS. IT IS SPECULATION THAT WAVE ACTION BROUGHT ON BY THE HURRICANE CHURNED UP THE SEA BOTTON WHICH MAY HAVE MOVED THE PIPELINE SOMEWHAT AND CAUSED A FLANGE ON A SUB-SEA TIE-IN TO DEVELOP A LEAK. DIVERS WERE SENT DOWN NOTING THAT NO MOVEMENT OF THE PIPELINE WAS APPARENT. THE DIVERS SUBSEQUENTLY TIGHTENED THE FLANGE THEREBY SECURING THE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050158 | 2005-10-26 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION, LP | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1300 | 2005-09-27 | 2005 |  |  |  |  | 10.4 | 530+20 | 28.5364 | 92.8142 | OFFSHORE |  | EAST CAMERON | 222 |  | YES | NO | INTERSTATE | OTHER | SEE F7 & G | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11000000 | 5757313.4402 | 9092380.7149 | 6000000 | 2373702.4221 | 5000000 | 6718678.2928 | 0 | 0 | NO | NO | NO | NO | 0 |  | 24 | 0 | 774090 | 2005-09-27 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | DWAYNE TESCHENDORF - PRINCIPAL ENGINEER | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | OTHER | PLATFORM DESTRUCTION (HURRICANE RITA) | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 12 | 0.38 | 5L | 42000 | SMLS |  | US STEEL | 1975 | UNDER WATER |  | 30 | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | A PLATFORM IN EAST CAMERON BLOCK 222 OWNED AND OPERATED BY ENERGY RESOURCES TECHNOLOGY (ERT) WAS DESTROYED BY HURRICANE RITA CAUSING TEXAS EASTERN'S 12-INCH LINE 41-A-2-B TO BE SEPARATED NEAR THE SITE OF THE PLATFORM.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050159 | 2005-10-31 | SUPPLEMENTAL | 22175 |  | TARGA MIDSTREAM SERVICES LP. | 1000 LOUISIANA SUITE 4700 | HOUSTON | HARRIS | TX | 77002 | 900 | 2005-09-24 | 2005 | [6 empty] | 29,08,2082 | 93,17.4350 | OFFSHORE |  | WEST CAMERON | 229A |  | YES | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343000 | 156268.7428 | 135696.6551 | 343000 | 135696.6551 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774344 | 2005-09-29 | 900 | 1300 | NO | YES | NO | NO | NO | NO | TIM HUFFER, ES&H ADVISOR | 3375834642 | TIM.HUFFER@DYNEGY.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO |  |  | 1969 | 12 | 0.31 | API 5LX | 52000 | SMLS |  |  | 1969 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | STORM SURGE | [51 empty] | HURRICANE FORCE WINDS AND STORM SURGE FROM HURRICAN RITA IMPACTED DYNEGY MIDSTREAM SERVICES, LIMITED PARTNERSHIP PLATFORM IN WC 229 A ON 9/24/05/. THE TIME OF DAY THE DAMAGE OCCURRED IS NOT KNOWN. THE PLATFORM SUSTAINED MAJOR DAMAGE AND THE STRUCTURE IS NOW COMPLETELY UNDER THE SURFACE OF THE WATER. THE RISER TO THE PLATFORM FROM DYNEGY'S 12 INCH PIPELINE WAS DAMAGED ALONG WITH THE PLATFORM AND IS ALSO UNDER THE WATER SURFACE. DYNEGY'S PELICAN GATHERING SYSTEM WAS NOT FLOWING AT THE TIME OF THE INCIDENT. DIVERS HAVE LOCATED THE PLATFORM TO DETERMINE THE NATURE OF THE DAMAGE. THE EXACT NATURE OF THE DAMAGE TO THE PIPELINE HAS NOT BEEN DETERMINED AT THIS TIME. BECAUSE OF THE DAMAGE TO THE PLATFORM, THE PRESSURE HAS BEEN REDUCED FROM 900 PSIG PRIOR TO THE STORM TO 20PISG. ADDITIONAL INSPECTIONS OF THE PIPELINE ARE PLANNED TO DETERMINE THE OVERALL INTEGRITY OF THE PIPELINE. EVALUATIONS OF THE METHOD AND COST TO REPAIR THE PIPELINE IS IN PROGRESS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050160 | 2005-10-31 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1200 | 2005-09-24 | 2005 | [6 empty] | 28.6' N | 90.47' W | OFFSHORE |  | SOUTH TIMABLIER | 146 |  | YES | NO | INTERSTATE | OTHER | DAMAGED BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258650 | 156418.5578 | 347557.2281 | 0 | 0 | 258650 | 347557.2281 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 774330 | 2005-09-29 | 0 | 1200 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENERGY.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 6 | 0.28 | API 5LX | 42000 | SMLS |  | NORTH STAR | 1968 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA | [51 empty] | HURRICANE RITA CAUSED THE ENERGY RESOURCES ST 146 PLATFORM A TO TOPPLE, WHICH RESULTED IN DAMAGE TO THE 6 INCH PIPELINE, OPERATED BY TRUNKLINE GAS COMPANY. THE ENERGY RESOURCES PLATFORM HAD BEEN PREVIOUSLY DAMAGED DUE TO HURRICANE KATRINA, BUT TRUNKLINE GAS COMPANY'S PIPELINE WAS UNAFFECTED BY KATRINA. HOWEVER, AS A PRECAUTION, THE PIPELINE HAD ALREADY BEEN ISOLATED, BLOWN DOWN AND MADE SAFE, BEFORE THE PLATFORM INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050161 | 2005-10-31 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 500 | 2005-09-24 | 2005 | [6 empty] | 28.39 N | 91.924 W | OFFSHORE |  | SOUTH MARSH ISLAND | 128 |  | YES | NO | INTERSTATE | OTHER | PIPE DAMAGED BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14679738 | 8875108.7992 | 19710043.4522 | 16500 | 6527.6817 | 14663238 | 19703515.7705 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 774082 | 2005-09-27 | 1150 | 1440 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 24 | 0.5 | API 5LX | 60000 | SAW |  | KAISER | 1977 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA | [51 empty] | HURRICANE RITA CAUSED THE DEVON SMI128 PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO SEA ROBING PIPELINE'S 24 INCH PIPELINE. THE 24 INCHE PIPELINE DID NOT LOSE PRESSURE, BUT IT IS ANTICIPATED THAT IT IS DAMAGED. THE PIPELINE HAS BEEN ISOLATED AND MADE SAFE. DIVERS HAVE NOT BEEN AVAILABLE TO INVESTIGATE THE FAILURE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050162 | 2005-10-31 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 500 | 2005-09-24 | 2005 | [6 empty] | 28.26' N | 91.81' W | OFFSHORE |  | EUGENE ISLAND | 333 |  | YES | NO | INTERSTATE | OTHER | DAMAGED BY DOWNED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569347 | 344123.8507 | 763852.496 | 1265 | 500.4556 | 568082 | 763352.0404 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 20 | 774084 | 2005-09-27 | 950 | 1440 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT ASSOCIATE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | USS | 1977 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA | [51 empty] | HURRICANE RITA CAUSED THE DEVON EI333A PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO SEA ROBIN PIPELINE COMPANY'S 12 INCH PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050163 | 2005-10-31 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 500 | 2005-09-24 | 2005 | [6 empty] | 28.76' N | 91.81' W | OFFSHORE |  | EAST CAMERON | 195 |  | YES | NO | INTERSTATE | OTHER | PULLED APART BY DOWNED PLATFORM | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522801 | 316089.2668 | 702032.2867 | 500 | 197.8085 | 522301 | 701834.4782 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 | 0 | 773965 | 2005-09-27 | 930 | 1250 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT ASSOCIATE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | JONES & LAUGHLIN | 1970 | OTHER | ON PLATFORM BRIDGE |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA | [51 empty] | HURRICANE RITA CAUSED THE AMERITECH EC195A PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO THE SEA ROBIN PIPELINE COMPANY'S 12 INCH PIPELINE. THE PIPE WAS MOUNTED ON A BRIDGE BETWEEN TWO PLATFORMS. THE LINE WAS SHUT IN AT THE TIME OF THE INCIDENT. THE PIPELINE WAS ISOLATED AND MADE SAFE. 12 INCH PIPE WAS ABANDONED AND REMOVED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050164 | 2005-10-31 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 500 | 2005-09-24 | 2005 | ABBEVILLE | VERMILLION | LA | 70510 | MP 3.5 | 186+03 | 29.82 | 92.23 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BROKEN INSTRUMENT TUBING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 36462.4358 | 31744.1775 | 79900 | 31609.8039 | 100 | 134.3736 | 0 | 0 | NO | NO | NO | NO | 0 |  | 192 | 0 | 773918 | 2005-09-26 | 925 | 1056 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MEHOVIS@PANHANDLEENERGY.COM | TRANSMISSION | OTHER | STAINLESS STEEL INSTRUMENT TUBING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1990 | [7 empty] | 1990 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | FLOOD MOVEMENT | [51 empty] | IT WAS DISCOVERED THAT A LEAK WAS BUBBLING IN THE FLOODWATERS, AFTER HURRICAN RITA. DUE TO THE HIGH FLOOD WATERS, NO ONE COULD REACH THE LOCATION FOR SEVERAL DAYS. ON THE EIGHTH DAY AFTER THE HURRICANE, THE PRODUCER WAS ABLE TO REACH THE SITE USING A SWAMP BUGGY AND FOUND THAT THE 1/2 INCH STAINLESS STEEL INSTRUMENT METER TUBING HAD BEEN SEVERED. HE CLOSED THE 1/2 INCH INSTRUMENT TUBING VALVE. IT IS SURMISED THAT THE BUILDING FLOATING IN THE FLOODWATERS PULLED THE TUBING AWAY FROM THE PIPING, SEVERING THE TUBING. 99% OF THE LOSS AT THIS LOCATION IS DUE TO GAS LOSS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050165 | 2005-11-04 | SUPPLEMENTAL FINAL | 12408 |  | MICHIGAN CONSOLIDATED GAS COMPANY | 2000 SECOND AVENUE | DETROIT | WAYNE | MI | 48226 | 1050 | 2005-10-04 | 2005 | WYOMING | KENT | MI | 49548 | 55' WEST OF ROGER B CHAF |  | 42.88425 | -85.65164 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 74351.118 | 160068.1814 | 8331 | 3295.8858 | 116669 | 156772.2955 | 0 | 0 | YES | NO | NO | YES | 50 | PRECAUTIONARY | 14 | 10 | 774933 | 2005-10-04 | 299 | 300 | NO | NO | YES | NO | NO | NO | JOSEPH A. DIDIA | 3132356921 | DIDIAJ@DTEENERGY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 22 | 0.25 | API5L GRADE B | 35000 | ERW |  | UNKNOWN |  | UNDER PAVEMENT |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | YES | 9 | 27 | 2005 | ONE-CALL SYSTEM | NO | [40 empty] | ON SEPTEMBER 27, 2005, MICHCON RECEIVED A NOTICE THROUGH THE MICHIGAN ONE-CALL CENTER (MISS DIG SYSTEMS, INC.) OF EXCAVATION OPERATIONS TO BE CONDUCTED BY DEWITT TRENCHING CONTRACTORS, INC. (DEWITT) ON THE SOUTHEAST, SOUTHWEST, AND NORTHWEST CORNERS OF THE INTERSECTION OF 44TH STREET S.E. AND ROGER B CHAFFEE BOULEVARD IN THE CITY OF WYOMING, MICHIGAN. IN RESPONSE TO THIS NOTICE, A MICHCON REPRESENTATIVE VISITED THE SITE ON SEPTEMBER 29, 2005, AND PROVIDED TEMPORARY MARKINGS CONSISTING OF FLAGS AND PAINT IN THE AREA REQUESTED. MICHCON'S REPRESENTATIVE CONTACTED DEWITT'S REPRESENTATIVE AT THE SITE AND DISCUSSED THE LIMITS OF THE WORK AND THE METHODS TO BE USED. DEWITT'S REPRESENTATIVE WAS VERBALLY MADE AWARE OF THE PRESENCE OF A 22" 300 PSI PIPELINE UNDER THE WESTBOUND LANES OF 44TH STREET, BUT BECAUSE OF HEAVY VEHICLE TRAFFIC IN THE AREA PAINT MARKS WOULD BE HAZARDOUS TO MAKE AND WOULD NOT LAST FROM VEHICLE WEAR. DEWITT'S REPRESENTATIVE STATED TO MICHCON'S REPRESENTATIVE THAT HE WOULD NOT NEED STAKING ON TEH NORTHWEST CORNER BECAUSE PLASTIC CONDUITS HAD ALREADY BEEN RUN UNDERNEATH THE NEW ROADWAY ON THE NORTH SIDE AND THAT THE BORING WORK WOULD NOT EXTEND TO THE NORTHWEST CORNER, SO MARKINGS FOR THE 22" PIPELINE WERE NOT NECESSARY. ON OCTOBER 4, 2004 AT APPROXIMATELY 10:50 AM MICHCON RECEIVED A REPORT THAT A PIPLINE HAD BEEN STRUCK BY AN EXCAVATOR AT THE CORNER OF 44TH STREET SE AND ROGER B CHAFFEE BOULEVARD. RESPONDING TO THAT REPORT, MICHCON ARRIVED AT THE SITE AT 11:03 AM AND FOUND THAT THE 22" 300 PSI PIPELINE HAD BEEN STRUCK BY A BORING MACHINE OPERATED BY DEWITT. THE 2-INCH BORING HEAD HAD PUNCTURED THE 22" PIPE AT A DEPTH OF APPROXIMATELY 41 INCHES FROM STREET GRADE; THE TOP OF THE 22" PIPE WAS FOUND AT 36 INCHES BELOW STREET GRADE. DEWITT'S REPRESENTATIVE STATED TO MICHCON THAT HE KNEW THE PIPELINE WAS THERE BUT THAT HE DECIDED TO BORE IN THE AREA OF THE 22" PIPELINE ANYWAY, AND THAT HE THOUGH THE 22" PIPELINE SHOULD HAVE BEEN DEEPER AT THAT LOCATION. NOTE: ALTHOUGH MISS DIGS WAS NOTIFIED AND RESPONDED AND RESPONDED TO THE AREA, THERE WERE NO MISS DIGS MARKS AT THE LOCATION OF THE DAMAGE. I QUESTIONED THE CONTRACTOR AS TO WHY HE DIDN'T CALL FOR ADDITIONAL STAKING AND HE REPLIED, "I KNEW THE MAIN WAS THERE."
2022-01-31 10:32 | YES | YES | GG (Gas Gathering) | 20050166 | 2005-11-08 | ORIGINAL FINAL | 4511 |  | EQUITRANS, LP | 225 NORTH SHORE DRIVE | PITTSBURGH | ALLEGHENY | PA | 15212 | 1410 | 2005-10-06 | 2005 | GLENVILLE | GILMER | WV | 26351-1306 | GLENVILLE COMPRESSOR STAT |  | 38.935 | -80.838 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 1 | 775233 | 2005-10-06 | 0 | 150 | NO | NO | YES | NO | NO | NO | JOE LOMBARDO, PIPELINE SAFETY ENGINEER | 4123953135 | JLOMBARDO@EQT.COM | GATHERING | OTHER | NOT A FAILURE | STEEL |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | INADEQUATE SAFETY PRACTICES |  | 0 | 0 | N | 6 |  |  | CONSTRUCTION WORK WAS IN PROGRESS AT GLENVILLE COMPRESSOR STATION. THE STATION HAD BEEN SHUT DOWN, BLOWN DOWN AND LOCKED OUT/TAGGED OUT. ONE 3" AND TWO 8" ABOVEGROUND VALVES HAD BEEN REMOVED BY CONTRACTOR PERSONNEL AS PART OF THE CONTRUCTION AND A GAS-TRAC WAS UTILIZED PERIODICALLY TO CHECK FOR THE PRESENCE OF GAS AT THE OPEN VALVE FLANGES. NO GAS HAD BEEN DETECTED PRIOR TO THE INCIDENT. A CONTRACTOR EMPLOYEE WAS USING AN ELECTRIC GRINDER TO REMOVE A GASKET AT TEH 3" ELEVATED ABOVEGROUND FLANGE WHILE ANOTHER CONTRACTOR EMPLOYEE WAS WORKING BELOW THE 3" VALVE FLANGE ON AN 8" ABOVEGROUND VALVE FLANGE. A FLASH OCCURRED AT THE 8" VALVE FLANGE WHICH BURNED THE CONTRACTOR EMPLOYEE THAT WAS WORKING ON THE 8" VALVE FLANGE AND THE CONTRACOTR EMPLOYEE WORKING ON THE 3" VALVE FLANGE. IT IS BELIEVED THE SPARKS EMANATING FROM THE GRINDER WHEEL WERE THE HEAT SOURCE FOR THE FLASH. IT IS BELIEVED THE FUEL FOR THE FIRE CAME FROM INSIDE THE 8" PIPE. THE EXACT LOCATION AND SOURCE OF FUEL INVOLVED IN THE FLASH FIRE COULD NOT BE DETERMINED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050167 | 2005-11-17 11:32 | SUPPLEMENTAL | 11272 |  | LAVACA PIPELINE | 103 FANIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 | 1800 | 2005-10-19 | 2005 | [6 empty] | 28.36.686 | 96.32.000 | OFFSHORE |  | LAVACA BAY | ST25 | TX | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34700 | 19687.1648 | 38378.9956 | 8700 | 3441.8685 | 26000 | 34937.1271 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 0 | 776781 | 2005-10-19 | 710 | 980 | NO | YES | NO | NO | NO | YES | ROBERT C. SERRATA | 3619878914 | ROBERTS@FTPC.FPCUSA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 10 | 0.32 | A | 35000 | LAP WELD |  |  |  | UNDER WATER |  | 60 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DURING AN INTEGRITY TEST ON STEAMBOAT PASS/ MAGNOLIA BEACH LINE |  | THE PIPE LINE RUPTURED DURING THE BASELINE INTEGRITY TEST. THE LINE OPERATE AT 500 PSI AND WAS GOING TO BE TESTED TO 750 PSI. THE RUPTURING PRESSURE WAS 710 PSI. THE SECTION OF PIPE HAS BEEN REPLACE WITH CLASS B PIPE. THE SYSTEM HAS BEEN PUT BACK IN TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050168 | 2005-11-17 16:30 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1715 | 2005-10-19 | 2005 | CORNUDAS | HUDSPETH | TX |  | 159+2635 |  | 31*40'35 | 105*42'42 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143000 | 71116.1776 | 94497.9846 | 103000 | 40748.5582 | 40000 | 53749.4263 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 30 | 776783 | 2005-10-19 |  | 837 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 26 | 0.3 | API | 52000 | SEAMLESS |  | NATIONAL TUBE | 1947 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDER INVESTIGATION | YES | 1966 | NO | [57 empty] | A SMALL LEAK WAS DISCOVERED ON THE 1100 LINE DURING AN ANOMALY INVESTIGATION AT DIG SITE 3, BETWEEN VALVES 19 AND 20.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20050169 | 2005-11-18 09:22 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1000 | 2005-11-09 | 2005 | BELLEVUE | JACKSON | IA | 52031 | 3.72 | 19633 | 42.23113 | -90.48561 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 299000 | 178284.5657 | 385658.9459 | 17000 | 6725.4902 | 32000 | 42999.5411 | 250000 | 335933.9146 | NO | NO | YES | NO | 0 |  | 8 | 0 | 778985 | 2005-11-09 | 733 | 960 | NO | YES | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 3 | 0.16 | 5L | 35000 | ERW |  | USSTEEL | 1966 | UNDER GROUND |  | 0 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | ON NOVEMBER 9 AT APPROXIMATELY 10:00 AM, A CATERPILLAR D8 BULLDOZER, OPERATED BY JOSH SCHECKEL, STRUCK THE 3-INCH, BELLEVUE BRANCH LINE (IAB78501) NEAR MP 3.31 IN JACKSON COUNTY, IA. THE LINE WAS PUNCTURED BY THE BULLDOZER, TORN IN TWO AND THE ESCAPING GAS IGNITED. JOSH SCHECKEL VACATED THE BULLDOZER, WHICH WAS FULLY ENGULFED IN FLAMES. AS A RESULT OF THE LINE RUPTURE AND FIRE, GAS SERVICE WAS INTERRUPTED TO THE TOWN OF BELLEVUE, IA. JOSH SCHECKEL WAS TRANSPORTED TO THE UNIVERSITY OF IOWA BURN CENTER IN IOWAS CITY, WITH REPORTED SECOND DEGREE BURNS ON HIS HANDS AND NECK AND THIRD DRGREE BURNS ON HIS FACE. JOSH SCHECKEL WAS IN THE PROCESS OF LEVELING THE GROUND BEHIND THE SCHECKEL HEAVY EQUIPMENT SALES AND RENTAL BUSINESS AT 21582 HIGHWAY 62 FOR PLANNED FUTURE EXPANSION. NORTHERN DETERMINED THAT THE LINE WAS HIT DUE TO THE FAILURE OF THE EQUIPMENT OPERATIOR TO NOTIFY THE IOWA ONE-CALL CENTER PRIOR TO PERFORMING THE EXAVATION ACTIVITIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050170 | 2005-11-18 14:11 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1819 | 2005-11-10 | 2005 | STANTON | POWELL | KY | 40380-0187 |  |  | 37:53:00 | 83:52:00 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | GAS RELEASE DUE TO EMERGENCY SHUTDOWN ACTIVATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414311 | 250297.0867 | 555088.0117 | 1726 | 682.8351 | 412585 | 554405.1767 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 779182 | 2005-11-10 | 810 | 1050 | NO | YES | NO | NO | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION | OTHER | COMPRESSOR ENGINE |  |  | NO | NO | NO | COMPRESSOR |  | 1954 | [8 empty] | INSIDE/UNDER BUILDING |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | INVESTIGATION AND ANALYSIS HAS DETERMINED THAT MOST LIKELY ROOT CAUSE OF ENGINE FAILURE WAS HIGH CYCLE FATIGUE FAILURE OF POWER CYLINDER ROD STUD BOLTS. |  | COMPRESSOR ENGINE (COOPER BESSIMER LSV UNIT) FAILURE RESULTING IN A RELEASE OF NATURAL GAS FROM AN EMERGENCY SHUTDOWN.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050171 | 2005-11-30 15:32 | SUPPLEMENTAL FINAL | 2859 |  | CRANBERRY PIPELINE CORPORATION | 900 LEE STREET, EAST SUITE 500 | CHARLESTON | KANAWHA | WV | 25301 | 1605 | 2005-11-03 | 2005 | DANVILLE | BOONE | WV | 25053 | N/A | 1538+55 | 38 05 13.5N | 81 53 8.8W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27850 | 14217.1408 | 20736.1509 | 17600 | 6962.8604 | 10250 | 13773.2905 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 778473 | 2005-11-04 | 200 | 200 | NO | NO | YES | NO | NO | NO | MICHAEL F. GOFF | 3043471664 | MIKE.GOFF@CABOTOG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1985 | 10 | 0.25 | API 5L | 42000 | SEAMLESS | N/A | UNKNOWN | 1985 | UNDER GROUND |  | 112 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 10 | 26 | 2005 | CONTRACTOR | YES |  | YES | ACCURATE | YES | [36 empty] | C.J. HUGHES (CONTRACTOR FOR) EASTERN AMERICA WHILE ATTEMPTING TO BORE A PIPELINE CROSSING BENEATH CRANBERRY PIPELINE CORPORATION'S B-1014 PIPELINE MISSED THE TARGET RECEIVING PIT AND PUNCTURED CRANBERRY'S PIPELINE WITH CONSEQUNCES AS NOTED ABOVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050172 | 2005-12-01 10:14 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | -7-7002 | 1000 | 2005-11-02 | 2005 |  |  |  |  | SV 823X-3801 + 0.00 | 823X-3701+ 6.97 | 29*14'38.6475 | -91*53' 58.2652 | OFFSHORE |  | SOUTH MARSH ISLAND | 252 |  | YES | NO | INTERSTATE | OTHER | DAMAGED DURING 2005 STORMS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 347934.3429 | 711429.5363 | 100000 | 39561.707 | 500000 | 671867.8293 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 778250 | 2005-11-02 | 1250 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | STORM DAMAGE | STEEL |  | NO | NO | NO | PIPELINE |  | 1998 | 8.63 | 0.32 | API | 35000 | SEAMLESS |  | US STEEL | 1998 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE RITA DAMAGE | [51 empty] | A LEAK WAS DISCOVERED AS LINE NO. 823X-3800 WAS BEING RETURNED TO SERVICE, FOLLOWING STORM DAMAGE ASSESSMENT. A PRESSURE LOSS WAS NOTED AT METER STATION 1-2400. LEAK WAS ACTUALLY DISCOVERED NEAR SUB-SEA TIE-IN TO LINE NO. 823X-3700, ON THE 8-INCH PIPELINE. A 2" BYPASS HAD BEEN BROKEN DURING HURRICANE RITA. IT WAS REPAIRED IN APRIL 2006 WITH THE LINE BEING RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050173 | 2005-12-06 18:50 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PIPELINE OPERATING, LP | 2707 NORTH LOOP WEST | HOUSTON | HARRIS | TX | 77382 |  | 2005-11-07 | 2005 | [6 empty] | 28.05.070 | 96.16.831 | OFFSHORE |  | MI | 638 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368000 | 222100.4901 | 491650.3666 | 3000 | 1186.8512 | 365000 | 490463.5154 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 778780 | 2005-11-07 | 1000 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7138032494 | JMCDONALD@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | [7 empty] | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | DID NOT REMOVE PIPE | OTHER | UNKNOWN-INTERNAL | YES | 1989 | NO | [57 empty] | LEAK AREA WAS REPAIRED WITH A CLAMP. LINE WAS NOT CUT SO WE COULD NOT INVESTIGATE FURTHER CAUSE OF LEAK.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050174 | 2005-12-06 19:08 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PIPELINE OPERATING LLC. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 610 | 2005-10-29 | 2005 | [6 empty] | 2813.0 | 9410.0 | OFFSHORE |  | HI | 489 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1805000 | 1090827.7635 | 2420702.2708 | 5000 | 1978.0854 | 1800000 | 2418724.1854 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 777880 | 2005-10-29 | 1100 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 16 | 0.44 | API 5L | 52000 |  |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | MICROBIOLOGICAL |  | YES | 1981 | NO | [57 empty] | SECURED DIVE VESSEL AND DIVERS TO INVESTIGATE SUSPECTED AREA. SEVERAL ATTEMPTS TO REPAIR PIPELINE WERE NOT SUCCESSFUL. THE PIPELINE WAS DEPRESSURIZED AND DISCONNECTED AT EACH END. THIS PIPELINE IS SCHEDULED TO BE ABANDONED FOURTH QUARTER 2007.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20050175 | 2005-12-06 19:34 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PIPELINE OPERATING, LP | 2707 NORTH LOOP WEST | HOUSTON | HARRIS | TX | 77382 | 1113 | 2005-10-25 | 2005 | [6 empty] | 28.15.7 | 93.56.7 | OFFSHORE |  | HIA | 469 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340000 | 205167.4933 | 454025.7681 | 3000 | 1186.8512 | 337000 | 452838.9169 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 777376 | 2005-10-25 | 1053 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7133812494 | JMCDONALD@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 8.63 | [7 empty] | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | UNKNOWN | OTHER | UNKNOWN | YES | 1980 | NO | [57 empty] | REPAIR COMPLETED. REPAIR WAS MADE USING A CLAMP ON THE PIPELINE INSTALLED OVER THE AFFECTED AREA OF THE LEAK. THE PIPELINE WAS NOT CUT OPEN AND THEREFORE AN INVESTIGATION OF THE INTERNAL CORROSION DAMAGE WAS NOT POSSIBLE. THIS IS AN OFFSHORE GATHERING PIPELINE WITH MINIMAL FLOW. THE PIPELINE HAS BEEN ADDED TO OUR INTERNAL PROTECTION PROGRAM AND IS BEING TREATED WITH A CORROSION INHIBITOR.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050176 | 2005-12-08 14:41 | SUPPLEMENTAL FINAL | 11820 |  | BRIDGELINE HOLDINGS, L.P. | 4800 FOURNACE PLACE | BELLAIRE | HARRIS | TX | 77401-2324 | 102 | 2005-12-03 | 2005 | HOLLY BEACH | CAMERON | LA | 70631 | MILE POST 3 |  | N29 - 49.436 | W93 - 26.273 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 48 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123900 | 74346.8028 | 162791.1856 | 3900 | 1542.9066 | 120000 | 161248.279 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 0 | 781297 | 2005-12-03 | 905 | 1440 | YES | NO | NO | NO | NO | NO | HENRY L. LEGER | 3376548915 | HENRYLEGER@CHEVRON.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 8 | 219 | API 5LX 42 | 42000 | ERW | N/A | NIPPON | 1977 | UNDER WATER |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | THE SUBJECT PIPELINE IS AN INTRASTATE NATURAL GAS PIPELINE AND IS JURISDICTIONAL TO THE LOUISIANA DEPARTMENT OF NATURAL RESOURCES, OFFICE OF CONSERVATION. THE SUBJECT PIPELINE WAS HIT BY 3RD PARTY EXCAVATION. EXCAVATION WAS OBSERVED IN THE AREA BY A 3RD PARTY WITNESS JUST PRIOR TO THE INCIDENT . THE SUBJECT PIPELINE WAS MARKED ADEQUATELY ON EACH SIDE OF THE RUPTURE WITH PERMANENT LINE MARKERS HAVING BRIDGELINE HOLDINGS, L.P.'S 24-HOUR EMERGENCY PHONE NUMBER ON THEM. BRIDGELINE HOLDINGS, L.P. DID NOT RECEIVE A REQUEST TO LOCATE THE SUBJECT PIPELINE FROM ANYONE INCLUDING,LOUISIANA ONE CALL OR THE EXCAVATING CONTRACTOR PRIOR TO THE INCIDENT. THE SUBJECT PIPELINE WAS HIT BY THE 3RD PARTY EXCAVATING CONTRACTOR AND RUPTURED AFTER THE CONTRACTOR LEFT THE AREA. THE SUBJECT PIPELINE INCIDENT TOOK PLACE IN SECTION 24, TOWNSHIP 14 SOUTH, RANGE 10 WEST OF CAMERON PARISH, LA. THE PIPELINE WAS REPAIRED AS PER CODE ON JANUARY 20, 2006 BY CUTTING OUT THE DMAGED PIPE AND REPLACING IT WITH 36-FEET OF PRE-TESTED PIPE OF THE SAME SIZE, WALL THICKNESS AND GRADE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050177 | 2005-12-12 13:18 | SUPPLEMENTAL FINAL | 13710 |  | NICOR GAS | 1844 FERRY ROAD | NAPERVILLE | DUPAGE | IL | 60563 | 31 | 2005-11-13 | 2005 | PLANO | KENDALL | IL | 60545 |  |  | 41.666987N | 88.53838W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82432 | 48742.216 | 103720.4005 | 7432 | 2940.2261 | 70000 | 94061.4961 | 5000 | 6718.6783 | NO | NO | NO | NO | 0 |  | 2 | 5 | 779380 | 2005-11-13 | 425 | 858 | NO | YES | NO | NO | NO | NO | LETICIA QUEZADA | 6303882316 | LQUEZAD@NICOR.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | OTHER | NIPPLE FITTING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2000 | 0.5 | 0.15 | A106 | 35000 |  |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | DRIVER LOST CONTROL OF PICK-UP TRUCK, TRAVELING ABOUT 150 YARDS ACROSS A FARM FIELD, GOING THROUGH THE REGULATING STATION FENCE AND STRIKING THE ABOVE-GROUND BYPASS VALVE PIPING. A 1/2" GAUGE NIPPLE ON THE ABOVE-GROUND BYPASS PIPING WAS SHEARED OFF.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050178 | 2005-12-12 17:08 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1130 | 2005-11-14 | 2005 |  |  |  |  | 523M-6501 + 0.82 |  | 28*39'21.947 | -90*58'41.707 | OFFSHORE |  | SHIP SHOAL | 168D |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 446104.6198 | 960395.8145 | 50000 | 19780.8535 | 700000 | 940614.961 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 779499 | 2005-11-14 | 1100 | 1200 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 6.63 | 0.31 | API | 42000 | SEAMLESS |  | US STEEL | 1982 | UNDER WATER |  | 54 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | DAMAGE DUE TO HURRICANE KATRINA | [51 empty] | FOLLOWING DAMAGE ASSESSMENT AFTER HURRICANE KATRINA, IT WAS DISCOVERED THAT THE 6-IN TGP LINE NO. 523M-6500 WAS SEVERED FROM THE PLATFORM PIPING AT THE SHIP SHOAL BLOCK 168D PLATFORM. THE PIPELINE HAS SINCE BEEN REPAIRED AND PLACED BACK INTO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050179 | 2005-12-13 12:44 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORPORATION | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84102 | 1250 | 2005-11-03 | 2005 | HANSEN | TWIN FALLS | ID | 83334 | 691.5 | 15822+32 | 42 29¿ 30 ¿¿ | 114 13¿ 33¿¿ | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 38725.4902 | 33627.451 | 85000 | 33627.451 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 778421 | 2005-11-03 | 733 | 850 | YES | NO | NO | NO | NO | NO | LANCE A. HOBBS | 8015846785 | LANCE.HOBBS@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 22 | 0.25 | API 5L | 52000 | ERW |  | CONSOLIDATED WESTERN | 1955 | OPEN DITCH |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | STRAY CURRENT |  | YES | 1957 | NO | [57 empty] | DURING THE REMEDIATION OF AN ANOMALY, A CORROSION PIT DEVELOPED A PIN HOLE LEAK NEAR MP 691.5 ON NORTHWEST PIPELINE¿S 22¿ LINE. NWP PERSONNEL WERE ON SITE WHEN THE LEAK STARTED AND THE DECISION WAS QUICKLY MADE TO ISOLATE THAT SECTION OF PIPE BY CLOSING MV 10-0 AND 10-1 (13.5 MILES BETWEEN THE VALVES). IN THE INTEREST OF SAFETY, THE SEGMENT WAS BLOWN DOWN (RESULTING IN A GAS LOSS IN EXCESS OF $50,000) AND A 22¿X14¿ LEAK CLAMP WAS INSTALLED. THE LINE WAS SLOWLY REPRESSURIZED AND AFTER A FEW ADJUSTMENTENTS TO THE CLAMP, THE PRESSURE WAS RESTORED TO ITS ORIGINAL VALUE AND THE SEGMENT RETURNED TO SERVICE. NWP IS INVESTIGATING SEVERAL OTHER ANOMALIES ALONG THE SAME SECTION OF PIPE AND INTENDS TO REPLACE THE CLAMP WITH NEW PIPE AFTER ALL OF THE ANOMALIES HAVE BEEN INVESTIGATED. THE REPLACEMENT IS TENTATIVELY SCHEDULED FOR DECEMBER 2005.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050180 | 2005-12-13 15:40 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 1651 | 2005-12-01 | 2005 | CARROLL | FAIRFIELD | OH | 43112 | CARROLL STATION | 1220+86 | 39.7994306 | -82.6958221 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | REGULATOR CONTROL LINES LEAK FROM VEHICLE IMPACT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106800 | 64587.2877 | 143510.9683 | 0 | 0 | 106800 | 143510.9683 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 54 | 781185 | 2005-12-01 | 400 | 540 | NO | YES | NO | NO | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1963 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | INCIDENT OCCURRED AS THE RESULT OF A MOTOR VEHICLE IMPACT WITH A MEASUREMENT & REGULATOR STATION BUILDING RESULTING IN DAMAGE TO THE PIPING AND EQUIPMENT. A STATION BYPASS INCLUDING REGULATION INSTALLED UNTIL STATION REBUILT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050182 | 2005-12-05 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1400 | 2005-10-29 | 2005 | [6 empty] | 28.26' N | 91.81' W | OFFSHORE |  | EAST CAMERON | 317 |  | YES | NO | INTERSTATE | OTHER | PARTIAL CIRCUMFERENTIAL TEAR | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1817220 | 1017044.1925 | 1921137.6224 | 549220 | 217280.8074 | 1268000 | 1703856.8151 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 777877 | 2005-10-29 | 950 | 1250 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@PANHANDLEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 12 | 0.5 | API 5LX | 42000 | SMLS |  | UNKNOWN | 1989 | UNDER WATER |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | IT IS SURMISED THAT HURRICANE RITA CAUSED THE OBSERVED DISPLACEMENT OF A 4 INCH PRODUCER'S LATERAL, WHICH RESULTED IN DAMAGE TO SEA ROBIN PIPELINE COMPANY'S 12 INCH, WHERE THE 4 INCH PIPELINE TIED IN. NO GAS LEAKAGE WAS PRESENT UPON INITIAL INVESTIGATION OF HURRICANE DAMAGE, BUT SUBSEQUENTLY BUBBLES WERE SPOTTED AT THIS LOCATION, WHEN PRESSURE WAS INCREASED. THE PIPELINE HAS BEEN ISOLATED AND MADE SAFE. DIVER INVESTIGATION SHOWS THAT THE 12-INCH PIPE TORE WHERE THE 4-INCH CONNECTS INTO THE 12-INCH PIPE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20050183 | 2005-12-20 10:21 | SUPPLEMENTAL FINAL | 31451 |  | KINDER MORGAN TEXAS PIPELINE CO. | 500 DALLAS ST | HOUSTON | HARRIS | TX | 77002 | 750 | 2005-09-11 | 2005 | DEER PARK | HARRIS | TX | 77536 |  |  | N29.43.815 | W095.04.892 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53521 | 32139.9525 | 70475.9878 | 1521 | 601.7336 | 52000 | 69874.2542 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 772429 | 2005-09-14 | 700 | 780 | YES | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1984 | 4 | [7 empty] | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20050184 | 2005-12-23 10:16 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1330 | 2005-12-01 | 2005 |  | NUECES | TX |  | 5A-203 + 5.57 |  | 27* 45' 22 | 97* 09' 44 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | PIPELINE DAMAGED BARGE DRAGGING ACROSS LINE. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740000 | 441846.9915 | 958335.881 | 38000 | 15033.4487 | 702000 | 943302.4323 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 781147 | 2005-12-01 | 608 | 892 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 12.75 | 0.38 | API | 42000 |  |  | JONES & LAUGHLUM | 1954 | UNDER WATER |  | 24 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A BARGE CARRYING A LOAD OF ROCK DRAGGED ACROSS THE 12-INCH TGP LINE NO. 5A-200 MUSTANG ISLAND LINE, DAMAGING IT AND CAUSING A LEAK. THIS PIPELINE HAS SINCE BEEN REPAIRED AND IS BACK IN SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060003 | 2005-12-22 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | PO BOX 770000 MAIL CODE H15E | SAN FRANCISCO | SAN FRANCISCO | CA | 94117 | 1320 | 2005-11-19 | 2005 | SALINAS | MONTEREY | CA | 93906 | LINE 103, MP 18.8 |  | 36.73933 | -121.60959 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60354 | 32717.3763 | 57061.2233 | 25354 | 10030.4752 | 35000 | 47030.748 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 10 | 780104 | 2005-11-19 | 340 | 350 | NO | NO | NO | NO | YES | NO | JIM MAGUDA, PRINCIPLE GAS ENGINEER | 4159735074 | JJMO@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 12 | 0.25 | UNKNOWN | 33000 | SSAW |  | UNKNOWN |  | UNDER GROUND |  | 24 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | OTHER | FARMING ACTIVITY ON LEASED LAND | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | EQUIPMENT OPERATOR "RIPPING" A LEASED FARM FIELD FAILED TO NOTIFY UNDERGROUNDSURVEY ALERT (USA - ONE CALL) AND IGNORED PERMANENT PIPELINE MARKERS. THE EQUIPMENT OPERATOR STRUCK THE 24" DEEP, 12.75" DIAMETER, TRANSMISSION PIPING, PUNCTURING THE LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060004 | 2005-12-27 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 930 | 2005-11-19 | 2005 | N/A | N/A |  |  | N/A | N/A | 28.51.54 N | 92.34.54 W | OFFSHORE |  | VERMILLION | 181 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1572370 | 862833.4185 | 1553108.8665 | 590370 | 233560.4498 | 982000 | 1319548.4167 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 780212 | 2005-11-19 | 950 | 1200 | YES | NO | NO | NO | NO | NO | MARVIN HOVIE PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 30 | 0.5 | AP15L X | 60000 | SAW | N/A | CRISPIN | 1970 | UNDER WATER |  | 18 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1970 | NO | [57 empty] | LEAK DEVELOPED IN 30 INCH PIPE DUE TO INTERNAL CORROSION. LEAK CLAMP HAS BEEN INSTALLED.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20060005 | 2005-12-28 | SUPPLEMENTAL FINAL | 18548 |  | SOUTHWESTERN GAS PIPELINE INC | 20 NORTH BROADWAY | OKLAHOMA CITY | OKLAHOMA | OK | 73102-8260 | 815 | 2005-11-14 | 2005 | HASLET | TARRANT | TX | 76052 |  | 21+560 | N32.98357 | W097.39787 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | OTHER | THIRD PARTY VEHICLE DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 779472 | 2005-11-14 | 300 | 1174 | NO | YES | NO | NO | NO | NO | R GLENN SMITH SREHS SPECIALIST | 4052288373 | GLEN.SMITH@DVN.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | RISER | 2001 | 16 | 0.31 |  | 52000 | ERW |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [64 empty] | INVESTIGATION COMPLETE | A THIRD PARTY DUMP TRUCK DRIVER BACKED INTO A PIPELINE RISER WHICH BROKE OFF A 2¿ BLOW DOWN VALVE. THERE WAS A VOLUNTARY EVACUATION OF SOME HOMES ON TWO STREETS. THE FIRE DEPARTMENT COULD NOT CONFIRM HOW MANY OR IF ANY RESIDENTS WERE ACTUALLY EVACUATED. THE LINE WAS X-RAYED TO ENSURE THE PIPELINE INTEGRITY BELOW GROUND AND REPAIRS WERE MADE TO THE 2¿ BLOW DOWN VALVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060006 | 2006-01-05 19:23 | SUPPLEMENTAL FINAL | 13845 |  | NORHTWEST PIPELINE COMPANY | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 110 | 2005-12-08 | 2005 | GREEN RIVER | SWEETWATER | WY | 82935 | 0.4 | 22+50 | 41N 17 53 | 109W 41 00 | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | OTHER | RUPTURE. 217' OF PIPE WERE DESTROYED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1205000 | 698892.4352 | 1429577.7509 | 200000 | 79123.4141 | 1000000 | 1343735.6586 | 5000 | 6718.6783 | NO | NO | YES | NO | 0 |  | 1 | 0 | 78765 | 2005-12-08 | 800 | 850 | NO | NO | YES | NO | NO | NO | LANCE A. HOBBS | 8015846785 | LANCE.HOBBS@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 22 | 0.5 | API 5L | 42000 | ERW |  | CONSOLIDATED WESTERN |  | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | SMALL STRESS RISER IN PIPE BODY | [10 empty] | MATERIAL DEFECT |  | NO | YES | 12 | 18 | 1991 | NATURAL GAS |  | 1 | 850 | [12 empty] | ON DECEMBER 8TH, 2005 AT 0110, THE LAST 217' OF NORTHWEST'S CIG INTERCONNECT (LENGTH ~2500') RUPTURED AND IGNITED. THE SITE IS APPROXIMATELY 1/2 MILE FOR THE NWP GREEN RIVER COMPRESSOR STATION AND DIRECTLY IN FRONT OF THE CIG METER STATION. THE METER STATION WAS DESTROYED ALONG WITH THE ENTIRE 217' OF PIPELINE. IN ORDER TO RESTORE SERVICE IN A PROMPT MANNER, NWP OPTED TO REPLACE THE ENTIRE LATERAL. ALL OF THE PIPELINE IN THE LATERAL WAS REPLACE AND RETURNED TO SERVICE DECEMBER 22, 2005. WHILE THE CONDITION OF THE PIPE MADE A DEFITE DETERMINATION "REASON FOR FAILURE" PROBLEMATIC, IT IS BELIEVED A SMALL STRESS RISER WORKING IN CONJUNCTION WITH COLD GAS TEMPERATURES WAS THE PRIMARY CAUSE OF FAILURE. COPIES OF THE METALLURGICAL REPORTS WERE SENT TO THE DENVER PHMSA OFFICE ON AUGUST 28, 2006.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060007 | 2006-01-06 15:47 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 352 | 2005-12-08 | 2005 |  | SWEETWATER | WY |  | VS 375 - 324+06 |  | 41.299573 | 109.678227 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FUEL GAS SUPPLY LINE DAMAGED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 83254.6886 | 154154.4194 | 50000 | 19780.8535 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 781766 | 2005-12-08 | 831 | 845 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | FUEL GAS SUPPLY LINE TO METER FACILITY | STEEL |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | A WILLIAMS PIPELINE RUPTURED NEAR COLORADO INTERSTATE'S (CIG) GREEN RIVER/MCKINNON JUNCTION METERING FACILITY. DEBRIS FROM THE RUPTURE BECAME AIRBORNE AND STRUCK A FUEL GAS SUPPLY LINE AT THE CIG METER STATION, RESULTING IN A RELEASE OF GAS AND HEAVY DAMAGES. THE FACILITY HAS BEEN REPAIRED AND PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060008 | 2006-01-11 11:27 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1715 | 2005-12-12 | 2005 |  |  |  |  | VS 1 | 0+ 283 | 28* 25' 25 | -91* 57' 57 | OFFSHORE |  | SOUTH MARSH ISLAND | 108 |  | YES | NO | INTERSTATE | OTHER | GAS LEAKED THROUGH END CONNECTION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 688600 | 328637.6183 | 367233.7735 | 588600 | 232860.2076 | 100000 | 134373.5659 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 782262 | 2005-12-12 | 25 | 1440 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | END CONNECTOR | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 24 | 0.41 | API | 60000 |  |  | UNKNOWN | 1979 | UNDER WATER |  | 36 | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | OTHER | END CONNECTOR NOT FULLY TIGHTENED | 0 | 0 | N | 8 |  |  | IN THE PROCESS OF REPAIRING THE ANR 614-32 PIPELINE IN SOUTH MARSH ISLAND BLOCK 108, IT WAS DISCOVERED THAT GAS WAS LEAKING THROUGH AN END CONNECTOR THAT HAD NOT BEEN FULLY TIGHTENED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060009 | 2006-01-12 15:21 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 330 | 2005-12-13 | 2005 | BIGGERS | RANDOLPH | AR | 72413 | MP 267 |  | 36.32060 | 90.82655 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | ESD SYSTEM MALFUNCTION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221000 | 100686.2745 | 87431.3725 | 221000 | 87431.3725 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 49 | 782309 | 2005-12-13 | 652 | 752 | NO | YES | NO | NO | NO | NO | JOHHNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | ESD SYSTEM | OTHER | RUBBER O-RING | NO | NO | NO | COMPRESSOR |  | 1983 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | COMBNED BAD O'RING & NEEDLE VALVES ADJUSTMENT | [10 empty] | AT 3:30 AM, DECEMBER 13, 2005 SYSTEM CONTROL NOTICES A LOSS OF PRESSURE ON MRT SYSTEM AT BIGGERS COMPRESSOR STATION. SYSTEM CONTROL NOTIFIES FIELD PERSONNEL TO INVESTIGATE. THE FIELD PERSONNEL ARRIVED AT THE STATION AT 3:40 AM AND FOUND THE 6¿ STATION ESD SUCTION BLOW DOWN OPEN AND VENTING. A SURVEY OF THE STATION YARD VALVES DISCOVERED ML2 STATION SUCTION VALVE AND DISCHARGE VALVE CLOSED, ML3 STATION SUCTION AND DISCHARGE VALVE OPEN, AND THE ESD STATION DISCHARGE BLOW DOWN VALVE CLOSED. THE ML3 STATION DISCHARGE VALVE WAS CLOSED AT 4:18 AM, THEN THE ML3 STATION SUCTION VALVE WAS CLOSED AT 4:19 AM. THIS ISOLATED THE STATION FROM THE MAIN LINES, WHICH WOULD ALLOW THE STATION PIPING TO BLOW DOWN. INVESTIGATION SHOWED THAT A NICKED ¿O¿ RING WAS FOUND IN THE SENSOR ON ML2 DISCHARGE OPERATOR, AND THE NEEDLE VALVE ORIFICES WERE OUT OF ADJUSTMENT ON ML3 STATION SUCTION VALVE AND ML3 STATION DISCHARGE VALVE. REPLACEMENT OF THE O-RING AND A NEEDLE VALVE ADJUSTMENT OF THE ML3 VALVE¿S OPERATOR WAS PERFORMED, AND UPON SUBSEQUENT ESD TEST, THE VALVES OPERATED PROPERLY. ESTIMATED LOSS OF GAS WAS 15,950 MCF.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060011 | 2006-01-19 13:27 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LP | 2727 NORTH LOOP WEST | HOUSTON | HARRIS | TX | 77382 | 920 | 2006-01-05 | 2006 | [6 empty] | 28.05.21 | 96.16.868 | OFFSHORE |  | MATAGORDA ISLAND | 638 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 174525.4319 | 381580.1823 | 10000 | 3983.7398 | 290000 | 377596.4425 | 0 | 0 | NO | NO | NO | NO | 0 |  | 24 | 0 | 784332 | 2006-01-05 | 925 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7138032494 | JMCDONALD@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.31 | [6 empty] | UNDER WATER |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | SUB SEA LEAK. A CLAMP WAS INSTALLED ON THE PIPELINE TO STOP THE LEAK. IN 2007 THE DECISION WAS MADE TO ABANDON THIS SECTION OF PIPELINE. THIS PROCESS WAS COMPLETED IN LATE 2007. DUE TO THE PIPELINE LOCATION AT THE BOTTOM OF THE GULF OF MEXICO, INFORMATION IS NOT CLEAR ON THE ACTUAL CAUSE OF THE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060012 | 2006-01-23 15:07 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1339 | 2006-01-08 | 2006 | [8 empty] | OFFSHORE |  | VERMILLION | 287D |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 92556.5017 | 185487.7406 | 32480 | 12939.187 | 132520 | 172548.5536 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 21 | 784598 | 2006-01-08 | 130 |  | NO | YES | NO | NO | NO | NO | MARK A. NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.41 | UNKNOWN |  | UNKNOWN |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | UNKNOWN | OTHER | UNKNOWN | YES | 1972 | NO | [57 empty] | ON 1-8-06 A FOREMAN FLYING OVER TO ANOTHER LOCATION REPORTED THAT HE SAW THE LEAK FROM THE AIR. THE CREW AT EUGENE ISLAND 292B BELIEVED THE LEAK WAS ON CGT'S 26" LINE AND SHUT IN VALVE 287D TO ISOLATE THE LEAK UNTIL IT COULD BE LOCATED. THE PLATFORM AFFECTING THE GAS FLOW WAS SHUT IN IMMEDIATELY UPON RECOGNITION OF THE LEAK. THE LINE WAS ALLOWED TO VENT UNTIL 1-9-06. DIVE BOATS LOCATED THE LEAK AT 6 PM CST ON 1-9-06 ON EL287D, 12" APPROXIMATELY 2606' FROM CGT 26" TIE-IN ASSEMBLY. THE COORDINATES WERE AS FOLLOWS: X: 1,891,743.2 Y: -105, 342.5 N: 28 22 36 W: 91 40 11 THE 12" LINE PRESSURE AT 8:30 AM ON 1-10-06 WAS 93 PSI, DOWN FROM THE RECORDED 130 PSI ON 1-9-06. THE LEAK ON CGT EL287D-12" WAS ISOLATED BY A SUB-SEA CHECK VALVE. ON 1/10/2006 AT 10:05AM THE INSPECTOR FLEW OVER LEAK SITE AND FOUND VERY LITTLE SERVICE BUBBLES. AT 10:40AM, PLACED E.I. 250 VALVES IN FLOW POSITION. FLEW OVER THE LEAK, NO CHANGE. AT 11:45AM - E.I. 292-B BEGAN FLOWING INTO CGT 26" PIPELINE. INSPECTOR WAITED THIRTY MINUTES FOR LINE PACK AND RETURNED TO LEAK AND FOUND NO CHANGE. AT 12:00NOON E.I. 292-B FLOW RATE AT 2.29MMCF WITH A 965PSI. AT 12:30PM - CALLED GAS CONTROL TO HAVE E.I. 273-D AND E.I 288 COME ON WITH PRODUCTION. MONITOR E.I. 287-D 12" PIPELINE PRESSURE TO INSURE CHECK VALVE IS HOLDING AND NO GAS IS ENTERING PIPELINE. ON 1/12/2006, 9:00 AM, EI292B: 1041PSI - 8.3MM, EI273D: 1068PSI - 6.8MM, AND EI287D: 82PSI. FINAL REPORT SUBMITTED ON 12/21/2007.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060013 | 2006-01-24 16:35 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 500 | 2005-12-29 | 2005 |  | ALLEN | KY |  | 89-3 + 1.2 |  | 36* 48' 12 | 86* 17' 56 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908032 | 438304.6538 | 515672.5267 | 743032 | 293956.143 | 165000 | 221716.3837 | 0 | 0 | NO | NO | NO | YES | 200 | PRECAUTIONARY | 2 | 0 | 783700 | 2005-12-29 | 700 | 750 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 30 | 0.31 | API 5L | 52000 | DSAW |  | CONSOLIDATED | 1957 | UNDER GROUND |  | 42 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 7 | 1 | 1973 | WATER |  | 8 | 1031 | [12 empty] | PIPELINE FAILURE ON TGP 30-INCH, 100-3 LINE, NEAR HALFWAY, KENTUCKY, IN ALLEN COUNTY. APPARENT PIPE FAILURE OCCURRED IN FACTORY GIRTH WELD. INVESTIGATION CONDUCTED. INVESTIGATION REVEALED THAT THE FAILURE WAS ATTRIBUTED TO THE COMBINED EFFECTS OF THE PRE-EXISTING UNDERBEAD CRACKING, INTRODUCED DURING ORIGINAL CONSTRUCTION, AND LONGITUDINAL STRESSES INDUCED BY THE TERRAIN.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060014 | 2005-12-27 | SUPPLEMENTAL FINAL | 2879 |  | ENBRIDGE PIPELINES LOUISIANA INTRASTATE L.L.C. | 13679 HWY. 23 (GLORIA COMPRESSOR STATION) RECORDS MAINTAINED | BELLE CHASSE | JEFFERSON PARISH | LA | 70037 | 1645 | 2005-11-20 | 2005 |  | JEFFERSON PARISH UNDER BA | LA | 70037 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75400 | 44117.0234 | 91902.8511 | 9930 | 3928.4775 | 65470 | 87974.3736 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 780167 | 2005-11-20 | 850 |  | YES | NO | NO | NO | NO | NO | JERRY HILL COMPLIANCE COORDINATOR | 9033234330 | JERRY.HILL@ENBRIDGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | [10 empty] | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [17 empty] | OTHER | ANCHOR DROPPED | NO |  |  |  |  | YES | [40 empty] | LEAKING PIPELINE ISOLATED. SITUATION; CONTAINED AND CONTROLLED. PIPELINE WILL BE REPAIRED PRIOR TO FACILITY COMING BACK ON LINE. IT WAS BROUGHT TO MY ATTENTION BY AN INSPECTOR WITH THE LOUISANA DNR, THAT ENBRIDGE HAD NOT FINIALIZED THIS INCIDENT REPORT. THE LINE WAS REPAIRED BY REPLACING DAMAGED PORTION OF THE 8.625", X-42, .322" WT PIPE. THE LINE WAS PRESSURE TESTED TO 1640 PSIG FOR 8 HOURS. REPAIR WAS COMPLETED AND LINE WAS PUT BACK IN SERVICE ON 11-22-05.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20060016 | 2006-01-26 08:03 | SUPPLEMENTAL FINAL | 2859 |  | CRANBERRY PIPELINE CORPORATION | 900 LEE STREET, EAST SUITE 500 | CHARLESTON | KANAWHA | WV | 25301 | 1300 | 2006-01-13 | 2006 | DANVILLE | BOONE | WV | 25053 |  | 120+00 | 38 10 38.7N | 81 44 48.5W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29141 | 14471.8829 | 19443.0417 | 20472 | 8155.5122 | 3792 | 4937.399 | 4877 | 6350.1305 | NO | NO | NO | YES | 0 |  | 4 | 0 | 785457 | 2006-01-17 | 30 | 0 | NO | NO | NO | NO | NO | NO | MICHAEL F. GOFF - CORROSION AND COMPLIANCE ENGINEER | 3043471664 | MIKE.GOFF@CABOTOG.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1938 | 10 | 0.25 | UNKNOWN | 24000 | UNKNOWN | N/A | UNKNOWN |  | UNDER GROUND |  | 30 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | SURFACE MINE RECLAMATION | NO |  |  |  |  | NO | [40 empty] | LINCOLN LEASING (CONTRACTOR TO COAL RIVER ENERGY) WHILE RECLAIMING AN ACCESS ROAD ON THE FORK CREEK(SURFACE)MINE PUNCTURED THE BURIED B-1007 CLASS 1 NONJURISDICTIONAL PIPELINE WITH A DOZER BLADE CREATING AN APPROXIMATE 6" DIAMETER HOLE. DEPTH OF COVER WAS ESTIMATED SINCE THE GROUND SURFACE HAD BEEN ALTERED BY THE DOZER ACTIVITY IN THE AREA. NO MAOP HAD BEEN ESTABLISHED ON THE REFERENCED LINE DUE TO IT BEING A NONJURISDICTIONAL GATHERING LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060017 | 2006-01-12 | SUPPLEMENTAL FINAL | 31978 |  | ATMOS PIPLINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1245 | 2005-11-28 | 2005 | COVINGTON HILL |  | TX | 76636 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116000 | 61798.2572 | 102778.6955 | 56000 | 22154.5559 | 60000 | 80624.1395 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 |  | 2005-11-28 | 580 | 800 | NO | YES | NO | NO | NO | NO | MICHAEL E. ARCHER - COMPLIANCE ANALYST | 2142062879 | MICAHEL.ARCHER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 10.75 | 0.22 | API 5L X42 | 42000 | [6 empty] | 66 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | GAS WELL SITE DRAINAGE | YES | 9 | 13 | 2005 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | AN EXCAVATOR STRUCK A GAS PIPELINE. UPDATED BY PHMSA ON 12/17/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060018 | 2006-01-26 11:30 | SUPPLEMENTAL FINAL | 32099 |  | ENERGY TRANSFER COMPANY | 800 E. SONTERRA BLVD. #400 | SAN ANTONIO | BEXAR | TX | 78258 | 430 | 2006-01-05 | 2006 | BARDWELL | ELLIS | TX | 75101 | MP 0 (HOWARD STATION) | 0+00 | N 32 17.848 | W 96 45.159 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462642 | 212245.7491 | 184304.5366 | 462642 | 184304.5366 | 0 | 0 | 0 | 0 | NO | NO | NO | YES | 14 | PRECAUTIONARY | 6 | 0 | 784344 | 2006-01-05 | 680 | 780 | YES | NO | NO | NO | NO | NO | DANNY A. NICHOLS | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | CONTROL VALVE | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1973 | 6 |  | ANSI 600 |  | FLANGED | SAFETY RELIEF | MERCER 9500 SERIES | 2005 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | FLOW CONTROL VALVE FAILED CAUSING PRESSURE TO INCREASE ON PIPELINE. THE 6" RELIEF VALVE OPENED, PREVENTING OVERPRESSURING THE PIPELINE. FINAL UPDATE: INITIAL GAS LOSS REPORTED AT 53921 MCF, WITH FINAL AMOUNT REPORTED TO ENVIROMENTAL AGENCIES 41023 MCF. ALL GAS WAS CLEAN AND DRY (PIPELINE QUALITY). ONLY OTHER CIRCUMSTANCE THAT MADE THIS REPORTABLE WAS THE PRECAUTIONARY EVACUATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060019 | 2006-01-30 | SUPPLEMENTAL FINAL | 31348 |  | ATMOS ENERGY CORPORATION., MID TEX DIVISION | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1130 | 2005-12-07 | 2005 | DALLAS | DALLAS | TX | 75150 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 27335.6401 | 23737.0242 | 60000 | 23737.0242 | 0 | 0 | 0 | 0 | YES | NO | NO | NO | 0 |  | 1 | 0 |  | 2005-12-07 | 430 | 588 | YES | NO | NO | NO | NO | NO | MIKE ARCHER - COMPLIANCE MONITORING | 2142062879 | MICHAEL.ARCHER@ATMOSENERGY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | OTHER | ELECTRONIC FLOW CONTROL BOARD | OTHER | ELECTRONIC COMPONENT | NO | NO | NO | REGULATOR/METERING |  |  | 20 | 0.28 | API 5LX46 | 46000 |  | 8 |  |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | AN ELECTRONIC FLOW CONTROL BOARD DID NOT FUNCTION PROPERLY CAUSING A RELIEF VALVE TO OPERATE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060020 | 2006-01-30 15:12 | SUPPLEMENTAL FINAL | 18646 |  | STINGRAY PIPELINE COMPANY, L.L.C. | 1100 LOUISIANA SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 1830 | 2006-01-15 | 2006 | [6 empty] | 28O16'57 | 92O32'16 | OFFSHORE |  | VM | 320 |  | YES | NO | INTERSTATE | OTHER | THIRD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2653941 | 1535603.8839 | 3316467.8348 | 153941 | 61326.0894 | 2500000 | 3255141.7454 | 0 | 0 | NO | NO | NO | NO | 0 |  | 8 |  | 785285 | 2006-01-15 | 1050 | 1200 | NO | YES | NO | NO | NO | NO | GREGG JOHNSON | 7133536369 | GREGG.JOHNSON@ENBRIDGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 20 | 0.44 | API 5L X-52 | 52000 |  |  |  |  | UNDER WATER |  | 0 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DURING HURRICANE RITA, AN ANCHOR APPARENTLY SNAGGED THIS PIPELINE AND DISPLACED IT APPROXIMATELY 2000' TO THE NORTH. |  | REPAIRS WERE MADE USING 460 FEET OF 20", X-52, 0.438 WT PIPE AND TIED IN UTILIZING QUALITY END CONECTORS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060021 | 2006-02-06 | ORIGINAL | 31978 |  | ATMOS PIPLINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 715 | 2005-12-18 | 2005 | KOSSE | LIMESTONE | TX | 76653 |  |  | 31.17.08.1 | 96.30.91.8 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | 28246.8281 | 24528.2584 | 62000 | 24528.2584 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 |  | 2005-12-18 | 332 | 500 | NO | NO | YES | NO | NO | NO | ELLEN WEAVER DIRECTOR, REGULATORY AND COMPLIANCE | 2142062875 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | OTHER | N/A RELIEF VALVE OPERATING PROPERLY | STEEL |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | A RELIEF VALVE OPERATED PROPERLY.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060022 | 2006-02-06 | ORIGINAL | 31978 |  | ATMOS PIPLINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 900 | 2005-12-26 | 2005 | WAZAHACHIE | ELLIS | TX | 75165 |  |  | 32.367048 | -96.859222 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57000 | 25968.8581 | 22550.173 | 57000 | 22550.173 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 43 |  | 2005-12-26 | 280 | 325 | NO | NO | YES | NO | NO | NO | ELLEN WEAVER DIRECTOR, REGULATORY AND COMPLIANCE | 2142062875 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6 | 0.13 | GRADE A | 30000 |  |  |  |  | UNDER GROUND |  | 18 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DIGGING A FIRE PIT | NO |  |  |  |  | NO | [40 empty] | AN EXCAVATOR STRUCK A TRANSMISSION FACILITY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060023 | 2006-02-14 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HOUSTON | TX | 77056-3050 | 1530 | 2004-07-15 | 2004 | [6 empty] | 28 10.17 | 96 40.85 | OFFSHORE |  | MATAJORDA | 628 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122400 | 76279.3095 | 169490.2814 | 0 | 0 | 122400 | 169490.2814 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7138401980 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 |  |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1977 | NO | [57 empty] | SEVEN SMALL LEAKS WERE DISCOVERED WITHIN 400 YARDS OF THE ORIGINAL REPORTED LEAK. ALL LEAKS WERE REPAIRED USING SLEEVE CLAMPS. SIX WERE IN THE 6 O'CLOCK POSITION ONE IN THE 11 O'CLOCK POSITION. (RRC NO 04-CA-422). REPORT FINALIZED ON 07/12/07 WITH SOME SUPPLEMENTAL DATA ADDED. NO CHANGE IN COST
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060024 | 2006-02-16 17:12 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 925 | 2006-01-20 | 2006 | HUGO | LINCOLN | CO |  | LN 2A, MP 147-028+21 |  | 39.09481 | -103.56990 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575000 | 273333.853 | 296841.2442 | 500000 | 199186.9919 | 75000 | 97654.2524 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 785778 | 2006-01-20 | 853 | 920 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 20 | 0.31 | 5L | 41000 |  |  | YOUNGSTOWN STEEL | 1947 | UNDER GROUND |  | 40 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | SUB-CRITICAL CRACKS | STRESS CORROSION CRACKING |  | YES | 1947 | NO | [57 empty] | THE 20-INCH CIG LINE 2A PIPELINE, NEAR HUGO, CO (APPROX. 5 MILES WEST) RUPTURED. THERE WERE NO INJURIES AND NO FIRE OCCURRED DURING THE INCIDENT. THE PIPE RUPTURE INITIATED DUE TO A CONFLUENCE OF THREE FACTORS: (I)THE HARD SPOT FROM THE ORIGINAL MANUFACTURING PROCESS; (II)THE DISBONDED COAL TAR COATING; AND (III) THE PRESENCE OF SUB-CRITICAL CRACKING THAT HAS BEEN IDENTIFIED AS HIGH PH SCC.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060025 | 2006-02-17 15:01 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1605 | 2006-01-27 | 2006 | HOUMA | TERREBONNE | LA | 70363 | 112.34 |  | 29.28'43.281 | 90.59'14.543 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 124233.9692 | 167369.6995 | 175000 | 69715.4472 | 75000 | 97654.2524 | 0 | 0 | NO | NO | NO | NO | 0 |  | 19 | 25 | 786528 | 2006-01-27 | 728 | 1169 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152183 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 30 | 0.41 | API-5LX | 60000 | SEAMLESS | ANSI 600 | US STEEL | 1964 | UNDER WATER |  | 84 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1965 | NO | [57 empty] | A LAND OWNER REPORTED BUBBLES AND A SMALL SHEEN WERE REPORTED IN WILLOW CANAL (ONE QUARTER MILE SOUTH OF BAYOU PENCHANT). THE LEAK SOURCE WAS SELA LATERAL LINE B. NOTIFICATIONS WERE MADE TO THE NRC, LOUISIANA STATE POLICE, AND THE TERREBONNE PARISH SHERIFF'S DEPARTMENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060026 | 2006-02-21 | ORIGINAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1740 | 2005-12-19 | 2005 | BYRON | OLMSTED | MN | 55920 | 0+00 | 0.00 | 44.0424 | -92.6784 | ONSHORE |  |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 35 | 782946 | 2005-12-19 | 5 | 150 | NO | YES | NO | NO | NO | NO | JOHN A. GORMLEY | 4023987494 | JOHN.GORMELY@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1961 | [8 empty] | INSIDE/UNDER BUILDING |  |  | NATURAL FORCES | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [14 empty] | FROZEN COMPONENTS | [50 empty] | ON DED.19, A SERVICE TO THREE AQUILA COMMUNITIES WAS INTERRUPTED WHEN A BRANCHLINE REGULATOR, OWNED BY NORTHERN NATURAL GAS, FAILED TO OPERATE CORRECTLY AND PRESSURES DROPPED TO CRITICAL LEVELS AT THE DELIVERY POINTS TO THE COMMUNITIES. AQUILA EXPERIENCED LOSS OF SERVICE TO A PORTION OF THEIR CUSTOMERS IN THE COMMUNITIES OF PINE ISLAND, WANAMINGO AND ZUMBROTA,MN. APPROX 250 HOMES AND BUSINESSES LOST NATURAL GAS SERVICE IN THE THREE COMMUNITIES. THE ZUMBROTA AREA HAD EXPERIENCED SEVERE WINTER WEATHER TEMPERATURES PRIOR TO THE INCIDENT. THE EVENING OF THE INCIDENT TEMPERATURES WERE IN THE SINGLE DIGITS WITH WIND CHILL BELOW ZERO. THE LACK OF PILOT GAS HEAT ALLOWED THE TEMPERATURES IN THE PILOT GAS LINE TO DROP TO AMBIENT TEMPERATURES, WHICH WERE AS LOW AS 8 DEGREES FAHRENHEIT. THE LOW GAS TEMPERATURES, COUPLED WITH THE TEMPERATURE DROP THROUGH THE PILOT REGULATOR, DROPPED THE TEMPERATURE OF THE GAS TO A POINT THAT MATCHED OR EXCEEDED THE DEW POINT OF THE GAS STREAM. WATER DROPPED OUT IN THE ORIFICE OF THE PILOT GAS REGULATOR AND FROZE, THUS IMPEDING FULL OPERATION OF THE REGULATOR. NORTHERN IS FILING THIS INCIDENT REPORT BECAUSE IT CONSIDERS THIS AS A SIGNIFICANT EVENT UNDER 191.3. THIS REPORT IS BEING SUBMITTED LATE AS THERE WAS AN OVERSIGHT IN FOLLOW-UP DUE TO THE FACT THAT THE INCIDENT DID NOT MEET THE $50,000 DOLLAR REQUIREMENT, THERE WERE NO INJURIES AND NO RELEASE OF PRODUCT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060027 | 2006-02-21 12:02 | SUPPLEMENTAL FINAL | 26330 |  | ENOGEX INC | 515 CENTRAL PARK DRIVE, SUITE 600 | OKLAHOMA CITY | OKLAHOMA | OK | 73124-0300 | 200 | 2006-01-24 | 2006 | HARRAH | OKLAHOMA | OK | 73045 | HSL POWER PLANT | N/A | 35.5082817 | -97.1757126 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | PSV GAS RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63113 | 28954.2799 | 25142.5772 | 63113 | 25142.5772 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 786138 | 2006-01-24 | 160 | 275 | YES | NO | NO | NO | NO | NO | MIKE REED | 4055584685 | REEDMD@OGE.COM | TRANSMISSION | OTHER | VALVE POSITION | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1965 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | BLOCK VALVE CLOSED BY CUSTOMER. |  | A MANUAL BLOCK VALVE SEPARATING THE PRIMARY CONTROL VALVE OUTLET HEADER FROM THE SECONDARY CONTROL VALVE OUTLET HEADER WAS CLOSED FOLLOWING A SHUTDOWN OF THE CUSTOMER'S POWER GENERATION UNITS 6 & 7 IN OCTOBER 2005. UPON RESTART OF POWER GENERATION UNIT 6 BY POWER PLANT PERSONNEL, THE PRIMARY PRESSURE CONTROLLERS SENSED DECREASING DOWNSTREAM PRESSURE RESULTING IN THE PRIMARY PRESSURE CONTROL VALVES TO FULLY OPEN, WHICH INCREASED THE OPERATING PRESSURE WITHIN THE PRIMARY CONTROL VALVE OUTLET HEADER TO 160 PSIG, AND THEREBY ACTIVATED THE PSV. AN INVESTIGATION TO DETERMINE CAUSAL FACTORS FOR THE INCIDENT IS UNDERWAY AT THIS TIME. THE INCIDENT WAS REPORTED TO THE OKLAHOMA CORPORATION COMMISSION AFTER HOURS VOICE MAIL BY ERIC SPERLING AT 2:30 AM ON 1/24/06. A FOLLOW-UP PHONE CALL WAS MADE BY TED LILLY TO KELLY PHELPS AT THE OKLAHOMA CORPOERATION COMMISSION AND TO THE NRC AT 12:15 PM ON 1/24/06.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060028 | 2006-02-22 10:50 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1935 | 2006-01-26 | 2006 | TALLAPOOSA | HARALSON | GA |  | ROME-CALHOUN MP 12 |  | 33.77879 | -85.35941 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59990 | 33119.3719 | 63660.4947 | 15990 | 6370 | 44000 | 57290.4947 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 786431 | 2006-01-26 | 750 | 1011 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 14 | 0.28 | API | 35000 | FLASH WELD |  | A.O. SMITH | 1957 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1960 | NO | [57 empty] | TWO SMALL LEAKS WERE DISCOVERED ON THE 14-INCH SNG ROME- CALHOUN LOOP LINE, AFTER A LANDOWNER NOTICED BUBBLES IN A CREEK CROSSING ALONG THE PIPELINE RIGHTS-OF-WAY. THE PIPELINE WAS EXCAVATED AND THE LEAKS WERE REPAIRED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060029 | 2006-02-23 10:17 | SUPPLEMENTAL FINAL | 3 |  | ACADIAN GAS PIPELINE SYSTEM | 338 WAVERLY ROAD | THIBODAUX | LAFOURCHE | LA | 70301 | 545 | 2006-01-30 | 2006 | LABADIEVILLE | LAFOURCHE | LA | 70301 |  |  | N29 48.819 | W90 52.228 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | VEHICLE ACCIDENT (SEE PART G NARRATIVE) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9681 | 5268.2932 | 9730.5962 | 3181 | 1267.2276 | 6500 | 8463.3685 | 0 | 0 | NO | YES | NO | YES | 3 | PRECAUTIONARY | 0 | 40 | 786709 | 2006-01-30 | 390 | 550 | NO | YES | NO | NO | NO | NO | JOEL E. KOHLER | 2256752507 | JKOHLER@EPROD.COM | TRANSMISSION | OTHER | 1 | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1984 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A CONTRACT UNITED STATES POSTAL SERVICE 18-WHEEL TRUCK LOST CONTROL WHILE DRIVING IN HEAVY FOG. THE VEHICLE RAN OFF HWY 308 JUST NORTH OF THIBODAUX, LA AND STRUCK THE ACADIAN TO ATMOS - ST. PETER PROTECTIVE BARRIER AND METER STATION. A 1" RISER TO THE STATION WAS SEVERED AND IGNITED RELEASING APPROXIMATELY 253 MCF OF GAS. THE TAP VALVE FOR THE 4" LATERAL SUPPLYING THE IMPACTED STATION WAS CLOSED AND THE REMAINING GAS IN THE LATERAL WAS ALLOWED TO BURN OFF. LOCAL FIRE AND SHERIFF DEPARTMENTS RESPONDED AND BLOCKED THE HIGHWAY.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060030 | 2006-02-24 11:41 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 1615 | 2006-01-30 | 2006 | TALLAPOOSA | HARALSON | GA |  | CHATTANOOGA/12 |  | 33.77879 | -85.35941 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58325 | 30701.6182 | 51249.3267 | 27325 | 10885.5691 | 31000 | 40363.7576 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 786773 | 2006-01-30 | 1200 | 1337 | YES | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 14 | 0.25 | API | 52000 | ERW |  | US STEEL | 1965 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1965 | NO | [57 empty] | SNG OPERATIONS WAS PERFORMING A LEAK SURVEY IN THE RIGHT-OF-WAY, AS FOLLOW-UP TO THE REPAIR ON THE ROME-CALHOUN LOOP LINE. A GAS LEAK WAS DETECTED ON THE CHATTANOOGA BRANCH LINE IN THE VICINITY OF THE REPAIRS ON THE ROME-CALHOUN LOOP LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060031 | 2006-02-24 15:50 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1315 | 2006-02-08 | 2006 | [6 empty] | 28 13 41.42 | 92 20 28.42 | OFFSHORE |  | VERMILLION | 116 | LA | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451000 | 264155.2669 | 586323.8882 | 1000 | 398.374 | 450000 | 585925.5142 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 787575 | 2006-02-08 | 700 | 1250 | NO | YES | NO | NO | NO | NO | MARK A NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | [5 empty] | BALL | GROVE MODEL B-5 | 1971 | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | MATERIAL DEFECT |  | NO | YES | 1 | 1 | 1972 | WATER |  | 8 | 1440 | [12 empty] | ON 2/8/06, A TENNESSEE GAS PIPELINE DIVE CREW REPORTED A LEAK ON A 12¿ SUBSEA VALVE INTERCONNECTING TWO PIPELINES THAT TIE INTO THE COLUMBIA GULF OPERATED LINE 100 OFFSHORE LOUISIANA. THE LEAK WAS CAUSED BY THE FAILURE OF A 1/2" BODY RELIEF FITTING ON THE 12¿ VALVE. THERE WAS A 5¿ GAS BUBBLE NOTED ON THE SURFACE OF THE WATER, BUT NO SHEEN WAS EVER REPORTED. COORDINATES OF THE LEAK WERE PROVIDED AS X = 1, 675, 299 Y = -158,020 OR LAT 28 13 41.42 LONG 92 20 28.42. CREWS WERE ABLE TO ISOLATE THE LEAK BY CLOSING THE 12¿ BLOCK VALVE. ONCE THE VALVE BODY WAS RELIEVED OF PRESSURE, THE LEAKING BODY BLEED FITTING WAS REPLACED. REPAIRS WERE COMPLETED ON 2/22/06 BY 3:45 PM. FINAL COSTS ESTIMATED AT $451,000. FINAL - EDITORIAL CHANGES ONLY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060032 | 2006-02-27 12:28 | ORIGINAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA, SUITE 900 | HOUSTON | HARRIS | TX | 77046 | 2100 | 2006-01-31 | 2006 | PENSACOLA | ESCAMBIA | FL | 32563 | MP 0.0 | 0+00 | N30 25.561 | W16.054 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | CONTROL PIPING DAMAGED BY VEHICLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89700 | 51432.4864 | 108760.7465 | 8890 | 3541.5447 | 80810 | 105219.2018 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 15 | 786878 | 2006-01-31 | 96 | 375 | YES | NO | NO | NO | NO | NO | JACK L ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | CONTROL PIPING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2001 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ESCAMBIA COUNTY FLORIDA SHERIFFS DEPUTIES WERE IN PURSUIT OF A STOLEN VEHICLE HEADING SOUTH ON BORDER ST. THE STOLEN VEHICLE WAS UNABLE TO NEGOTIATE THE CURVE AT THE LILLIAN HWY/BORDER ST INTERCHANGE DUE TO ITS HIGH RATE OF SPEED. THE VEHICLE LEFT THE ROADWAY AND VEERED THROUGH A HIGHWAY GUARDRAIL AND FENCED FACILITY ENTERING GULF SOUTH'S PROPERTY AT THE PENSACOLA T.B.#2 METERING STATION. THE STOLEN VEHICLE WAS AIRBORNE AS IT STRUCK THE ABOVE GROUND REGULATION FACILITIES FEEDING GULF SOUTH'S NAVY 8" PIPELINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060033 | 2006-03-03 16:21 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1337 | 2006-02-06 | 2006 | CRYSTAL CITY | JEFFERSON | MO | 63028 | 0 | 000+01 | +38.16013 | -90.37161 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | VALVE FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48000 | 27046.228 | 54817.4184 | 8500 | 3386.1789 | 39500 | 51431.2396 | 0 | 0 | NO | NO | NO | YES | 46 | PRECAUTIONARY | 5 | 30 | 787386 | 2006-02-06 | 170 | 400 | NO | NO | NO | NO | YES | NO | JOHHNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | VALVE | 1966 | [5 empty] | GATE | WKM | 1966 | UNDER GROUND |  | 44 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | VALVE STEM BROKE | [8 empty] | SYSTEM CONTROL NOTICED A REDUCTION IN THE NORMAL INLET PRESSURE TO THE A-194 METER STATION EARLY IN THE MORNING OF FEBRUARY 6, 2006. THE FIELD PERSONNEL VERIFIED THAT THE INLET PRESSURE WAS BEING RESTRICTED BY THE 2" WKM TAP VALVE FOR THE A-194 LINE. HE CALLED IN A CREW TO DIG UP AND DETERMINE WHAT WAS CAUSING THIS PROBLEM. AFTER THEY DUG UP THE VALVE, THEY REMOVED THE VALVE HANDLE EXTENSION. THE STEM IN THE VALVE BROKE AND BLEW OUT OF THE VALVE AFTER THE EXTENSION WAS REMOVED, CAUSING GAS TO START EXCAPING FROM THE VALVE. THEY ATTEMPTED TO REINSTALL THE STEM BUT COULD NOT GET THE GAS TO STOP LEAKING. WHEN THE STEM BROKE APPARENTLY THE GATE ON THE 2" WKM VALVE BECAME ALMOST COMPLETELY CLOSED RESULTING IN THE LOSS OF GAS SERVICE TO THE A-194 CUSTOMER. IN ORDER TO REPLACE THIS FAULTY VALVE WE HAD TO BLOWDOWN OUR A-151 AND A-183 LINES, WHICH RESULTED IN THE LOSS OF SERVICE TO THE CUSTOMERS ON THOSE LINES ALSO. WE INSTALLED A NEW 2" ORBIT VALVE TO REPLACE THE WKM VALVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060034 | 2006-03-03 18:18 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1320 | 2006-02-08 | 2006 | CARTHAGE | PANOLA | TX | 75633 | CARTHAGE JCT COMP STA |  | N32 08' 38.5 | W094 15' 59.2 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100100 | 58645.0987 | 130245.5072 | 100 | 39.8374 | 100000 | 130205.6698 | 0 | 0 | NO | YES | NO | NO | 0 |  |  | 5 | 787567 | 2006-02-08 | 145 | 1000 | YES | NO | NO | NO | NO | NO | JACK L ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | OTHER | COMPRESSOR STATION | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1980 | [8 empty] | INSIDE/UNDER BUILDING |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | FLANGES NOT LEVEL, LEAD TO LEAK. | [6 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | INSTALLED A NEW PULSATION BOTTLE AND ONE OF THE THREE INLET FLANGES WAS SHORTER THAN THE LEFT AND CENTER INLET FLANGES. THE GAP IN THE HEIGHT OF THE INLET FLANGE RELATIVE TO THE REMAINING TWO INLET FLANGES LEAD TO A GASKET FAILURE WHICH LEAD TO LEAK DURING START-UP.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20060035 | 2006-03-07 18:54 | ORIGINAL | 31121 |  | EXPRO ENGINEERING, INC. | 3220 NORTH FREEWAY, SUITE 112 | FORT WORTH | TARRANT | TX | 76111 | 1345 | 2005-11-12 | 2005 | BAY CITY | MATAGORDA | TX | 77414 |  |  |  |  | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | OTHER | RELIEF VALVE LEAK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 45 |  |  |  |  | NO | NO | NO | NO | NO | NO | DENNIS W. BROWNING | 8176248425 | DWBROWNING@EXPROENG.COM | GATHERING | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | PIPELINE | [7 empty] | RELIEF |  |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | RELIEF VALVE MALFUNCTION RELEASING GAS AT A RATE TOO SMALL TO MEASURE. THE RELIEF VALVE WAS LOCATED ON AN ABANDONED SECTION OF THE PIPELINE. THE PIPE WAS CAPPED PRIOR TO THE RELIEF VALVE, THUS ELEMINATING THE POTENTIAL FOR A FUTURE OCCURENCE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060036 | 2006-03-13 09:31 | ORIGINAL | 17620 |  | ROCKY MOUNTAIN NATURAL GAS COMPANY | 500 DALLAS ST. SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1805 | 2006-02-27 | 2006 | GLENWOOD SPRINGS | GARFIELD | CO | 81601 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 25868.4048 | 26428.9827 | 50000 | 19918.6992 | 5000 | 6510.2835 | 0 | 0 | NO | NO | NO | YES | 6 | PRECAUTIONARY | 1 | 15 | 789344 | 2006-02-27 | 690 | 824 | NO | NO | YES | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6 | [7 empty] | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | FAILURE OCCURED IN A WELD THAT WAS MADE IN 1960 VINTAGE CONSTRUCTION. EARTH SUBSIDANCE IS PROBABLE CAUSE OF WELD FAILURE. INVESTIGATION IS ONGOING TO DETERMINE EXACT CAUSE OF SUBSIDANCE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060037 | 2006-03-14 09:03 | SUPPLEMENTAL FINAL | 18646 |  | STINGRAY PIPELINE COMPANY, L.L.C. | 1100 LOUISIANA SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 1700 | 2006-03-01 | 2006 | [8 empty] | OFFSHORE |  | VM | 321 |  | YES | NO | INTERSTATE | OTHER | RISER SEVERED BY ANCHOR DRAG. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 878988.3268 | 1953085.0472 | 0 | 0 | 1500000 | 1953085.0472 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 5 | 789571 | 2006-03-01 | 80 | 1200 | NO | YES | NO | NO | NO | NO | GREGG JOHNSON | 7133536369 | GREGG.JOHNSON@ENBRIDGE.COM | GATHERING | OTHER | PLATFORM RISER | STEEL |  | NO | NO | NO | OTHER | PLATFORM RISER | 1974 | 12 | 0.44 | API 5L X-52 |  | SEAMLESS |  |  |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DURING HURRICANE RITA AN ANCHOR APPARENTLY SNAGGED THE PLATFORM RISER SEVERING 80' OF THE RISER. |  | REPAIRS WERE MADE BY REPLACING 2,937 FEET OF 12" WITH 2,937 FEET OF 6.625", X-42, 0.432" WT PIPE AND REPAIRING A 10"SUBSEA TAP TIE-IN WITH 61 FEET OF 22", X-56, 0.500" WT AND 21 FEET OF 10.75", X-42, 0.365" WT. TIE-INS WERE MADE WITH HYDROTECH END CONNECTORS.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060039 | 2006-03-14 09:23 | ORIGINAL | 31485 |  | ENBRIDGE OFFSHORE (GAS GATHERING) L.L.C. | 1100 LOUISIANA, SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 1715 | 2006-03-06 | 2006 | [8 empty] | OFFSHORE |  | GB | 783 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 87898.8327 | 195308.5047 | 0 | 0 | 150000 | 195308.5047 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 790088 | 2006-03-06 | 1438 | 2160 | NO | YES | NO | NO | NO | NO | JOHN LOCANTRO | 7133535672 | JOHN.LOCANTRO@ENBRIDGE.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2004 | 16 | 0.63 | X-60 |  | SEAMLESS | 4 " BALL | CAMERON | 2004 | UNDER WATER |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | GREASE FITTING | [8 empty] | LEAK IS COMING FROM A GREASE ZERT IN A 4" BY-PASS VALVE LOCATED ON THE PONTOON OF THE MAGNOLIA TLP. THE BY-PASS IS AROUND THE 16" CHECK VALVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060040 | 2006-03-14 17:39 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 745 | 2006-02-16 | 2006 |  | WASHINGTON | MS |  | 5.91/21 |  | 33*22'22 | 91*00'00 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362322 | 183389.5739 | 266282.604 | 227382 | 90583.0732 | 134940 | 175699.5309 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 |  | 788227 | 2005-02-16 | 800 | 858 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 30 | 0.3 | API 5L | 60000 | DSAW |  |  | 1965 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 9 | 9 | 1965 | WATER |  | 24 | 1180 | [12 empty] | A LEAK OCCURRED ON ANR LINE 1-501, IN THE GREENVILLE, MS AREA AT APPROXIMATE MP 5.91, VALVE SECTION 20. THE LEAK WAS APPARENTLY DUE TO A CRACK IN A GIRTH WELD. THE FAILURE WAS ATTRIBUTED TO A PRE-EXISTING UNDERBEAD CRACKING, INTRODUCED DURING ORIGINAL CONSTRUCTION, WITH A MINOR EXTERNAL LONGITUDINAL STRESS COMPONENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060041 | 2006-03-15 | SUPPLEMENTAL FINAL | 31531 |  | ONEOK WESTEX TRANSMISSION, L.P. | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103 | 1130 | 2006-02-13 | 2006 | LUBBOCK | LUBBOCK | TX |  | BLOCK B, SECTION 12 | INE 0256-000 | N 3334.152 | W 10146.307 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 28798.3658 | 32939.2662 | 50000 | 19918.6992 | 10000 | 13020.567 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 787951 | 2006-02-13 | 415 | 575 | NO | YES | NO | NO | NO | NO | STEVE STUDTMANN | 8063546505 | SSTUDTMANN@ONEOK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 20 | 0.25 | X-46 | 1150 | ERW | ANSI 300 | UNITED STATES STEEL CORPORATION | 1967 | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | XCEL ENERGY WAS USING AN AUGER TO DIG A HOLE TO INSTALL A POWER POLE. THE AUGER STRUCK WES TEX'S PIPELINE AND PUNCTURED THE WALL OF THE PIPE AT TOP CENTER, CREATING A 1-INCH DIAMETER HOLE IN THE PIPE. WESTEX DID NOT RECEIVE PRIOR NOTIFICATION FROM DIG-TESS REGARDING THIS EXCAVATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060042 | 2006-03-17 15:13 | SUPPLEMENTAL FINAL | 12876 |  | QUESTAR GAS COMPANY | P.O. BOX 45360 | SALT LAKE CITY | SALT LAKE | UT | 84145-0360 | 1805 | 2006-02-18 | 2006 | SOUTH WEBER | DAVIS | UT | 84405 | NOT APPLICABLE | 160+76 | 41.12877 | -111.93422 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 258607.5643 | 549778.2056 | 40000 | 15934.9593 | 110000 | 143226.2368 | 300000 | 390617.0094 | NO | NO | YES | YES | 210 | THREAT TO THE PUBLIC | 2 | 15 | 78489 | 2006-02-18 | 315 | 499 | NO | NO | YES | NO | NO | NO | JEFFREY D. HANSEN | 8013243645 | JEFF.HANSEN@QUESTAR.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 14 | 0.25 | EQUAL TO API 5L | 42000 | FLASH WELD | NOT APPLICABLE | AO SMITH | 1929 | UNDER PAVEMENT |  | 41 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | SEE NARRATIVE (PART G) |  | THIS PIPE RUPTURED AT OR NEAR THE SITE WHERE A CORROSION PIT HAD BEEN REPAIRED BY FILLING WITH WELD MATERIAL. CONSTRUCTION RECORDS INDICATE THAT THIS REPAIR WAS MADE PRIOR TO INSTALLING THE PIPE IN 1955. A METALLURGICAL INVESTIGATION BY EWI WORKING IN CONJUNCTION WITH AMERICAN METALLURGICAL SERVICES CONCLUDED THAT "THE FEEDER-LINE 18 FAILURE ORIGIN WAS IN A WELD REGION NEAR THE BOTTOM OF THE PIPELINE." THE INVESTIGATION FOUND NO EVIDENCE OF ACTIVE CORROSION, FATIGUE CRACKING, HYDROGEN STRESS CRACKING, OR STRESS CORROSION CRACKING. FURTHER, THE METALLURGICAL INVESTIGATION FOUND THAT "THE ORIENTATION OF THE FRACTURE AND THE DISTINCT DOG-LEG APPEARANCE OF THE REMOVED PIPELINE SECTION WOULD SUGGEST AN EXTERNAL LOAD MAY HAVE CONTRIBUTED TO THE FRACTURE." AN INVESTIGATION OF POTENTIAL EXTERNAL LOADING DID FIND THAT ADDITIONAL THIRD-PARTY FILL HAD BEEN PLACED OVER THE PIPELINE IN THE REGION OF THE FRACTURE, AND THAT OTHER UTILITIES HAD BEEN INSTALLED UNDER THE PIPELINE IN THIS SAME AREA. HOWEVER, IT COULD NOT BE CONCLUDED THAT THESE FACTORS OR OTHER FACTORS INCLUDING NATURALLY OCCURRING OUTSIDE FORCES ALONE PROVIDED SUFFICIENT EXTERNAL LOADING TO HAVE CAUSED THIS FAILURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060043 | 2006-03-17 16:01 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 830 | 2006-02-13 | 2006 | CAMDEN | OUACHITA | AR | 71701 |  | 398835 | +33.54140 | -92.81675 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64207 | 37089.5737 | 79799.3612 | 4207 | 1675.9593 | 60000 | 78123.4019 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 787939 | 2006-02-13 | 275 | 300 | NO | NO | NO | NO | YES | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.25 | UNKNOWN | 24000 | ERW |  | UNKNOWN | 1930 | UNDER GROUND |  | 30 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | DEFECTIVE BOLTED CLAMP | [6 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | A CALL WAS RECEIVED AT OUR EL DORADO FIELD OFFICE ABOUT GAS ODOR AND A POSSIBLE GAS LEAK NEAR APPLE ST.CAMDEN AR. AT APPROXIMATELY 0830, FEB 13, 2006. FIELD PERSONNEL WERE DISPATCHED TO THE AREA, AND AT FIRST SUSPECTED A MINOR LEAK ON LINE K-NORTH. UPON EXCAVATION IT WAS DETERMINED THAT THE LEAK INVOLVED A DEFECTIVE BOLTED CLAMP COUPLING THAT HAD ALLOWED THE PIPE TO PULL OUT ABOUT 2.75 INCHES. IT WAS DETERMINED THE REPAIR WOULD PROBABLY EXCEED $50,000 AND A CALL WAS PLACE TO THE SYSTEM CONTROL, WHO IN TURNED INITIATED OUR INCIDENT REPORTING PROCEDURE AND MADE TELEPHONIC NOTIFICATIONS TO THE APPROPRIATE AGENCIES. ABOUT A 500 FOOT SECTION OF THE PIPELINE WAS ISOLATED AND BLOWN DOWN. THE LEAKING COUPLING WAS REPAIRED BY INSTALLING A 220 WELDOVER SLEEVE. NO CUSTOMERS WERE LOST DURING THE REPAIR. THE PIPELINE WAS RETURNED TO NORMAL OPERATION AT 1900 HOURS ON FEB 14, 2006.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060044 | 2006-03-20 11:10 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1259 | 2006-03-02 | 2006 | ANNANDALE | WRIGHT | MN | 55308 | 16.59 | 875+95 | 45.2608 | -94.1434 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113000 | 61637.0802 | 114599.8292 | 36000 | 14341.4634 | 77000 | 100258.3658 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 789669 | 2006-03-02 | 800 | 950 | NO | YES | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | OTHER | FARM TAP (RURAL SALES FACILITY) | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1966 | 2.38 | 0.22 | API 5L | 35000 | SEAMLESS |  | US STEEL | 1966 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | AT 12:59 PM ON 3/2/06 CENTERPOINT ENERGY REPORTED THAT A VEHICLE HAD STRUCK NORTHERN'S RODNEY CARLSON FARM TAP 1-1/2 MILES WEST OF THE TOWN OF ANNANDALE, MN. THE FARM TAP IS ON THE 3" WATKINS (MNB63401) BRANCH LINE AT MP 16.59. THIS IS SECTION 25-T121N-R28W IN WRIGHT COUNTY, MN. THE VEHICLE LEFT COUNTY ROAD 38, HIT A POWER POLE THEN HIT THE FARM TAP. THE WRIGHT COUNTY SHERIFF, CITY OF ANNANDALE POLICE AND THE ANNANDALE FIRE DEPARTMENT RESPONDED TO THE ACCIDENT. WIND WAS FROM THE NW AT 5 TO 10 MPH. THE TEMPERATURE WAS 30°F. THE COUNTY ROAD IS BLACK TOP AND BUSY. THE AREA IS NOT DENSELY POPLULATED. THE DRIVER REFUSED MEDICAL TREATMENT BUT WAS TAKEN INTO CUSTODY FOR REASONS UNKNOWN. THE WRIGHT COUNTY SHERIFF ACCIDENT NUMBER IS 06007832. THE DRIVER, SHANNON LINDQUIST, LIVES IN SOUTH HAVEN, MN. MNOPS INVESTIGATED THE INCIDENT.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060045 | 2006-03-20 11:33 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1245 | 2006-03-02 | 2006 | CORPUS CHRISTI |  | TX |  |  |  | 27.70605 | -96.597283 | OFFSHORE |  | MUSTANG ISLAND | 757 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500000 | 1452258.2103 | 3164773.474 | 100000 | 39837.3984 | 2400000 | 3124936.0756 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 |  |  |  | 1250 | NO | YES | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.38 | API 5LX | 60000 | DSA |  | STELCO | 1986 | UNDER WATER |  | 18 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1986 | NO | [57 empty] | ON FEBRUARY 28, NORTHERN RECEIVED NOTIFICATION OF POSSIBLE LEAKS IN THE MUSTANG ISLAND AREA. THE LEAK WAS DUE TO INTERNAL CORROSION. EXAMINATION OF THE SURROUNDING PIPE SHOWED NO OTHER MEASURABLE CORROSION. THE LEAK AREA WAS SLEEVED AND RETURNED TO SERVICE. BAD WEATHER AND SEAS PREVENTED TIMELY MITIGATION.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060046 | 2006-03-20 13:20 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1245 | 2006-03-02 | 2006 | CORPUS CHRISTI |  | TX |  |  |  | 27.63265 | -96.649717 | OFFSHORE |  | MUSTANG ISLAND | 782 | TX | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500000 | 1452258.2103 | 3164773.474 | 100000 | 39837.3984 | 2400000 | 3124936.0756 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 |  |  |  | 1250 | NO | YES | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.38 | API 5LX | 60000 | DSAW |  | STELCO | 1986 | UNDER WATER |  | 18 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1986 | NO | [57 empty] | THIS LEAK WAS FOUND TO BE AN INTERNAL CORROSION PIT. THE SURROUNDING PIPE WAS EXAMINED FOR OTHER DETRIMENTAL CORROSION AND NONE WAS FOUND. THE LEAK WAS REPAIRED WITH A SLEEVE AND RETURNED TO SERVICE. BAD WEATHER AND ROUGH SEAS PREVENTED TIMELY MITIGATION OF THIS LEAK. SUPPLEMENTAL INFORMATION - DURING THE REPAIR AND PRESSURING UP PROCESS OF THE TWO LEAKS REPORTED ON TWO SEPARATE 7100 FORMS DATED 3/2/2006 A THIRD LEAK, WITHIN THE SAME PIPE SEGMENT AND WITH NEARLY IDENTICAL LONGITUTDE/LATITUDE WAS FOUND. IT WAS REPAIRED BY CLEANING, INSPECTING AND INSTALLATION OF A LEAK REPAIR CLAMP. A SEPARATE 7100 FORM WAS NOT FILLED OUT AS IT WAS DEEMED TO BE COVERED BY THE TWO MARCH 2, 2006 7100 FORMS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060048 | 2006-03-27 | SUPPLEMENTAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1520 | 2006-02-19 | 2006 | STURGEON | BOONE | MO | 65243 | 3.3 | 172+36 | N 39-14.374 | W 92-20.586 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 32064.1816 | 70438.3309 | 1300 | 517.8862 | 53700 | 69920.4447 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 788557 | 2006-02-19 | 400 | 450 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPLE ENGINEER | 7139897473 | MARVIN.HOVIS@PANHANDLEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 1 | 0.14 |  | 24000 | SMLS |  |  |  | UNDER GROUND |  | 24 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A VEHICLE TRAVELING ON STATE ROUTE F, STRUCK AN ABOVEGROUND MARKER POST. THE MARKER POST WAS PUSHEDINTO THE STEM OF A VALVE ON A BELOW GROUND 1" TAP ON THE LATERAL. THE EXTERNAL LOAD CAUSED BY THE VEHICLE STRIKING THE MARKER POST WAS TRANSFERRED TO THE 1" PIPE THROUGH THE VALVE. THIS LOAD EXCEEDED THE STRESS LEVEL OF THE 1" PIPE, RESULTING IN SMALL CIRCUMFERENTIAL SEPARATION IN THE 1" LINE, BELOW THE VALVE. SINCE THIS LATERAL IS THE SOLE SOURCE OF SUPPLY FOR 2 SMALL TOWNS AND IT WAS DETERMINED THAT THERE WAS NO THREAT TO THE PUBLIC IN ALLOWING CONTINUED LEAKAGE, THE LINE WAS LEFT INSERVICE UNTIL THE FOLLWING DAY, THE LINE WAS STOPPLED AND THE LEAK REPAIRED ON FEB. 20, 2006.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060049 | 2006-03-30 11:31 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFT ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 200 | 2006-02-04 | 2006 | NORTHRIDGE | LOS ANGELES | CA |  | WELL SITE FF-32 |  | 34.296772 | -118.550951 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 32229.572 | 71613.1184 | 0 | 0 | 55000 | 71613.1184 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 10 | 789509 | 2006-03-01 | 710 | 710 | YES | NO | NO | NO | NO | NO | W. JEFFREY KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | OTHER | NO FAILURE |  |  | NO | NO | NO | OTHER | RELIEF VALVE @ WELLHEAD | [9 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | EXCESSIVE PRESSURE TRIGGERED RELIEF VALVE |  | ON FEBRUARY 04, 2006, A RELIEF VALVE TRIGGERED ON AN UNDERGROUND STORAGE FACILITY WELLHEAD, SPRAYING PETROLEUM MIST ON NEARBY BRUSH AND HILLSIDE. NO INJURIES RESULTED FROM THIS INCIDENT. OVERPRESSURE WAS QUICKLY ALLEVIATED, AND RELIEF VALVE RESET. AN INVESTIGATION OF THIS INCIDENT DETERMINED THAT WHILE 400 BARRELS WERE BEING INJECTED INTO THE WELL, EXCESSIVE BACKPRESSURE DURING FLOWBACK OCCURRED, TRIPPING A RELIEF VALVE, AS DESIGNED, WHEN PRESSURE EXCEEDED MAOP. THIS INCIDENT DID NOT INITIALLY MEET CPUC/DOT REPORTING CRITERIA. CLEANUP WAS COMPLETED TO INITIAL DEPARTMENT OF FISH AND GAME PARAMETERS AT A TOTAL COST THAT DID NOT EXCEED $50,000. IT WAS NOT UNTIL MARCH 1 THAT A SUBSEQUENT SITE VISIT BY THE DEPARTMENT OF FISH AND GAME EXPANDED THE MITIGATION SCOPE TO AND TOTAL ESTIMATE COST THAT WOULD EXCEED $50,000. AS A RESULT, THIS INCIDENT WAS REPORTED ON MARCH 1, 2006.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060050 | 2006-03-31 15:30 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 39 | 2006-03-26 | 2006 | MARBLE HILL | BOLLINGER | MO | 63764 | MP 885 |  | 37.35839 | -89.872056 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147524 | 67679.4193 | 58769.7236 | 147524 | 58769.7236 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 34 | 791968 | 2006-03-26 | 835 | 858 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | COMPRESSOR | [7 empty] | PILOT OPERATED RELIEF VALVE |  |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | A RELIEF VALVE ON THE DISCHARGE SIDE OF A COMPRESSOR UNIT FAILED TO RESET ITSELF AND CONTINUED TO BLOW UNTIL PERSONNEL ARRIVED TO CLOSE THE VALVE MANUALLY.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060051 | 2006-04-05 12:12 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE CORPORATION | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 610 | 2006-03-11 | 2006 |  |  |  |  | MP 9.031 |  | 28'55.043 | 91'46.215 | OFFSHORE |  | EUGENE ISLAND | 135 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 104 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1800000 | 1016618.9889 | 2072597.2424 | 300000 | 119512.1951 | 1500000 | 1953085.0472 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 50 | 790564 | 2006-03-11 | 1050 | 1440 | NO | YES | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 20 | 0.5 | API-5LX | 52000 | SEAMLESS | ANSI 600 | US STEEL | 1966 | UNDER WATER |  | 26 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | PERSONNEL AT EOG'S EI 135 PLATFORM CALLED TRANSCO GAS CONTROL AND THE DISTRICT OFFICE TO REPORT A DROP IN PIPELINE PRESSURE. SHORTLY AFTER, BUBBLES WERE DISCOVERED ABOUT 3400 FEET FROM THE EI 135 PLATFORM. THE PIPELINE WAS ISOLATED AND BLOWN DOWN. DIVERS LATER DISCOVERED THE 20" PIPELINE WAS SEPARATED BY AN 8 FOOT GAP BETWEEN THE TWO ENDS. LATER IT WAS DISCOVERED THAT THE PIPELINE WAS WEAKENED BY CONTACT DURING AN ANCHOR DRAG FROM HURRICANE RITA. THE PIPELINE IS SCHEDULED TO BE ABANDONED IN 2007.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20060052 | 2006-04-05 | SUPPLEMENTAL FINAL | 13840 |  | NW NATURAL | 220 N.W. SECOND AVENUE | PORTLAND | MULTNOMAH | OR | 97209 | 1430 | 2006-03-01 | 2006 | PORTLAND | MULTNOMAH | OR | 97232 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | NO | NO | NO | 0 |  |  |  | 789579 | 2006-03-01 | 360 | 400 | NO | YES | NO | NO | NO | NO | DAKOTA DUNCAN, PIPELINE SAFETY COMPLIANCE SPECIALIST | 5032264211 | DAKOTA.DUNCAN@NWNATURAL.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | OTHER | RISER VALVE | [9 empty] | OPEN DITCH |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 7 |  |  | EMPLOYEE WAS OPENING A BALL VALVE ON TEST RISER AT THE COMPANY'S GATE STATION. AS EMPLOYEE OPENED VALVE, EMPLOYEE'S HAND SLIPPED OFF AND APPROX 360 PSIG GAS IMPINGED EMPLOYEE'S WRIST. THE GAS IMPINGEMENT FORCED METAL SHAVINGS,DIRT AND OIL UNDER SKIN OF THE EMPLOYEE'S HAND AND CREATED AN AIR POCKET IN ARM AND WRIST. EMPLOYEE FAILED TO INSTALL A 3/4 INCH PURGE STACK TO DEFLECT FLOW OF GAS PRIOR TO TAPPING. EMPLOYEE WAS TREATED AT A LOCAL HOSPITAL AND KEPT OVERNIGHT FOR OBSERVATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060053 | 2006-04-07 15:43 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1745 | 2006-03-13 | 2006 | PRINCETON | BOSSIER | LA | 71067 |  | 1290+69 | 32.5924000 | -93.515000 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | REGULATOR FAILURE CAUSING RV RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24000 | 11124.954 | 10374.2901 | 23100 | 9202.439 | 900 | 1171.851 | 0 | 0 | NO | NO | NO | YES | 9 | PRECAUTIONARY | 2 |  | 790783 | 2006-03-13 | 900 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1990 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | AT APPROXIMATELY 1650 HRS, ON MARCH 13, 2006 A REGULATOR FAILURE CAUSED THE RELIEF VALVE TO RELEASE NATURAL GAS AT AN M&R STATION ON THE CENTERPOINT ENERGY GAS TRANSMISSION'S (CEGT) LINE F-WEST SYSTEM. THE M&R STATION IS LOCATED AT LODGEHILL ROAD AND LA HIGHWAY 157 DELIVERING NATURAL GAS TO THE CALUMET REFINERY IN PRINCETON LA. CEGT SYSTEM CONTROL WAS NOTIFIED AT 1745 HRS. AND DISPATCHED A FIELD TECHNICIAN TO THE LOCATION. DURING THE TRAVEL TIME, THE EMERGENCY RESPONDERS AT THE RELEASE LOCATION BLOCKED LA HIGHWAY 157 AND ORDERED A PRECAUTIONARY EVACUATED OF 9 PERSONS FROM FOUR HOUSES DIRECTLY ACROSS THE STREET FROM THE M&R STATION. CEGT FIELD TECHNICIAN SECURED THE SITE AT 1835 HRS. UPON INVESTIGATION OF THE M&R STATION IT WAS DETERMINED THAT THE PRIMARY REGULATOR HAD FAILED OPEN DUE TO A BROKEN LINKAGE WHICH IN TURN CAUSED THE RELIEF VALVE TO RELEASE AS DESIGNED. THE REGULATOR WAS REPAIRED ON MARCH 14 AND RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060054 | 2006-04-10 16:05 | ORIGINAL | 31130 |  | DUKE ENERGY FIELD SERVICES (EASTRANS LIMITED PARTNERSHIP) | 370 17TH STREET, SUITE 2500 | DENVER | DENVER | CO | 80202 | 1120 | 2006-04-01 | 2006 | HENDERSON | RUSK | TX | 75652 |  |  | 32.30611 | -94.759722 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172032 | 94189.7282 | 176974.9989 | 52032 | 20728.1951 | 120000 | 156246.8038 | 0 | 0 | NO | NO | NO | NO | 0 |  | 10 |  | 793094 | 2006-04-05 | 910 | 1264 | YES | NO | NO | NO | NO | NO | CINDY LOPEZ | 3615848518 | CALOPEZ@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.24 | X-60 |  | ERW | NA |  |  | UNDER GROUND |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1989 | NO | [57 empty] | LANDOWNER HEARD GAS BLOWING AND NOTIFIED OPERATOR. DEFS SENT FIELD OPERATOR OUT TO INVESTIGATE AND DETERMINED THAT THE LEAK WAS ON OUR PIPELINE ETL-1. PIPELINE WAS ISOLATED AND BLOWN DOWN. LEAK WAS REPAIRED APRIL 7, 2006.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060055 | 2006-04-17 17:17 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORPORATION | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1130 | 2006-03-29 | 2006 | DEMING | WHATCOM | WA | 98244 | MP: 1468.8 | 21353+85.8 | N. 48.81867 | W. 122.19694 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 33251.1829 | 64568.1612 | 15000 | 5975.6098 | 45000 | 58592.5514 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 792361 | 2006-03-29 | 683 | 809 | NO | NO | YES | NO | NO | NO | MARYBETH KELLER | 8015846726 | MARYBETH.KELLER@WILLIAMS.COM | TRANSMISSION | OTHER | GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.28 | API X52 | 1124 | DSAW |  | KAISER | 1956 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | GIRTH WELD |  |  |  |  | MATERIAL DEFECT |  | NO | YES | 8 | 27 | 1972 | WATER |  | 8 | 1143 | [12 empty] | PINHOLE LEAK DISCOVERED AFTER FLAME I WALK. LEAK DUE TO MANUFACTURING DEFECT ON THE GIRTH WELD. OPERATOR DAMAGE CONSISTED ALMOST ENTIRELY OF CONSTRUCTION CREW COSTS. GAS LOSS AMOUNT DUE TO BLOWING DOWN ON PIPELINE. ORIGINAL WELD AND EIGHT FEET OF PIPE CUT OUT AND REPLACED. PIPE RETURNED TO SERVICE 4/1/06.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060056 | 2006-04-19 14:12 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1520 | 2006-03-26 | 2006 | FORT GAY | WAYNE | WV |  |  | 1879+25 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72600 | 35580.483 | 45073.4724 | 54727 | 21801.813 | 17873 | 23271.6594 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 792009 | 2006-03-26 | 278 | 285 | NO | NO | NO | YES | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1900 | 10 | 0.3 | 24000 |  |  | N/A | UNKNOWN | 1899 | UNDER GROUND |  | 12 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | GROUND MOVEMENT CAUSED A 10 INCH LINE TO PULL APART AT A THREADED JOINT. PIPE INSTALLED IN 1899. INCIDENT DUE TO DAMAGES IN EXCESS OF $50,000.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060057 | 2006-04-20 08:56 | ORIGINAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 2155 | 2006-04-03 | 2006 | RED OAK | LATIMER | OK | 74563 | 100 | 532348.9 | 095.10314 | 34.95997 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61070 | 28017.0151 | 24328.6992 | 61070 | 24328.6992 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 5 | 792894 | 2006-04-03 | 500 | 1050 | NO | NO | NO | NO | NO | NO | BILL STEPHENS | 3039144877 | BILL_STEPHENS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 24 | 0.25 | 5LX70 | 70000 | ERW |  | NAPA | 1990 | UNDER GROUND |  | 60 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | WATER/LIQUID | YES | 1990 | NO | [57 empty] | A LANDOWNER REPORTED A SUSPECTED LEAK ON THE LATIMER LINE ROW. THE PIPELINE WAS EXCATED TO CONFIRM THAT THE LEAK WAS ON THE KINDER MORGAN FACILITY DUE TO ANOTHER PIPELNE WITHIN 70'. THE LEAK WAS FOUND TO BE A LEAKING CORROSION PIT UNDER A SHRINK SLEEVE THAT WAS IMPROPERLY APPLIED DURING CONSTRUCTION IN 1990.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060058 | 2006-04-20 15:43 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1430 | 2006-03-29 | 2006 | GREENVILLE | WASHINGTON | MS |  |  | MP 54-1 + 0.0 | 33*21'21 | 91*03'03 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | GAS LEAKED THROUGH BROKEN SIGHT GLASS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 183507.5494 | 159349.5935 | 400000 | 159349.5935 | 0 | 0 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 |  | 792353 | 2006-03-29 | 715 | 750 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | BROKEN SIGHT GLASS ON SCRUBBER | STEEL |  | NO | NO | NO | COMPRESSOR |  |  | 24 | 0.38 |  | 40000 |  |  |  | 1944 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE SIGHT GLASS ON AN SA-1 SCRUBBER INSIDE THE STATION YARD FAILED, CAUSING A LEAK. |  | GAS BLOWING ACROSS THE ISOLATION VALVE PREVENTED THE FACILITATION OF THE STATION YARD BLOWDOWN. THE VALVE SECTIONS BETWEEN MLV 54-1SH AND 53-1B1 & BETWEEN 54-2SH AND 53-2B1 HAD TO BE SHUT-IN AND BLOW DOWN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060059 | 2006-04-21 04:55 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1430 | 2006-03-22 | 2006 | [6 empty] | 29.08703 | 091.69764 | OFFSHORE |  | EUGENE ISLAND | 95-F |  | YES | NO | INTERSTATE | OTHER | REPLACED BOLTS AND RETORQUED. SEE NARRATIVE. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 146498.0545 | 325514.1745 | 0 | 0 | 250000 | 325514.1745 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 791664 | 2006-03-21 | 870 | 1440 | NO | YES | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 10 | 0.5 |  | 42000 |  | SWIVEL BALL CONNECTOR | BIG INCH |  | UNDER WATER |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | BOLTS | [8 empty] | A 10' SWIVEL BALL CONNECTOR WAS FOUND TO HAVE A MINOR LEAK WHICH WAS DISCOVERED 22 DAYS AFTER THE ASSOCIATED (PREVIOUS HURRICANE RITA STORM DAMAGED) SUB SEA TIE-IN WAS REPAIRED AND PLACED BACK INTO SERVICE. UPDATE: LEAK CAUSED BY MISALIGNMENT AND /OR BOLT TORQUE ISSUE ON SWIVEL BALL CONNECTOR. BOLTS WERE CHANGED AND RE-TORQUED. LINE PLACED BACK IN SERVICE ON OR NEAR APRIL 7, 2006.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060060 | 2006-04-28 | ORIGINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1230 | 2006-01-04 | 2006 | KRUM | DENTON | TX | 76249 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58000 | 33478.6553 | 71904.5576 | 4000 | 1593.4959 | 54000 | 70311.0617 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 |  | 2006-01-04 | 600 | 800 | NO | YES | NO | NO | NO | NO | ELLEN WEAVER | 2142062875 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 3 | 0.16 | GRADE B | 35000 | SEAMLESS |  |  |  | UNDER GROUND |  | 42 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 12 | 12 | 2005 | ONE-CALL SYSTEM | YES | PAINT | YES |  | YES | [36 empty] | AN EXCAVATOR CLEARING RIGHT-OF-WAY FOR A PIPELINE PROJECT STRUCK A TRANSMISSION LINE CAUSING THE TRANSMISSION LINE TO BE TAKEN OUT OF SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060061 | 2006-04-28 | SUPPLEMENTAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION LP | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1320 | 2006-04-09 | 2006 | DELMONT | WESTMORELAND | PA | 15626 | .41 | 21+64 | 40.384 | 79.548 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR ROD PACKING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402700 | 235635.5631 | 521898.289 | 2700 | 1075.6098 | 400000 | 520822.6793 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 0 | 774490 | 2006-04-19 | 1000 | 1050 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | OTHER | COMPRESSOR ROD PACKING | OTHER | COMPRESSOR ROD PACKING | NO | NO | NO | COMPRESSOR |  | 2002 | [8 empty] | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | ON SUNDAY APRIL 9, A FIRE WAS OBSERVED AT DELMONT COMPRESSOR STATION. THE FIRE WAS CONFINED TO A SINGLE COMPRESSOR UNTI. TRANSITE BUILDING SIDING WAS DAMAGED, POTENTIALLY RELEASING ASBESTOS INTO THE BUILDING. THE FIRE WAS QUARANTINED DUE TO THE CONCERN OF EMPLOYEE EXPOSURE TO ASBESTOS. AN INITIAL ASSESSMENT WAS PERFORMED AND DETERMINED THE EVENT TO BE AN OIL FIRE CAUSED BY A TUBING LEAK AND BROKEN SIGHT GLASS WHICH CONTINUED TO FEED OIL INTO THE FIRE. SINCE THERE APPEARED TO BE NO GAS RELEASE AND DUE TO THE COFINED NATURE OF THE FIRE,TEXAS EASTERN DETERMINED IT DID NOT MEET THE DEFINITION OF A REPORTABLE INCIDENT. AN AIR MONITORING CONTRACTOR WAS BROUGHT IN AND VERIFIED NO ASBESTOS HAD BEEN RELEASED AND THE QUARANTINE WAS LIFTED ON THURSDAY APRIL 13, ALLOWING A MORE THOROUGH INVESTIGATION TO PROCEED AFTER THE EASTER HOLIDAY. THE INVESTIGATION WAS COMPLETED LATE ON TUESDAY, APRIL 18 AND FOUND ROD PACKING DAMAGE ON ONE OF THE COMPRESSOR CYLINDERS WHICH CAUSED A SMALL GAS LEAK INTO THE CRANKCASE. THE GAS VENTED FROM THE CRANKCASE INTO THE COMPRESSOR BUILDING AND IGNITED WHICH APPEARS TO HAVE CAUSED THE DAMAGE TO THE OIL SYSTEM. THE FIRE SHUT DOWN THE COMPRESSOR WHICH VENTED GAS FROM THE COMPRESSOR, LEAVING ONLY THE OIL FIRE WHICH CAUSED THE MAJORITY OF THE DAMAGE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060062 | 2006-05-01 12:50 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1322 | 2006-04-07 | 2006 | THURSTON | FAIRFIELD | OH |  |  | 1+96 ON G-300 | N39.50.385 | W082.33.312 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACKED VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63300 | 34423.5255 | 63456.4072 | 20985 | 8359.878 | 42315 | 55096.5292 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 793334 | 2006-04-07 | 145 | 170 | NO | NO | YES | NO | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION | COMPONENT |  | OTHER | IRON | NO | NO | NO | PIPELINE |  | 1952 | [5 empty] | WEDGE GATE VALVE | WALWORTH |  | UNDER GROUND |  | 24 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | A FOUR INCH BURIED VALVE DEVELOPED A CRACK RESULTING IN A LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060063 | 2006-05-03 11:02 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPELINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1529 | 2006-04-04 | 2006 | MAGNOLIA | AMITE | MS | 39652 | 635.53 | 440+08 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245000 | 117232.8611 | 131941.5692 | 207000 | 82463.4146 | 38000 | 49478.1545 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 51 | 793005 | 2006-04-04 | 640 | 800 | NO | YES | NO | NO | NO | NO | MISCHA GIBSON | 7132153632 | MISCHA.GIBSON@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 36 | 0.34 |  | 60000 | FLASH WELD |  | AO SMITH |  | UNDER GROUND |  | 54 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | MIC | YES | 1965 | NO
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20060064 | 2006-05-04 14:51 | SUPPLEMENTAL FINAL | 12462 |  | ENBRIDGE PIPELINES (MIDLA) L.L.C. | 1100 LOUISIANA SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 1450 | 2006-04-05 | 2006 | VIDALIA | CONCORDIA | LA | 71373 | MP 4764 + 52 |  | N31 32.785 | W91 28.307 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COUPLING SEPARATION | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 990500 | 577944.4366 | 1272065.3466 | 19500 | 7768.2927 | 34000 | 44269.9277 | 937000 | 1220027.1262 | NO | NO | YES | NO | 0 |  | 3 | 0 | 793117 | 2006-04-05 | 160 | 204 | YES | NO | NO | NO | NO | NO | TERRY MCMILLIN | 7133535670 | TERRY.MCMILLIN@ENBRIDGE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1926 | 18 | 0.38 |  | 35000 | LAP WELD | GATE | UNKNOWN |  | UNDER GROUND |  | 48 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | 04/16/2014 - FAILED COUPLING CAUSED BY VIBRATION & PRESSURE ON PIPING. LESLIE STEVENS COMPLIANCE COORDINATOR 832-214-1649 LESLIE.STEVENS@ENBRIDGE.COM THE FOLLOWING IS BASED ON INFORMATION OBTAINED FROM THE CONTRACTOR AND ITS EMPLOYEES AND THE ONE ENBRIDGE EMPLOYEE AT THE SITE. THE INITIAL OPERATION INVOLVED THE REPLACEMENT OF A 20¿ LOOP LINE VALVE LOCATED ON THE 20¿ LOOP LINE. PARALLEL TO THE 20¿ LOOP LINE IS ENBRIDGE¿S 22¿ MAIN LINE. THE LOOP LINE AND MAIN LINE ARE CONNECTED BY AN 18¿ CROSSOVER LINE. THE 18¿ CROSSOVER LINE VALVE HAD BEEN CLOSED AND THE 20¿ LOOP LINE SEGMENT HAD BEEN ISOLATED AT THE MAIN HEADER SOUTH OF THE 20¿ LOOP LINE VALVE TO BE REPLACED AND AT ANOTHER LOOP LINE VALVE LOCATED TO THE NORTH OF THE EXCAVATED SITE. THE ISOLATED SEGMENT WAS BLED DOWN TO ATMOSPHERE AT THIS POINT. THE 18¿ CROSSOVER LINE VALVE HAD BEEN SKIDDED OR SUPPORTED WITH BLOCKS SO THERE WOULD BE NO MOVEMENT WHEN THE 18¿ CROSSOVER LINE WOULD BE CUT DOWNSTREAM OF THE 18¿ CROSSOVER LINE VALVE. CUTS ONE, TWO AND THREE WERE THEN MADE. THE NOW FREE TEE SECTION WAS REMOVED FROM THE EXCAVATION AS WAS THE WEST CONCRETE WALL OF THE 18¿ CROSSOVER LINE VALVE BOX. THE SKIDDED 18¿ CROSSOVER LINE VALVE REMAINED STABLE AND UNMOVED AFTER THE CUTS WERE MADE. THE PORTION OF THE 20¿ LOOP LINE CONTAINING THE 20¿ LOOP LINE VALVE TO BE REPLACED, EXPOSED IN THE EXCAVATION, WAS CUT AGAIN (CUT 4) ON THE NORTH SIDE OF THE 20¿ LOOP LINE VALVE. THIS LEFT THE 20¿ LOOP LINE VALVE FREE TO BE REMOVED FOR REPLACEMENT. BECAUSE THE 20¿ LOOP LINE SEGMENT HAD A HUGE BLOCK OF CONCRETE POURED AROUND IT FOR SUPPORT WHEN ORIGINALLY LAID, THE BLOCK OF CONCRETE HAD TO BE BROKEN UP IN ORDER FOR THE 20¿ LOOP LINE VALVE AND 20¿ LOOP LINE CUT SEGMENT TO BE LIFTED OUT OF THE EXCAVATION. CONTRACTOR¿S CREWS BEGAN JACK HAMMERING ON THE BLOCK OF CONCRETE AND WITHIN 30 MINUTES TO AN HOUR THE GAS RELEASE OCCURRED. LATER IT WAS DISCOVERED THAT A COUPLING ON THE 18¿ CROSSOVER LINE BETWEEN THE 18¿CROSSOVER LINE VALVE AND THE 22¿ MAIN LINE, WHICH WAS STILL UNDER PRESSURE, HAD UNCOUPLED. ALSO PRESENT BETWEEN THE EXCAVATION AND THE COUPLING ON THE 18¿ CROSSOVER LINE WAS AN OLD ABANDON UNEXPOSED CISTERN. IT IS POSSIBLE THAT THESE WERE THE THREE MAIN CONTRIBUTING FACTORS TO THE RELEASE EVENT. IT IS BELIEVED THAT THE CROSSOVER COUPLING PROVIDED MINIMAL STRENGTH, TO THE HORIZONTAL PRESSURE CREATED WHEN THE 18¿ CROSSOVER LINE WAS CUT AND REMOVED FROM THE 20¿ LOOP LINE AND THAT THE ABANDON CISTERN PROVIDED REDUCED SOIL COMPACTION, VOLUME AND STRENGTH HOLDING CAPACITIES AFTER THE CUT AND REMOVAL WERE MADE. FINALLY, THE JACK HAMMERING ON THE CONCRETE POURED OVER THE CUT 20¿ LOOP LINE PROVIDED EXTERNAL VIBRATION TO THE REDUCED VOLUME OF UNDISTURBED, COMPACTED SOIL CREATED BY THE CISTERN. A SKETCH OF THE INCIDENT AREA WAS NOT ATTACHED BECAUSE OF LIMITATIONS REGARDING THE OPS ONLINE DATA ENTRY AND OPERATOR REGISTRATION SYSTEM, HOWEVER A SKETCH CAN BE PROVIDED UPON REQUEST.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060065 | 2006-05-05 16:02 | ORIGINAL FINAL | 26330 |  | ENOGEX INC | 515 CENTRAL PARK DRIVE, SUITE 600 | OKLAHOMA CITY | OKLAHOMA | OK | 73124-0300 | 1500 | 2006-05-05 | 2006 | ALLEN | COAL | OK | 74825 | ALLEN COMPRESSOR STATION |  | 34 42 32.72N | -96 23 31.54W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | GAS RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173497 | 79595.0232 | 69116.6911 | 173497 | 69116.6911 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 45 | 793145 | 2006-04-05 | 945 | 973 | YES | NO | NO | NO | NO | NO | MIKE REED | 4055584685 | REEDMD@OGE.COM | TRANSMISSION | COMPONENT |  | OTHER | PNUEMATIC ACTUATOR | NO | NO | NO | COMPRESSOR |  | 1985 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | AN AUTOMATED COMPRESSOR DISCHARGE VALVE FAILED TO FULLY CLOSE DURING A COMPRESSOR SHUTDOWN SEQUENCE DUE TO A BIND IN THE ACTUATOR LINKAGE ASSEMBLY. |  | INSTRUMENT AIR IS USED TO SUPPLY CONTROL PRESSURE TO A FAIL-OPEN ACTUATED BLOWDOWN VALVE LOCATED IN THE NATURAL GAS COMPRESSOR'S DISCHARGE PIPING. FOLLOWING THE MANUAL SHUTDOWN OF THE GAS COMPRESSOR, THE AIR COMPRESSOR WAS MANUALLY SHUTDOWN, WHICH EVENTUALLY RESULTED IN INSUFFICIENT CONTROL AIR PRESSURE TO MAINTAIN THE BLOWDOWN VALVE IN THE CLOSED POSITION. AS THE BLOWDOWN VALVE TRAVELED TO THE FAIL-OPEN POSITION, NATURAL GAS ESCAPED THROUGH THE OPEN DISCHARGE VALVE AND THE OPEN BLOWDOWN VALVE TO THE ATMOSPHERE. FOLLOWING THE ARRIVAL OF ON-CALL PERSONNEL, THE DISCHARGE VALVE WAS MANUALLY CLOSED TO ISOLATE THE ESCAPING NATURAL GAS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060066 | 2006-05-08 | SUPPLEMENTAL FINAL | 792 |  | ATLANTA GAS LIGHT COMPANY | 660 RALPH MCGILL BLVD | ATLANTA | FULTON | GA | 30312 | 1715 | 2006-03-30 | 2006 | CONLEY | DEKALB | GA | 30288 |  |  | 33.6709290 | -84.3409042 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58400 | 33216.8811 | 68901.0177 | 7900 | 3147.1545 | 50500 | 65753.8633 | 0 | 0 | YES | NO | NO | NO | 0 |  | 4 | 20 | 792500 | 2006-03-30 | 280 | 300 | NO | YES | NO | NO | NO | NO | SCOTT CRIDER | 4045844697 | SCRIDER@AGLRESOURCES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1984 | 36 | 0.38 | API-5L | 42000 | ELECTRIC RESISTANCE WELD |  |  |  | UNDER PAVEMENT |  | 60 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | FRACTURE | [10 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 9 | 24 | 1984 | WATER |  | 10 | [13 empty] | A LEAK WAS DETECTED DURING ROUTINE SURVEY AT THE BRANCH CONNECTION BETWEEN A 36¿ LINE AND A 6¿ LINE. UPON INVESTIGATION IT WAS FOUND THAT A CRACK HAD FORMED ON THE 36¿ PIPE BODY AT A POINT OUTSIDE THE WELD SEAM OF THE 6¿ CONNECTION. IT IS BELIEVED THAT THE 6¿ BRANCH CONNECTION CAUSED STRESSES ON THE 36¿ LINE WHICH LED TO THE FRACTURE. A CONTRIBUTING FACTOR WAS THE NON-STANDARD ANGLE AT WHICH THE CONNECTION WAS MADE. THE LEAK WAS NOT JUDGED TO CREATE A HAZARDOUS SITUATION BUT THE NATIONAL RESPONSE CENTER WAS NOTIFIED WHEN IT WAS DETERMINED THAT REPAIRS WOULD EXCEED THE THRESHOLD. PERMANENT REPAIRS HAVE SINCE BEEN COMPLETED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060067 | 2006-05-08 15:54 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 912 | 2006-04-12 | 2006 |  |  | LA |  |  | 527A-301A+14.27 | 29*03'12.6 | -89*35'51 | OFFSHORE |  | WEST DELTA | 61 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 140136.8872 | 280330.0388 | 50000 | 19918.6992 | 200000 | 260411.3396 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 793757 | 2006-04-12 | 1100 | 1246 | NO | NO | YES | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 30 | 0.5 | API 5L | 60000 |  |  |  | 1981 | UNDER WATER |  | 48 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | DIVERS CONFIRMED A LEAK ON THE 30-IN. TGP LN. NO. 527A-300, WEST DELTA BLK. 61, OFFSHORE GULF OF MEXICO. THE LEAK WAS IN THE 6 O'CLOCK POSITION AND IT WAS REPAIRED BY INSTALLING A CLAMP. THE INVESTIGATION COULD NOT DETERMINE THE EXACT CAUSE OF THE PINHOLE LEAK SINCE NO PIPE WAS REMOVED FOR ANALYSIS. THE PIPELINE HAS BEEN RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060068 | 2006-05-11 | SUPPLEMENTAL FINAL | 1800 |  | KEYSPAN ENERGY DELIVERY | 1 METRO TECH CENTER | BROOKLYN | NEW YORK | NY | 11201 | 1046 | 2006-04-10 | 2006 | QUEENS | NEW YORK | NY | 11369 |  |  | 40.76076 | -73.87431 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453321 | 265220.0695 | 587248.5142 | 3321 | 1323 | 0 | 0 | 450000 | 585925.5142 | YES | YES | NO | YES | 65 | THREAT TO THE PUBLIC |  | 52 | 793545 | 2006-04-10 | 280 | 350 | NO | NO | NO | NO | NO | YES | PARASHAR N SHETH, SECTION MANAGER & DAVID ANGELONE | 7184033347 | DANGELONE@KEYSPANENERGY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | OTHER | GAS METER | OTHER | STAINLESS STEEL 316L | NO | NO | NO | REGULATOR/METERING |  | 1992 | 2 | 0.05 | 316L | 38 | ERW | NA | MICROMOTION |  | ABOVE GROUND |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | DURING THE TRANSFER OF 2800 PSIG CNG FROM STORAGE VESSEL TO A 350 PSIG GAS SYSTEM, MICROMOTION METER TUBING RUPTURED. THIS OCCURRED DUE TO OVERPRESSURIZATION CREATED AS A RESULT OF AN INTERNAL BLOCKAGE. THIS CREATED A RUPTURE AND GAS IGNITED AT THE METER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060069 | 2006-05-16 18:10 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1100 | 2006-04-18 | 2006 |  |  | LA |  | 2.66 |  | 28.2436 | -92.0091 | OFFSHORE |  | SOUTH MARSH ISLAND | 146 |  | YES | NO | INTERSTATE | OTHER | PIPELINE DAMAGED BY RIG DRAGGING ACROSS LINE. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 33887.2996 | 69086.5747 | 10000 | 3983.7398 | 50000 | 65102.8349 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 794323 | 2006-04-18 | 650 | 1440 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 10.75 | 0.31 | API | 35000 |  |  |  | 1979 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | WORKOVER RIG DAMAGED PIPELINE | [51 empty] | LEAK DISCOVERED ON 10-IN. ANR LINE NO. 616-32 IN SOUTH MARSH ISLAND BLK. 146. DAMAGE TO PIPELINE PROBABLY SUSTAINED DURING HURRICANE RITA. PIPELINE WAS ABANDONED IN DECEMBER, 2006.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060070 | 2006-05-18 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 458 | 2006-04-21 | 2006 | ABBEVILLE | VERMILION | LA | 70510 | COMPRESSOR STATION 210 | 477+80.6 | 29^53'14.38 | 92^16'36.56 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10584266 | 6191576.9058 | 13705164.7129 | 84266 | 33569.3821 | 10500000 | 13671595.3307 | 0 | 0 | NO | YES | NO | YES | 200 | PRECAUTIONARY | 1 | 47 | 794665 | 2006-04-21 | 1023 | 1500 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS | 7139897473 | MAVIN.HOVIS@SUG.COM | TRANSMISSION | OTHER | COMPRESSOR SEAL | OTHER | CARBON | NO | NO | NO | COMPRESSOR |  | 1964 | [8 empty] | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | AT APPROXIMATELY 4:58 AM, UNIT # 4624 WENT INTO SURGE. THE SURGE RESULTED IN FAILURE OF THE HIGH PRESSURE COMPRESSOR SEAL ON THE GAS COMPRESSOR. A 20% GAS ALARM WAS NOTED @ 5:04 AM. MIGRATION OF HIGH PRESSURE SEAL OIL AND GAS ALONG THE SHAFT PAST THE FAILED SEAL WAS MOST LIKELY IGNITED BY THE EXHAUST. THE SHERIFF'S DEPARTMENT CONTACTED TRUNKLINE GAS COMPANY'S CONTROL @5:33 AM. STATION ESD WAS ACTIVATED @ 6:45AM MAKING THE AREA SAFE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060071 | 2006-05-30 16:08 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1640 | 2006-05-02 | 2006 |  |  | LA |  | 15+ | 527A-301A+15.27 | 29* 04 | 89*35'55 | OFFSHORE |  | WEST DELTA | 47 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210000 | 121786.1323 | 264395.0795 | 10000 | 3983.7398 | 200000 | 260411.3396 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 795877 | 2006-05-02 | 1100 | 1264 | NO | NO | YES | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 30 | 0.5 | API | 60000 |  |  |  |  | UNDER WATER |  | 120 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 7 | 1 | 1982 | WATER |  | 8 | 1946 | [12 empty] | DIVERS CONFIRMED LEAK ON THE 30-IN TGP LN. NO. 527A-300, IN WEST DELTA BLOCK 47, GULF OF MEXICO. LEAK OCCURRED IN A FIELD JOINT AT THE APPROX. 6:00 PIPE POSITION. PIPELINE WAS REPAIRED BY INSTALLING A CLAMP MAY 20, 2006.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060072 | 2006-05-31 15:14 | ORIGINAL | 31130 |  | DUKE ENERGY FIELD SERVICES (DUKE ENERGY INTRASTATE NETWORK) | 370 17TH STREET, SUITE 2500 | DENVER | DENVER | CO | 80202 | 1135 | 2006-05-12 | 2006 | ZAPATA | ZAPATA | TX | 78076 |  |  | 27 31.6' | 99 10.14' | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | 3RD PARTY DAMAGE - LINE HIT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25883 | 12827.5993 | 17082.4084 | 18390 | 7326.0976 | 7493 | 9756.3108 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 796986 | 2006-05-12 | 500 | 1110 | NO | YES | NO | NO | NO | NO | CINDY LOPEZ | 3615848518 | CALOPEZ@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 8.63 | 0.28 | GRADE A | 30000 | ERW | NA | NA |  | UNDER GROUND |  | 25 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | THIS INCIDENT WAS REPORTED TO THE NRC BEFORE IT WAS DETERMINED THAT IT DIDN'T MEET THE REPORTING CRITERIA OF $50,000 TOTAL LOSS. THIRD PART CONTRACTOR DOUBLE RAFTER H CONSTRUCTION WAS LAYING A WATER LINE FOR THE ASCHE RANCH. CONTRACTOR DID NOT MAKE A ONE-CALL REQUEST AND WAS DIGGING DEEPER THAN 16". CONTRACTOR STRUCK OUR LINE WITH THE ANGLE BLADE ON THE MAINTAINER CAUSING THE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060073 | 2006-05-31 15:27 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 1645 | 2006-05-04 | 2006 | CALIPATRIA | IMPERIAL | CA |  | 10200+00 |  | 33.169327 | -115.493178 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320000 | 184973.0428 | 398584.4891 | 20000 | 7967.4797 | 300000 | 390617.0094 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 796138 | 2006-05-04 | 650 | 756 | NO | NO | YES | NO | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 12 | 0.22 | X-42 | 1443 |  |  |  |  | UNDER GROUND |  | 60 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | A CRACK WAS DISCOVERED AT A MAIN-TO-MAIN CONNECTION. FURTHER INVESTIGATION DETERMINED THAT THE CRACK WAS THE RESULT OF CUMULATIVE LOAD UPON THE FAILED WELD. IT HAS NOT YET BEEN DETERMINED IF OUTSIDE FORCES CONTRIBUTED TO THIS FAILURE. |  | ON MAY 4, 2006, WHILE PERFORMING A LEAK INVESTIGATION ON A 12¿ HIGH PRESSURE SUPPLY LINE, A CRACK WAS DISCOVERED AT A MAIN-TO-MAIN CONNECTION. REPAIR COSTS WERE ESTIMATED TO EXCEED $50,000, AND AS A RESULT, THE INCIDENT WAS REPORTED TO DOT AND CPUC. FURTHER INVESTIGATION DETERMINED THAT THE CRACK WAS THE RESULT OF CUMULATIVE LOAD UPON THE FAILED WELD. ANY POTENTIAL THIRD PARTY CONTRIBUTION TO THIS FAILURE IS BEING INVESTIGATED BY SOCALGAS CLAIMS DEPARTMENT. ALL REPAIRS HAVE BEEN COMPLETED, AND LINES PUT BACK INTO NORMAL OPERATING PRESSURE. NO INJURIES OR PROPERTY DAMAGE RESULTED FROM THIS INCIDENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060074 | 2006-06-02 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HOUSTON | TX | 77056-3050 | 1530 | 2006-02-08 | 2006 | [6 empty] | 28 3.13N | 96 43.23W | OFFSHORE |  | MATAGORDA | 629 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76016 | 43691.1158 | 92913.431 | 6710 | 2673.0894 | 69306 | 90240.3415 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 |  |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7138401980 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 6.63 | 0.25 | 5LX-42 | 42000 |  |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1977 | NO | [57 empty] | SHORTAGES OF BOATS,DIVERS AND EQUIPMENT DUE TO HURRICANE REPAIRS IN THE GULF CREATED THE LONG DELAY FOR NO. 06-CA-304. A LEAK WAS DISCOVERED ON 2/8/06 AT THE REFERENCED LOCATION ON OUR 6 INCH PIPELINE. DIVERS WERE DISPATCHED ON 03/07/2006. THE LEAK ( A PINHOLE IN THE SIX O'CLOCK POSITION) WAS SUCCESSFULLY FIXED WITH A SLEEVE CLAMP.. RAILROAD COMMISSION OF TEXAS -- CALL IN NO. 06-CA-304. REPORT FINALIZED ON 07/12/07 WITH MINOR SUPPLEMENTAL DATA ENTERED. NO CHANGE IN COST
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060075 | 2006-06-02 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 830 | 2005-08-04 | 2005 | [6 empty] | 28 9.256N | 96 40.48W | OFFSHORE |  | MATAGORDA | 628 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194552 | 98974.122 | 142678.3991 | 125246 | 49549.4556 | 69306 | 93128.9436 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 |  |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7138401980 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 |  |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1975 | NO | [57 empty] | SHORTAGES OF BOATS, DIVERS AND EQUIPMENT DUE TO HURRICANE REPAIRS IN THE GULF CREATED THE LONG DELAY FOR NO. 05-CA-478. A LEAK WAS DISCOVERED ON 8/4/05 AT THE REFERENCED LOCATION ON OUR 10 INCH PIPELINE. DIVERS WERE DISPATCHED ON 03/07/2006. TWO HOLES WERE LOCATED ( 2 INCH ELONGATED HOLES/SPLITS IN THE SIX O'CLOCK POSITION) AND WERE SUCCESSFULLY FIXED ON 03/10/06 WITH TWO SLEEVE CLAMPS. RAILROAD COMMISSION OF TEXAS -- CALL IN NO. 05-CA-478. REPORT FINALIZED ON 07/12/07 WITH MINOR SUPPLEMENTAL DATA UPDATED. NO CHANGE IN COST
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060076 | 2006-06-05 12:17 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1745 | 2006-05-31 | 2006 | BUSHTON | RICE | KS | 67427-8842 | 0 | 0 | 38.5174 | -98.3514 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50150 | 23026.3425 | 20114.0077 | 50000 | 19918.6992 | 150 | 195.3085 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 799097 | 2006-05-31 | 50 | 3000 | YES | NO | NO | NO | NO | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1960 | 0.25 | 0.08 | 5LX | 35000 | SEAMLESS |  |  |  | ABOVE GROUND |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | STEEL TUBING | [8 empty] | A SECTION OF BSD PILOT GAS TUBING, INSTALLED BETWEEN THE 1¿ ISOLATION VALVE AND THE SHAFFER 2-WAY POPPET ESD CONTROL VALVE FOR THE D-LINE DISCHARGE VALVE BROKE. THE BROKEN TUBING VENTED THE PILOT GAS AND CAUSED BSD PRESSURE TO FALL BELOW THE LOW PILOT PRESSURE SWITCH SET POINTS IN THE INITIATION OF A BUILDING THREE BSD. THE UNIT 31 VENT VALVE ACTIVATED, BUT DID NOT MAKE THE LIMIT SWITCH TO CONFIRM THAT THE BSD FUNCTIONED PROPERLY. THE FAILURE OF THIS COMPONENT OF THE BSD SYSTEM INITIATED A STATION ESD. THE PILOT GAS TUBING BROKE AT THE POINT WHERE IT ENTERS THE SWAGELOK FITTING THAT ATTACHES THE TUBING TO THE SUPPLY LINE. PRELIMINARY EVALUATION OF THE BROKEN TUBING INDICATES THAT VIBRATION FATIGUE OR IMPROPER INSTALLATION, WHICH DID NOT FOLLOW NNG ENGINEERING STANDARDS, WAS THE ROOT CAUSE FOR THE FAILURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060077 | 2006-06-05 16:29 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1940 | 2006-05-06 | 2006 | TROUP | CHEROKEE | TX | 75769 | 37.98 | 2005+62 | 32.06343 | 95.17622 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55985 | 29500.8757 | 49413.4489 | 25985 | 10351.748 | 25000 | 32551.4175 | 5000 | 6510.2835 | NO | NO | NO | NO | 0 |  | 1 | 41 | 796339 | 2006-05-06 | 442 | 430 | NO | NO | NO | NO | YES | YES | JACK L ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1928 | 8.63 | 0.24 | API-5L | 24000 | FURNACE LAP WELD | NA | UNKNOWN |  | UNDER GROUND |  | 26 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1970 | NO | [57 empty] | COMPRESSSOR UNITS SHUTDOWN AT DOWNSTREAM COMPRESSOR STATION CAUSING PRESSURE TO RAISE IN PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060078 | 2006-06-07 10:18 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1300 | 2006-06-06 | 2006 | STRINGTOWN | ATOKA | OK |  | 34.7 | 183361 | 34.47.424 | 95.97.6967 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123791 | 63042.8311 | 93719.3714 | 74654 | 29740.2114 | 49137 | 63979.16 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 799718 | 2006-06-06 | 620 | 1050 | YES | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1991 | 24 | 0.25 | 5LX70 | 70000 | ERW |  | AMERICAN STEEL | 1990 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | GOUGE | [11 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 1 | 1 | 1990 | WATER |  | 7 | 1356 | [12 empty] | PIPE WAS RESTING ON ROCK IN DITCH.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060079 | 2006-06-12 13:06 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 725 | 2005-05-18 | 2005 | LOMA LINDA | SAN BERNARDINO | CA |  |  |  | 34.052468 | -117.231854 | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 38644.2267 | 58114.8379 | 45000 | 17802.7682 | 30000 | 40312.0698 | 0 | 0 | NO | NO | NO | NO | 0 |  | 9 | 52 | 796756 | 2006-05-11 | 300 | 340 | NO | YES | NO | NO | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.25 | X-42 | 21 |  |  |  |  | UNDER PAVEMENT |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | SEWER |  | YES | 5 | 15 | 2005 | ONE-CALL SYSTEM | YES | PAINT | NO | ACCURATE | YES | [36 empty] | ON MAY 18, 2005, A CONTRACTOR INSTALLING SEWER PULLED A GAS SERVICE OFF OF A 12¿ HIGH PRESSURE SUPPLY LINE, RIPPING A HOLE INTO THE LINE. GAS WAS CONTROLLED, REPAIRS PERFORMED AND ALL CUSTOMERS PUT BACK INTO SERVICE. ORIGINAL ESTIMATES OF COSTS ASSOCIATED WITH THIS INCIDENT WERE $25K. THE LINE HAD BEEN MARKED AND WAS EXPOSED AS THE RESULT OF A USA REQUEST. THE LIKELY CAUSE WAS FAILURE BY THE CONTRACTOR TO EXERCISE CARE WHILE MACHINE EXCAVATING IN VICINITY OF LINES. IN MAY OF 2006, A SUPERVISOR DISCOVERED THAT THE ACTUAL GAS LOSS CALCULATION WOULD PUT THE TOTAL COST ASSOCIATED WITH THIS INCIDENT OVER $50K. AS A RESULT THE INCIDENT WAS IMMEDIATELY REPORTED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060080 | 2006-06-12 14:08 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORPORATION | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84102 | 1130 | 2006-05-24 | 2006 | SPRAGUE | LINCOLN | WA | 99147 | 133.06 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 87898.8327 | 195308.5047 | 0 | 0 | 150000 | 195308.5047 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 798315 | 2006-05-24 | 607 | 811 | NO | NO | YES | NO | NO | NO | AUSTIN SORENSEN | 8015846117 | AUSTIN.SORENSEN@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 16 | 0.25 | 5LX | 52000 | ERW |  | A.O. SMITH | 1956 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | DENT | [11 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 9 | 4 | 1956 | WATER |  | 6 | 996 | [12 empty] | ONCE THE LEAK WAS CONFIRMED THE SITE WAS EXCAVATED TO DO NECESSARY REPAIRS. THE PIPE WAS FOUND RESTING ON A ROCK FROM ORIGINAL CONSTRUCTION. THE LEAK WAS FROM A DENT IN THE PIPE. THE DENT WAS A RESULT OF THE PIPE RESTING ON THE ROCK. THE REPAIR WILL BE IN COORDINATION WITH OTHER ANOMALY DIGS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060081 | 2006-06-13 15:14 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 2215 | 2006-05-19 | 2006 | EAST MILLFIELD | ATHENS | OH |  | MP 205-2 + 9.0 |  | 39* 26' 24 | 82* 04' 00 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 114653.9767 | 242337.6853 | 20000 | 7967.4797 | 180000 | 234370.2057 | 0 | 0 | NO | NO | NO | YES | 4 |  |  |  | 797824 | 2006-05-19 | 650 | 790 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 26 | 0.28 | API 5L | 52000 |  |  |  | 1952 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 9 | 1 | 1969 | WATER |  | 8 | 1052 | [12 empty] | A PRIVATE CITIZEN HEARD A BUBBLING NOISE IN THE VICINITY OF TGP'S 200-2 LINE, APPROXIMATE MP 205-2+ 9.0. UPON FURTHER INVESTIGATION, A LEAK WAS DISCOVERED APPARENTLY DUE TO A FAULTY WELD.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060082 | 2006-06-20 10:51 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1815 | 2006-06-16 | 2006 | SIOUX FALLS | MINNEHAHA | SD | 57106 | 72.85 | 384719 | 43.5085 | -96.8306 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14400 | 8438.2879 | 18749.6165 | 0 | 0 | 14400 | 18749.6165 | 0 | 0 | NO | YES | NO | YES | 10 | PRECAUTIONARY | 7 | 45 | 800994 | 2006-06-16 | 626 | 787 | NO | NO | NO | NO | YES | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | OTHER | FARM TAP SETTING (RURAL SERVICE PIPING) | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1956 | 1 | 0.18 | A106 | 35000 | SEAMLESS |  |  | 1990 | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | AT 6:15 PM A MIDAMERICAN EMPLOYEE REPORTED THAT A NORTHERN FARM TAP WAS ON FIRE. THERE WERE THUNDERSTORMS IN THE AREA AND IT IS LIKELY THAT LIGHTNING STUCK THE TAP. THE FIRE WAS EXTINGUISHED AT 2:00 AM. THE TAP WAS REPLACED. THE RISER PIPING AND ABERDEEN MAINLINE (M471B) WERE INSPECTED FOR DAMAGE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20060083 | 2006-06-26 16:52 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 215 | 2006-06-03 | 2006 |  | CRAWFORD | PA |  | MLV 221-1+9.64 | 508+75 | 41*41'42 | 79*55'40 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | TOWNVILLE SALES STATION EREGULATOR SETTING DAMAGED | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 55000 | 26657.1895 | 32031.8155 | 43800 | 17448.7805 | 11200 | 14583.035 | 0 | 0 | NO | YES | NO | NO | 0 |  |  |  | 799389 | 2006-06-03 | 650 | 790 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | REGULATOR PIPING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  |  | 26 | 0.28 | API | 52000 |  |  |  | 1950 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A CAR TRAVELING ON PA STATE HIGHWAY #408 LOST CONTROL AND STRUCK THE TGP TOWNSVILLE SALES STATION DAMAGING THE REGULATOR SETTING, CAUSING A GAS RELEASE AND RESULTING IN A FIRE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060084 | 2006-06-27 | ORIGINAL FINAL | 857 |  | MARKWEST PINNACLE L.P. | 3417 73RD STREET SUITE I | LUBBOCK | LUBBOCK COUNTY | TX | 79423 | 1038 | 2006-06-14 | 2006 | WOLFFORTH | LUBBOCK COUNTY | TX | 79423 | 16.276 M.P. | 5 | 33DEGREES 27.054 | 102 DEGREE 00.529W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | THIRD PARTY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 800672 | 2006-06-14 | 688 | 920 | NO | YES | NO | NO | NO | NO | HAROLD PAULK, FIELD TECHNICIAN | 8067990569 | HPAULK@MARKWEST.COM | TRANSMISSION | OTHER | NIPPLE VALVE CONNECTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1984 | 1 |  | ASTM A106 | [5 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [55 empty] | NIPPLES | [9 empty] | IT IS BELIEVED THAT A FARM TRACTOR STRUCK AND DAMAGED A METER ON THE PIPELINE CAUSING THIS INCICDENT. A JOHN DEERE TRACTOR WAS OBSERVED NEAR THE INCIDENT SITE WHEN THE EVENT WAS REPORTED. THE DAMAGE TO THE PIPE WAS CONSISTENT WITH BEING STRUCK BY A VEHICLE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060085 | 2006-07-07 17:00 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 745 | 2006-06-09 | 2006 | VILONIA | FAULKNER | AR | 72173 | LINE JM-30 VILONIA TB | 1024+63 | 35.4750 | -92.11959 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100766 | 59048.0918 | 131203.0452 | 0 | 0 | 100766 | 131203.0452 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 800083 | 2006-06-09 | 175 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | METER STATION | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1971 | [8 empty] | INSIDE/UNDER BUILDING |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 7 |  |  | THE VILONIA TOWN BORDER STATION ON LINE JM-30 WAS BEING REPAINTED ON WEDNESDAY, JUNE 7, 2006. A REGULATOR AND METER RUN WAS SWEATING, PROHIBITING IT FROM BEING PAINTED. GAS FLOW WAS SWITCHED TO A SECONDARY REGULATOR AND METER RUN BY CEGT TECHNICIANS TO ALLOW THE PRIMARY RUN TIME TO DRY AND BE PAINTED. DURING THE SWITCH, A SERIES OF DIFFERENT VALVES WERE CLOSED, ISOLATING THE REMAINING SECTION OF THE STATION, AND ENABLING THE PAINTERS TO FINISH THEIR WORK. ON AUGUST 9TH, WHEN THE TIME CAME TO OPEN THE PRIMARY RUN THAT HAD BEEN ISOLATED, MISCOMMUNICATION, LACK OF KNOWLEDGE AND FAILURE TO FOLLOW COMPANY PROCEDURE LED TO THE CLOSURE OF AN OUTLET VALVE (FIGURE 1 AND 2) ON THE SECONDARY RUN, WHICH CAUSED THE GAS FLOW TO BE CUT OFF TO CENTERPOINT ENERGY SGO¿S FACILITIES. THIS RESULTED IN THE LOSS OF APPROXIMATELY 1580 SGO CUSTOMERS IN AND AROUND THE TOWN OF VILONIA
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060086 | 2006-07-10 18:23 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE COMPANY OF AMERICA | 500 DALLAS STREET 1000 | HOUSTON | HARRIS | TX | 77002 | 1400 | 2006-07-07 | 2006 | MARSHALL | PANOLA | TX |  | VALVE 2446 | 2156961 | 31.59.782 | 94.30.979 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | 3RD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99200 | 54860.7881 | 105939.3787 | 25700 | 10238.2114 | 73500 | 95701.1673 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 803336 | 2006-07-07 | 808 | 858 | YES | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | 3RD PARTY DAMAGE | STEEL |  | NO | NO | NO |  |  |  | 36 | 0.33 | 5LX65 | 65000 | DSAW |  | U.S. STEEL | 1979 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DISPOSAL WELL DRILLER | NO |  |  |  |  | NO | [40 empty] | 3 RD PARTY DID NOT MAKE A ONE CALL AND DUG INTO THE PIPELINE AND CAUSED AN NON-LEAKING GOUGE. THE GOUGE OCCURED IN A SIDE BEND CAUSING THE PIPELINE TO BE BLOWN DOWN FOR REPAIR. THE COST OF THE REPAIRS EXCEEDED $50,000.00.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060087 | 2006-07-12 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1830 | 2006-04-02 | 2006 | [6 empty] | 20 6.86 | 96 39.57 | OFFSHORE |  | MATAGORDA | 628 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615592 | 356999.134 | 775019.8287 | 29342 | 11689.0894 | 586250 | 763330.7393 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | N/A |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7135953612 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 | N/A | N/A | N/A |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1975 | NO | [57 empty] | A LEAK WAS DISCOVERED ON 4/2/06 AT THE REFERENCED LOCATION ON OUR 10" PIPELINE. DIVERS WERE DISPATCHED ON 5/8/06. THE LEAK (A PINHOLE IN THE SIX O'CLOCK POSITION) WAS SUCCESSFULLY FIXED ON 5/13/2006 WITH A SLEEVE CLAMP. THE ABOVE COSTS REFLECT THE USE OF OVERSIZED EQUIPMENT AND CREWS TO EFFECTUATE THE REPAIRS IN LIGHT OF A TIGHT MARKET CREATED DUE TO REPAIRS FOR HURRICANE DAMAGE. IT WAS NECESSARY TO SHUT-IN THE LINE IN ORDER TO INSTALL THE CLAMP. RAILROAD COMMISSION OF TEXAS - CALL IN NO. 06-CA-409
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060088 | 2006-07-11 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION, LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 1500 | 2006-06-13 | 2006 | N/A | TERREBONNE | LA |  | 10.9813 | N/A | N 29.2377 | W 91.0258 | OFFSHORE |  |  |  | LA | NO | YES | INTERSTATE | OTHER | BLEED VALVE LEAKING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 800554 | 2006-06-13 | 950 |  | NO | NO | NO | NO | YES | NO | JEFFREY B. MCMAINE | 2706886361 | JEFF.B.MCMAINE@TXGT.COM | TRANSMISSION | OTHER | BLOCK AND BLEED VALVE ON 16 | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | [5 empty] | GROVE |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | A 1" BLOCK AND BLEED VALVE, LOCATED ON A 16" GROVE VALVE WAS FOUND LEAKING. |  | 1" BLOCK AND BLEED VALVE, UNDER THE BODY OF 16" GROVE GATE VALVE, WAS FOUND LEAKING. THE 16" VALVE WAS REPLACED ON 06-28-06 ON CO48107.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060089 | 2006-07-21 17:03 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1800 | 2006-07-20 | 2006 | CORPUS CHRISTI |  | TX |  |  |  | 27.37857 | - 96.391016 | OFFSHORE |  | MUSTANG ISLAND | 782 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300000 | 760517.6498 | 1683636.8805 | 10000 | 3983.7398 | 1290000 | 1679653.1406 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 804942 | 2006-07-20 | 918 | 1250 | NO | YES | NO | NO | NO | NO | BYRON WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.38 | API 5LX | 60000 | DSAW |  | STELCO | 1986 | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1986 | NO | [57 empty] | THIS LEAK WAS DISCOVERED BY APACHE IN BLOCK 782. THE WATER DEPTH IS 160 TO THE MUD LINE PLUS 7 FEET OF BURIAL. A PLIDCO SLEEVE WILL BE USED TO REPAIR THE PIPE. THE PRESSURE IS BEING KEPT BELOW 250 PSIG UNTIL NORTHERN COMPLETES AN ASSESSMENT OF ITS OPTIONS. SUPPLEMENTAL/FINAL - ON AUGUST 29, NORTHERN INSTALLED A LEAK CLAMP. THE LEAK WAS CAUSED BY A CRACK APPROXIMATELY FOUR INCHES LONG; IT WAS NOT ON THE LONGITUDINAL SEAM WELD. THE REPAIR WAS MADE AS A PRECAUTIONARY MEASURE TO PREVENT SAFETY AND ENVIRONMENTAL CONCERNS FROM OCCURRING, AND NOT FOR RETURNING THE LINE TO SERVICE. THE LINE REMAINS OUT OF SERVICE WITH A POSITIVE PRESSURE OF 84 PSIG TO PREVENT ENTRY OF SEA WATER. NORTHERN IS CONSIDERING APPROPRIATE INTEGRITY ASSESSMENT OPTIONS AND COURSES OF ACTION. NORTHERN WILL FILE FOR A TEMPORARY CESSATION ON SEPTEMBER 6 PER TITLE 30, CHAPTER II OF THE CODE OF FEDERAL REGULATIONS. ALEX ALVARDO OF THE MMS HAS BEEN VERBALLY NOTIFIED AND UPDATED VIA A E-MAIL MMS SEGMENT 14888 UPDATE - AUGUST 31 FROM ADAM WRIGHT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060091 | 2006-07-27 17:44 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 900 | 2006-07-05 | 2006 |  |  | LA |  | MP 507K-800 +8.34 |  | 29*27'27 | -93*8'9 | OFFSHORE |  | WEST CAMERON | 143 |  | YES | NO | INTERSTATE | OTHER | LEAK NEAR EXISTING SIDE VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 67774.5993 | 138173.1495 | 20000 | 7967.4797 | 100000 | 130205.6698 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 803000 | 2006-07-05 | 999 | 1440 | YES | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | NEAR A SUB-SEA ASSEMBLY | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 16 | 0.47 | API | 52000 |  |  | US STEEL | 1972 | UNDER WATER |  | 48 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | A LEAK WAS DISCOVERED ON THE 16 IN. TGP LINE NO. 507K-800, IN WEST CAMERON BLK. 143, BY STONE ENERGY SERVICES. DIVERS DEPLOYED TO INVESTIGATE THE LEAK ACTUALLY NEVER FOUND THE LEAK. THERE HAS BEEN NO EVIDENCE OF A LEAK SINCE AND THE FACILITY CONTINUES IN SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060092 | 2006-07-29 12:04 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1017 | 2006-07-10 | 2006 | LAKEVILLE | DAKOTA | MN | 55044 | 98.851 | 521933 | 44.6359 | -93.2932 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 27136.814 | 49740.2288 | 17000 | 6772.3577 | 33000 | 42967.871 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 |  | 2006-07-10 | 602 | 796 | NO | NO | NO | NO | YES | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 2 | 0.22 | 5LX | 42000 | SMLS |  |  |  | OPEN DITCH |  | 42 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | ON JULY 10 NORTHERN WAS EXCAVATING THE 16-INCH WELCOME TO MINNEAPOLIA 1P MAINLINE IN PREPARATION FOR A SMART PIG RUN. AN ELBOW WAS BEING EXAMINED TO ENSURE THAT THE SMART TOOL WOULD PASS. DURING EXCAVATION OF THE 16-INCH ELBOW THE BACKHOE STRUCK AND DAMAGED AN ABANDONED FARM TAP. THE ABANDONED FARM TAP CONSISTED OF A 2-INCH VALVE, 12 INCHES OF 2-INCH PIPE AND A SADDLE PAD, STICKING UP ABOVE THE MAINLINE ABOUT 21 INCHES. THE BACKHOE BUCKET SNAGGED THE UNEXPOSED ABANDONED FARM TAP BENDING IT AND CRACKING THE WELD AT THE TOP OF THE SADDLE PAD. THE CRACK WAS OPENED ABOUT 1/16" ABOUT ONE QUARTER WAY AROUND THE 2-INCH. THE PIPELINE WAS BLOWN DOWN AND 35 FEET OF 16-INCH PIPE WAS REPLACED ON JULY 11. THE FARM TAP WAS REMOVED AND NOT REPLACED. THE 16-INCH ELBOW THAT WAS THE INITIAL REASON FOR THE EXCAVATION WAS ALSO REMOVED AND REPLACED WITH A 3D ELBOW. SUPPLEMENTAL/FINAL INFORMATION - REPAIRS WERE MADE AS INDICATED IN THE ORIGINAL NARRATIVE WITH THE ONLY CHANGE BEING THAT CURRENTLY THE COST TO REPAIR HAS BEEN ESTIMATED TO BE APPROXIMATELY $45,500. NO FURTHER ACTION IS PLANNED OR REQUIRED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060093 | 2006-08-03 11:54 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORPORATION | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84102 | 1914 | 2006-07-28 | 2006 | MOUNTAIN HOME | ELMORE | ID | 83623 | 1.36 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579224 | 310258.1125 | 547036.7224 | 229224 | 91316.878 | 350000 | 455719.8444 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 40 | 805935 | 2006-07-28 | 890 | 910 | NO | NO | YES | NO | NO | NO | AUSTIN SORENSEN | 8015846117 | AUSTIN.SORENSEN@WILLIAMS.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 16 | 0.23 |  | 46000 | ERW |  | KAISER | 1962 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | LF ERW |  | MATERIAL DEFECT |  | NO | YES | 12 | 5 | 1962 | NATURAL GAS |  | 8 | 1055 | [12 empty] | RUPTURE DUE TO MANUFACTURING DEFECTS IN FACTORY GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060095 | 2006-08-07 14:02 | SUPPLEMENTAL FINAL | 18646 |  | STINGRAY PIPELINE COMPANY, L.L.C. | 1100 LOUISIANA SUITE 3300 | HOUSTON | HARRIS | TX | 77002 | 230 | 2006-07-10 | 2006 | [8 empty] | OFFSHORE |  | EC | 268 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1319510 | 758018.1295 | 1610077.7126 | 119510 | 47609.6748 | 1200000 | 1562468.0378 | 0 | 0 | NO | NO | NO | NO | 0 |  | 142 | 30 | 803535 | 2006-07-10 | 856 | 1200 | NO | YES | NO | NO | NO | NO | GREGG JOHNSON | 7133536369 | GREGG.JOHNSON@ENBRIDGE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1984 | 20 | 0.44 | API 5L-X-60 | 2628 | DSAW | BALL | CAMERON | 1974 | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | 20" PIPELINE WAS BLOWN DOWN TO 200 PSI AND AN 8" VALVE WAS INSTALLED INLINE WITH THE EXSITING 8" TAP VALVE, WHICH WOULD NOT SEAL OFF COMPLETELY. NO LEAKS WERE DETECTED AFTER REPAIRS. REPAIRS COMPLETED ON 7-16-06.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060096 | 2006-08-08 08:45 | SUPPLEMENTAL FINAL | 21252 |  | VIKING GAS TRANSMISSION COMPANY | 3140 NEIL ARMSTRONG BLVD., SUITE 208 | EAGAN | DAKOTA | MN | 55121 | 900 | 2006-07-26 | 2006 | CLEAR LAKE | POLK | WI |  | 2222-1+16.17 | 854+01 | N45.20951 | W092.29603 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK IN BODY OF PIPE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376500 | 189011.0689 | 265659.1923 | 248500 | 98995.935 | 128000 | 166663.2574 | 0 | 0 | NO | NO | NO | YES | 9 | COMPANY POLICY | 7 | 5 | 805584 | 2006-07-26 | 816 | 877 | YES | NO | NO | NO | NO | NO | MARK MICKELBERG | 6519940332 | MARK.MICKELBERG@ONEOK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 24 | 0.28 | API 5L | 52000 | DSAW | NA | REPUBLIC | 1960 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | SCC | OTHER | SCC | YES | 1960 | NO | [57 empty] | LANDOWNER REPORTED GAS LEAK TO GAS CONTROL ON JULY 26, 2006. VIKING PERSONNEL RESPONDED TO SITE AND CONFIRMED THE LEAK LOCATION. VIKING PERSONNEL PROCEEDED TO ISOLATED THE VALVE SECTION BETWEEN MLV 2222 AND MLV 2223 AND REDUCED PRESSURE TO EXCAVATE AND LOCATE LEAK. THE VALVE SECTION WAS BLOWN DOWN AND NDE TESTING CONFIRMED CRACK LIKE FEATURES IN THE PIPE BODY. REPAIRS WERE MADE BY REPLACING APPROXIMATELY 50 FEET OF 24 " PIPE. THE LINE WAS RETURNED TO SERVICE AT A REDUCED PRESSURE (80% OF ACTUAL)ON JULY 30, 2006.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060097 | 2006-08-09 09:19 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1430 | 2006-08-03 | 2006 | NEW VIRGINIA | WARREN | IA |  | 688 | 3142310 | 41.23186 | -93.73660 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232204 | 111286.6295 | 126305.3808 | 194800 | 77603.252 | 37404 | 48702.1287 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 806589 | 2006-08-03 | 700 | 712 | YES | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 2 | 0.22 | 5LX GRB | 35000 | SMLS |  |  |  | UNDER GROUND |  | 120 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | 6 | 26 | 1969 | WATER |  | 8 | 1068 | [12 empty] | WELD CRACKED IN 2-INCH NIPPLE WHICH WAS PART OF SIDE TAP CONNECTION BETWEEN 36-INCH CARRIER PIPE AND 2-INCH SIDE TAP VALVE, 1969 CONSTRUCTION.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20060099 | 2006-08-09 | SUPPLEMENTAL | 1031 |  | ONYX PIPELINE COMPANY | 802 N. CARANCAHUA, SUITE 575 | CORPUS CHRISTI | NUECES | TX | 78470 | 930 | 2006-07-15 | 2006 | CLARKWOOD | NUECES | TX |  |  |  | 27 38.62'N | 47 31.65'W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51000 | 26323.3495 | 41101.7756 | 28000 | 11154.4715 | 23000 | 29947.3041 | 0 | 0 | NO | NO | YES | NO | 0 |  | 2 | 0 |  |  | 780 | 975 | NO | YES | NO | NO | NO | NO | GARY W. BOENING | 3618847878 | GARY@ONYXGAS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 12.75 | 0.32 | API 5L GRADE B |  | ERW |  |  |  | UNDER GROUND |  | 43 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | IMPROPER CATHODIC PROTECTION | COATING DISBONDMENT | YES | 1955 | NO | [57 empty] | THE 12" PIPELINE WAS HYDROTESTED TO 1100 PSIG DURING JANUARY 2006. THE LINE TESTED GOOD. THE LINE WAS EXPOSED AND CUT IN TWO PLACES TO INSTALL NEW BLOCK VALVES. THE OBSERVED PIPE APPEARED TO BE IN EXCELLENT SHAPE. IT IS THOUGHT THAT THE LEAK OCCURED AT A POINT IN THE PIPE WHICH MAY HAVE HAD SOME COATING DISBONDMENT AND POSSIBLY SOME LOCALIZED LOW CATHODIC PROTECTION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060100 | 2006-08-01 | ORIGINAL | 31978 |  | ATMOS PILELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1308 | 2006-06-07 | 2006 | LANCASTER | DALLAS | TX | 75146 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81000 | 44539.2327 | 84681.8901 | 23000 | 9162.6016 | 58000 | 75519.2885 | 0 | 0 | NO | NO | NO | NO | 0 |  | 11 | 15 |  | 2006-06-07 | 555 | 7108 | NO | YES | NO | NO | NO | NO | ELLEN WEAVER | 2142062875 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.28 | API 5LX | 42000 | SEAMLESS |  |  |  | UNDER GROUND |  | 28 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | EQUIPMENT TEST | NO |  |  |  |  | NO | [40 empty] | AN EXCAVATOR WHO WAS TESTING HIS EQUIPMENT STRUCK A TRANSMISSION LINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060101 | 2006-08-11 09:47 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1002 | 2006-08-10 | 2006 | CENTERVILLE | ST. MARY | LA | 70522 | MP 66.5 / VS 1207 | 3511+20 | 29.7214 | -91.4227 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77646 | 35621.5679 | 30932.1463 | 77646 | 30932.1463 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 20 | 807459 | 2006-08-11 | 894 | 894 | NO | YES | NO | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 2002 | [5 empty] | PILOT OPERATED RELIEF VALVE | AXELSON TYPE HF |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | SCADA OUTAGE RESULTED IN PRESSURE REACHING THE RELIEF VALVE SET POINT. |  | PROBLEMS WITH SCADA SYSTEM RESULTED IN PRESSURE REACHING THE SET POINT OF THE RELIEF VALVE LOCATED ON COLUMBIA GULF'S EAST LATERAL LINE. PRESSURE ON THE LINE WAS 894 PSIG AND THE SET POINT OF THE RELIEF VALVE IS 894 PSIG. THE RELIEF VALVE VENTED FOR APPROXIMATELY 20 MINUTES BEFORE IT WAS RESET TO A POINT BELOW 894 PSIG. THE PIPELINE WAS MONITORED UNTIL PROBLEMS WITH THE SCADA SYTEM WERE CORRECTED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060102 | 2006-08-17 10:46 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION INC. | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 830 | 2006-07-18 | 2006 | NEW MARTINSVILLE | MARSHALL | WV | 26155 |  |  | 39.83811 | 80.81610 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RUPTURE OCCURRED ON ANOTHER COMPANY'S PIPELINE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 4 | 804551 | 2006-07-18 | 270 | 320 | NO | YES | NO | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN_A_MILLER@DOM.COM | TRANSMISSION | OTHER | FAILURE OCCURRED ON ANOTHER COMPANY'S PIPELINE | STEEL |  | NO | NO | NO | REGULATOR/METERING | [13 empty] | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | OTHER | INADVERTENT VALVE OPERATION | 0 | 0 | N | 2 |  |  | AT APPROXIMATELY 8:30 A.M. ON JULY 18, 2006, DOMINION TRANSMISSION EMPLOYEES INADVERTENTLY CLOSED THE VALVES ON THE SENSING LINES TO A REGULATOR SET LOCATED AT XS-2125. THIS ACTION CAUSED THE REGULATORS TO OPEN; THEREBY, RESULTING IN OVERPRESSURING OF THE CUSTOMER¿S DOWNSTREAM PIPING. THE CUSTOMER¿S PLASTIC PIPELINE RUPTURED AND TRAFFIC WAS SHUTDOWN ON HIGHWAY 2 IN MARSHALL COUNTY, WEST VIRGINIA UNTIL SUCH TIME THAT THE AREA WAS MADE SAFE AND REPAIRS WERE COMPLETE.DOMINION TRANSMISSION¿S FACILITIES DID NOT EXCEED THEIR MAXIMUM ALLOWABLE OPERATING PRESSURE; HOWEVER, THIS INCIDENT WAS DEEMED TO BE SIGNIFICANT AND THUS REPORTED TO THE NATIONAL RESPONSE CENTER.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060103 | 2006-08-17 14:11 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1130 | 2006-07-19 | 2006 |  |  | LA |  |  |  | 28 22.615 | 91 39.688 | OFFSHORE |  | EUGENE ISLAND | 286 | LA | NO | NO | INTERSTATE | OTHER | LEAK FROM GREASE FITTING ON VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 175797.6654 | 390617.0094 | 0 | 0 | 300000 | 390617.0094 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 804711 | 2006-07-19 | 1100 | 1250 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | [5 empty] | 16 BALL VALVE | CAMERON | 1969 | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | GREASE ZERK ON 16" BALL VALVE SHEARED OFF. |  | GREASE ZERK ON 16" BALL VALVE SHEARED OFF. GAS SLOWLY LEAKING FROM ZERK. GREASE ZERK WAS REPLACED ON 8/23/06.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060104 | 2006-08-17 17:03 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1207 | 2006-07-22 | 2006 |  | CLARK | KY |  | MP 105-1 + 3.7 |  | 37* 53' 54 | 84* 1'1 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 887566 | 485120.3491 | 907148.5089 | 275000 | 109552.8455 | 431000 | 561186.4369 | 181566 | 236409.2265 | NO | YES | NO | YES | 14 | PRECAUTIONARY |  |  | 805135 | 2006-07-22 | 716 | 750 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1944 | 24 | 0.25 | API | 50000 |  |  | A.O. SMITH | 1944 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1950 | NO | [57 empty] | THE 24 IN. TGP LN. NO. 100-1, NEAR MP 105-1 + 3.70, RUPTURED NEAR SH 974. THERE WAS A GAS RELEASE AND SUBSEQUENT IGNITION, BUT NO INJURIES OCCURRED. THE FAILURE OCCURRED IN A FLASH WELDED LONG SEAM (AO SMITH PIPE)AND WAS DUE TO WALL THINNING PRIMARILY FROM EXTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060105 | 2006-08-21 13:30 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 1010 | 2006-08-21 | 2006 | LOST RIVER | HARDY | WV | 26812 |  | 8299+32 | 38.876133619 | -78.85698795 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132908 | 61406.1039 | 56015.9959 | 129512 | 51594.2114 | 1896 | 2468.6995 | 1500 | 1953.085 | NO | NO | NO | NO | 0 |  | 4 | 0 | 808563 | 2006-08-21 | 725 | 800 | YES | NO | NO | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@CPG.COM | TRANSMISSION | OTHER | WELD-O-LET | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 2 | [7 empty] | UNDER GROUND |  | 19 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | ST PIPELINE, OUR CONTRACTOR HIT A 2" NIPPLE JUST BELOW THE TAP VALVE ON LINE WB-LOOP WHILE EXCAVATING FOR CONSTRUCTION RELATED ACTIVITIES AT LOST RIVER COMPRESSOR STATION. APPROXIMATELY 12 MILES OF PIPELINE WAS BLOW DOWN. THERE NO INJURIES OR FIRE. NO ONE WAS EVACUTATED. REPAIRS WERE MADE 8/21/06 AND THE LINE WAS PLACED BACK INTO SERVICE. UPDATED BY PHMSA ON 12/7/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060106 | 2006-08-22 11:41 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC. | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1514 | 2006-07-25 | 2006 | JOPLIN | NEWTON | MO | 64804 |  | SERIES 120 STATION 46784 | 37.046529285 | -94.47354076 | ONSHORE | 3 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297344 | 172034.7084 | 371485.2739 | 17344 | 6909.3984 | 280000 | 364575.8755 | 0 | 0 | YES | NO | NO | YES | 200 | THREAT TO THE PUBLIC | 2 | 11 | 805480 | 2006-07-25 | 350 | 400 | YES | NO | NO | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 16 | 0.25 |  | 35000 |  |  | REPUBLIC STEEL |  | UNDER PAVEMENT |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 7 | 5 | 2006 | ONE-CALL SYSTEM | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | WE WERE NOTIFIED OF A BLOWING LEAK NEAR THE HOLIDAY INN IN JOPLIN AT 3:15 PM. WE RESPONDED TO FIND GAS BLOWING FROM THE VENT ON THE NORTH SIDE OF I-44. AN ABOVE GROUND INSPECTION WAS PERFORMED AND NO APPARENT THIRD PARTY DAMAGE WAS NOTICED. HOWEVER THERE WERE LIVE HIGH VOLTAGE LINES DOWN ACROSS THE INTERSTATE AND ACROSS THE TOP OF A GUARD RAIL THAT WAS 30 FEET FROM THE PIPEINE CROSSING. THE DISTRICT MANAGER, RICK SCHUMAN, DETERMINED THE AREA TO BE UNSAFE DUE TO GAS BLOWING AND THE PROXIMITY OF TWO HOTELS AND I-44. WE BEGAN TO BLOW DOWN THE PIPELINE AT APPROXIMATELY 4:15 PM. THE PIPELINE WAS BLOWN DOWN BY 6:15 PM AND THE CREW BEGAN TO EXCAVATE AND MAKE REPAIRS. DECEMBER 8, 2006 RECEIVED FINAL REPORT FROM BATTELL WHICH STATES:"LEAKAGE IN LINE HM (RANGE LINE) RESULTED FROM CURRENT FLOW DUE TO THE ELECTRIC TRANSMISSION LINE FAULT. THE CURRENT FLOW CREATED ELECTRIC ARCING WITH THE CASED CROSSING RESULTING IN LOCALIZED MELTING THAT PENETRATED THE PIPE WALL AT MULTIPLE LOCATIONS. ASIDE FROM THE ARCING-RELATED DAMAGE, THERE WERE NO OTHERE FACTORS OR PIPE CONDITONS FOUND THAT CONTRIBUTED TO THE GAS LEAKAGE THAT OCCURRED."
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060107 | 2006-08-22 14:38 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 1442 | 2006-07-28 | 2006 | MANSFIELD | RICHLAND | OH | 44903 |  | 284+17 | 40.41.632 | 082.27.676 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65315 | 32508.9559 | 44093.451 | 45315 | 18052.3171 | 20000 | 26041.134 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 28 | 805902 | 2006-07-28 | 176 | 250 | NO | NO | NO | NO | YES | NO | MARK NEWMAN | 3043572869 | MNEWMAN@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 12.75 | 0.25 | API 5LX | 42000 | SEAMLESS |  | NATIONAL TUBE | 1965 | UNDER GROUND |  | 42 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON 7/28/06 AT APPROXIMATELY 2:42 PM COLUMBIA GAS TRANSMISSION'S LINE D-434 WAS DAMAGED BY A LANDOWNER WHO WAS OPERATING A TREE SPADE IN CLOSE PROXIMITY TO THE PIPELINE. THE EQUIPMENT HIT THE PIPELINE CAUSING A LEAK. TEMPORARY REPAIRS CONSISTED OF INSTALLING A STOPPLE FITTING IN ORDER TO RE-ROUTE GAS IN THE AREA. PERMANENT REPAIRS CONSISTED OF REPLACING 54" OF THE EXISTING PIPE WITH A NEW PIPE. PERMANENT REPAIRS WERE COMPLETED ON 7/29/06. THE LANDOWNER DID NOT NOTIFY THE STATE'S ONE CALL SYSTEM PRIOR TO THIS EVENT. THE PIPELINE ROW IS VISIBLE AND PROPERLY MARKED. THE LANDOWNER WAS AWARE THAT OUR PIPELINE WAS ON HIS PROPERTY AND THE APPROXIMATE PROXIMITY TO WHICH HE WAS WORKING. SINCE HE DID NOT NOTIFY THE ONE-CALL SYSTEM, THE AREA IN WHICH HE WAS WORKING WAS NOT MARKED. A COPY OF THE COMPANY¿S PUBLIC AWARENESS BROCHURE AND MINIMUM CONSTRUCTION GUIDELINES HAS BEEN PROVIDED TO THE LANDOWNER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060108 | 2006-08-22 | SUPPLEMENTAL FINAL | 6141 |  | PUBLIC SERVICE COMPANY OF NEW MEXICO | 414 SILVER AVENUE, SW | ALBUQUERQUE | BERNALILLO | NM | 87102-1007 | 330 | 2006-07-29 | 2006 | ALBUQUERQUE | BERNALILLO COUNTY | NM | 87114 | BTW MP 1 AND MP 2, ALAMED |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60900 | 29910.9862 | 38268.0577 | 45400 | 18086.1789 | 15500 | 20181.8788 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 805953 | 2006-07-29 | 439 | 466 | NO | NO | NO | YES | NO | NO | GARY G. ROYBAL, P.E. MANAGER, DOT COMPLIANCE & TECHNICAL | 5056973636 | GARY.ROYBAL@NMGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.22 | X-42 | 42000 | ERW | N/A |  | 1960 | UNDER GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | VANDALISM | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [65 empty] | PIPELINE WAS DAMAGED BY THE UNAUTHORIZED USE OF HEAVY EQUIPMENT (BULLDOZER), THAT WAS DRIVEN INTO THE PIPELINE BY AN INTOXICATED PERSON OR PERSONS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060109 | 2006-08-25 16:34 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1715 | 2006-08-09 | 2006 | TYRONZA | POINSETT | AR | 72386 | 43 | 2262+75 | +35.47817 | -90.35478 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72777 | 39240.0961 | 70561.8683 | 26777 | 10667.2602 | 46000 | 59894.6081 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 807295 | 2006-08-09 | 600 | 680 | NO | NO | NO | YES | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 4.5 | 0.24 | GRADE B | 35000 | ERW | NA | UNKNOWN |  | UNDER GROUND |  | 6 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GOVERNMENT | ROAD WORK |  | NO |  |  |  |  | NO | [40 empty] | CONTRACTOR WORKING FOR THE ARKANSAS HWY DEPT WAS REMOVING PREVIOUSLY STORED DIRT IN A FIELD OVER THE PIPELINE FROM A HWY RE-ROUTE. THEY KNEW THE PIPELINE WAS IN THE AREA DUE TO IT BEING MARKED IN MARCH, 2005 FOR THE ORIGINAL WORK. THEY FAILED TO SUBMIT A NEW ONE-CALL FOR THE WORK IN 2006 SO THE LINE WAS NOT RE-FLAGGED FOR THE EXCAVATION ACTIVITIES. THERE WERE PERMANT MARKERS AT THE EDGE OF THE FIELD IN THE FENCE ROW, BUT NOT VERY VISIBLE FROM THE WORK AREA. CONTRACTOR WAS USING A ROAD GRATER WITH A FRONT END RIPPER. IT WAS THE RIPPER THAT PUNCTURED A 1 INCH HOLE IN THE LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060110 | 2006-08-30 08:53 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1100 | 2006-08-02 | 2006 |  | ROWAN | KY |  | 30.34 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237500 | 109084.8308 | 95517.5039 | 236500 | 94215.4472 | 1000 | 1302.0567 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 806438 | 2006-08-02 | 835 | 935 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 30 | 0.38 | API5L | 52000 | SAW |  | NATIONAL TUBE | 1954 | OPEN DITCH |  |  | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | YES | 8 | 23 | 1972 | WATER |  | 24 | 1363 | [12 empty] | WHILE UNCOVERING THE PIPE FOR A RECOAT JOB, A PINHOLE LEAK WAS DISCOVERED IN THE LONG SEAM OF THE PIPE. LEAK WAS REPAIRED BY REPLACING PIPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060111 | 2006-08-30 09:07 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1802 | 2006-08-25 | 2006 | CORINTH | ALCORN | MS | 388349664 | CORINTH COMPRESSOR STATIO |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | ESD OF STATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197000 | 90377.4681 | 78479.6748 | 197000 | 78479.6748 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 40 | 809201 | 2006-08-25 | 857 | 1008 | NO | YES | NO | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | OTHER | VALVE | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1987 | [5 empty] | 24 | ROCKWELL INTERNAITIONAL | 1987 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FAULTY HEAT SENSOR ACTIVATED ESD. IN ADDITION, FIRE GATE DID NOT PROPERLY CLOSE. |  | A FAULTY HEAT SENSOR IN THE ENGINE ROOM ACTIVATED THE ESD FOR THE ENGINE BLOCK. A FIRE GATE DID NOT PROPERLY CLOSE. VALVE CONTINUED TO BLOW GAS UNTIL FIRST RESPONDER MANUALLY CLOSED VALVE. VALVE HAS BEEN CLEANED AND REPAIRED, AND RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060114 | 2006-08-31 17:08 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1430 | 2006-08-07 | 2006 |  |  | LA |  | MP 524C-401 +6.00 |  | 29* 01' 01 | -90*09'03 | OFFSHORE |  | SOUTH TIMBALIER | 23 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469100 | 268527.7822 | 565610.6614 | 50000 | 19918.6992 | 419100 | 545691.9622 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 807000 | 2006-08-07 | 900 | 980 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | NEAR A SUB-SEA ASSEMBLY | STEEL |  | NO | NO | NO | PIPELINE |  | 1994 | 16 | 0.41 | API | 42000 |  |  |  | 1961 | UNDER WATER |  | 72 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | IN BETWEEN 2-IN. VALVE AND A TEE | [8 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | NO | [19 empty] | LEAK OCCURRED IN CONNECTION BETWEEN A 2-INCH VALVE AND A TEE IN A SUB-SEA ASSEMBLY. THE LEAK WAS LOCATED ON TGP LINE NO. 524C-400 IN SOUTH TIMBALIER BLOCK 23.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060115 | 2006-09-05 09:56 | SUPPLEMENTAL FINAL | 31130 |  | DUKE ENERGY FIELD SERVICES (EASTRANS LIMITED PARTNERSHIP) | 370 17TH STREET, SUITE 2500 | DENVER | DENVER | CO | 80202 | 1555 | 2006-08-05 | 2006 | KILGORE | RUSK | TX | 75662 |  |  | 32 18 8.951 N | 94 47 53.536 W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120996 | 63142.5993 | 102422.6214 | 60996 | 24299.2195 | 60000 | 78123.4019 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 35 | 806802 | 2006-08-05 | 900 | 1264 | NO | YES | NO | NO | NO | NO | CINDY LOPEZ | 3615848518 | CALOPEZ@DUKE-ENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.25 | X-60 | 60000 | ERW | NA |  |  | UNDER GROUND |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1989 | NO | [57 empty] | LANDOWNER DISCOVERED LEAK AND CALLED OPERATOR. OPERATOR SHUT DOWN AND ISOLATED LINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060116 | 2006-09-08 09:03 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC. | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 930 | 2006-08-20 | 2006 | BENEZETTE | ELK | PA | 15821 |  |  | 41.293812 | -78.168823 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK - CRACKED PIPE NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82330 | 38194.0951 | 35807.3935 | 79000 | 31471.5447 | 3330 | 4335.8488 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 1 | 808521 | 2006-08-21 | 738 | 1000 | NO | YES | NO | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN_A_MILLER@DOM.COM | TRANSMISSION | OTHER | PIPE NIPPLE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 0.5 | 0.15 |  | 35000 |  |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | CONTRACT MOWER WAS MOWING AROUND THE ARDELL GATE SETTING (GATE 44) WITH A ZERO TURN MOWER. HIT 1/2" VALVE LOCATED ON 10" BYPASS RISER, CAUSING NIPPLE TO CRACK AND RELEASE GAS. CONTRACTOR IMMEDIATELY SHUTOFF MOWER AND WENT TO STATION TO NOTIFY OPERATOR. OPERATOR NOTIFIED SUPERVISOR THAT VALVE WAS BELOW BYPASS VALVE (44 B) AND COULD NOT BE ISOLATED WITHOUT BLOWING DOWN A SEGMENT OF LN-50. NOTIFIED GAS CONTROL AND CALLED OUT EMPLOYEES TO MAKE REPAIRS. WE WERE ABLE TO ISOLATE LN-50 AND USE FINNEFROCK TO PULL PRESSURE DOWN TO 542 PSI BEFORE VENTING TO ATMOSPHERE. THE 1/2" VALVE & NIPPLE WERE REPLACED AND THE LINE WAS PURGED , LOADED AND PUT BACK IN SERVICE AT 6:00PM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060117 | 2006-09-12 08:53 | ORIGINAL | 17620 |  | ROCKY MOUNTAIN NATURAL GAS COMPANY | 500 DALLAS ST. SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1015 | 2006-08-21 | 2006 | GLENWOOD SPRINGS | GARFIELD | CO | 81601 |  | 18+86 | 107 16.71 | 39 28.385 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | PUNCTURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 46378.1324 | 72000.9671 | 50000 | 19918.6992 | 40000 | 52082.2679 | 0 | 0 | NO | NO | NO | YES | 0 | THREAT TO THE PUBLIC | 4 | 15 | 808573 | 2006-08-21 | 800 | 1200 | NO | YES | NO | NO | NO | NO | BILL STEPHENS | 3039144877 | BILL_STEPHENS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 12 | 0.31 | X-52 | 2545 | ELECTRIC RESISTANCE WELD |  | NEWPORT STEEL | 1994 | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | RETAINING POND | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | HOBBS EXCAVATING REMOVED COVER OVER THE TOP OF THE RIFLE TO AVON 12" IN THE AREA OF THE IRON BRIDGE SUBDIVISION. EXCAVATION WORK WAS PERFORMED WITH EARTH MOVING EQUIPMENT (BELLY DUMP SCRAPERS). DURING EXCAVATION OVER THE PIPELINE, THE SCRAPER PUNCTURED THRU THE PIPE AND CREATED ~6"X3" TEAR WHICH ALLOWED GAS TO VENT TO ATMOSPHERE. AT APPROXIMATELY 10:15 AM MST A KMI RETAIL EMPLOYEE REPORTED A HIGH PRESSURE GAS RELEASE WEST OF THE ROARING FORK RIVER EAST OF THE GLENWOOD INTERCONNECT ON THE ROW FOR THE 12" MAINLINE. KMI RETAIL AND TRANSMISSION PERSONNEL WORKING WITH LKW GAS CONTROL DETERMINED THE DAMAGE WAS ON THE 12" AND MOBILIZED TO THE GLENWOOD SPRINGS INTERCONNECT AND SUBSTATION MAINLINE BLOCK VALVE TO ISOLATE THE AFFECTED SEGMENT. THE SEGMENT WAS ISOLATED (~5 MILES OF PIPELINE) AT 11:10 AM MST AND ALLOWED TO BLOW DOWN THRU THE PUNCTURE. COUNTY ROADS 109 (WEST SIDE), AND 154 (EAST SIDE) WERE CLOSED. RESIDENTIAL AND COMMERCIAL BUILDINGS WERE EVACUATED (50-100 PEOPLE) IN THE IMMEDIATE AREA DUE TO THE NATURAL GAS PLUME. EMERGENCY RESPONSE SUPPORT WAS PROVIDED BY THE CARBONDALE FIRE DEPARTMENT, COUNTY SHERIFF, AND STATE PATROL. THE AREA WAS DETERMINED TO BE SAFE AT APPROXIMATELY 2:30 PM, ROADS OPENED AND THE EVACUATION LIFTED. AFTER COMPLETING REPAIRS TO AN ADJACENT 4" RETAIL PE LINE THE TRANSMISSION PIPE WAS REPAIRED (7' REPLACED) AND RETURNED TO SERVICE ~7:45 PM. NO FIRE OR PERSONAL INJURIES AS A RESULT OF THE INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060118 | 2006-09-15 16:57 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1630 | 2006-08-21 | 2006 |  | OWYHEE | ID | 83624 | 30.5 |  |  |  | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 131848.249 | 292962.7571 | 0 | 0 | 225000 | 292962.7571 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 808635 | 2006-08-21 | 705 | 910 | NO | NO | YES | NO | NO | NO | JARED ELLSWORTH, P.E., MANAGER - PIPELINE SAFETY | 8015846539 | JARED.ELLSWORTH@WILLIAMS.COM | TRANSMISSION | OTHER | FACTORY GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 16 | 0.23 | API 5L | 46000 | ERW | N/A | KAISER | 1962 | ABOVE GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | MATERIAL DEFECT |  | NO | YES | 12 | 5 | 1962 | NATURAL GAS |  | 1 | 1055 | [12 empty] | DURING FI LEAK SURVEY POTENTIAL LEAK WAS DISCOVERED. LEAK WAS VERIFIED BY FIELD PERSONNEL AT 4:30. REPAIR HAS BEEN COMPLETED. PINHOLE IN FACTORY GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060119 | 2006-09-15 17:52 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1420 | 2006-08-21 | 2006 |  | OWYHEE | ID | 83624 | 31.5 |  |  |  | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 131848.249 | 292962.7571 | 0 | 0 | 225000 | 292962.7571 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 808617 | 2006-08-21 | 705 | 910 | NO | NO | YES | NO | NO | NO | JARED ELLSWORTH, P.E., MANAGER - PIPELINE SAFETY | 8015846539 | JARED.ELLSWORTH@WILLIAMS.COM | TRANSMISSION | OTHER | FACTORY GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 16 | 0.23 | API 5L | 46000 | ERW | N/A | KAISER | 1962 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | MATERIAL DEFECT |  | NO | YES | 12 | 5 | 1962 | NATURAL GAS |  | 1 | 1055 | [12 empty] | DURING FI LEAK SURVEY POTENTIAL LEAK WAS DISCOVERED. LEAK WAS VERIFIED BY FIELD PERSONNEL AT 2:20. REPAIR HAS BEEN COMPLETED. LEAK OCCURRED IN FACTORY GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060120 | 2006-09-18 14:44 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1506 | 2006-09-18 | 2006 | ADDISON | SOMERSET | PA |  |  | 2959+04 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215100 | 107077.9254 | 145333.3031 | 149100 | 59397.561 | 66000 | 85935.7421 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 5 | 809997 | 2006-09-01 | 810 | 936 | NO | YES | NO | NO | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | UNDERSLUNG DRIP | 1981 | [8 empty] | UNDER GROUND |  | 108 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1981 | NO | [57 empty] | INTERNAL CORROSION WAS THE CAUSE OF THIS EVENT. CAUSE OF THE INTERNAL CORROSION WAS MIC. THE PIPE AND ASSOCIATED DRIP -- EXTERNALLY COATED BUT NOT INTERNALLY COATED. FINAL COST TO REPLACE THE DRIP PLUS GAS LOST- $215,100.00.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060121 | 2006-09-22 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC COMPANY | PO BOX 770000 | SAN FRANCISCO | SAN FRANCISCO | CA | -9-4177 | 1534 | 2006-08-19 | 2006 | MAD RIVER | TRINITY | CA | 95552 | 125 |  | N. 40.45537 | W 123.48936 | ONSHORE | 1 |  |  |  | NO | YES | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358000 | 196045.0928 | 368538.5648 | 108000 | 43024.3902 | 250000 | 325514.1745 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 13 | 808427 | 2006-08-19 | 615 | 819 | NO | NO | YES | NO | NO | NO | RICHARD ARITA; GAS CONSULTING ENGINEER | 9259744313 | RTA2@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.25 | API 5L | 46000 | ELECTRIC RESISTANCE WELDING (ERW) |  | KAISER STEEL AT FONTANA |  | UNDER GROUND |  | 36 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | METTALURGISTS AND GEOLOGISTS DETERMINED THAT EARTH MOVEMENT INDUCED A WRINKLE OR BUCKLING IN PIPE AND OVERSTRESSED PIPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060122 | 2006-09-26 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1704 | 2006-08-30 | 2006 |  | OWYHEE | ID | 83624 | 61.2 |  |  |  | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275000 | 161147.8599 | 358065.592 | 0 | 0 | 275000 | 358065.592 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 809775 | 2006-08-30 | 710 | 910 | NO | NO | YES | NO | NO | NO | JARED ELLSWORTH, P.E., MANAGER - PIPELINE SAFETY | 8015846539 | JARED.ELLSWORTH@WILLIAMS.COM | TRANSMISSION | OTHER | FACTORY GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 16 | 0.23 | API 5L | 46000 | ERW | N/A | KAISER | 1962 | ABOVE GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | MATERIAL DEFECT |  | NO | YES | 12 | 5 | 1962 | NATURAL GAS |  | 1 | 1055 | [12 empty] | DURING FI LEAK SURVEY POTENTIAL LEAK WAS DISCOVERED. LEAK WAS VERIFIED BY FIELD PERSONNEL AT 5:04. REPAIR HAS BEEN COMPLETED. PINHOLE LEAK WAS FOUND IN FACTORY GIRTH WELD.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060123 | 2006-10-02 | SUPPLEMENTAL FINAL | 14210 |  | OKLAHOMA NATURAL GAS COMPANY | 401 N. HARVEY AVENUE | OKLAHOMA CITY | OKLAHOMA | OH | 73102-3470 | 1005 | 2006-09-01 | 2006 | EDMOND | OKLAHOMA COUNTY | OK | 73083-2847 |  |  | 35.68 | -97.42 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305320 | 13544.861 | 23787.5629 | 10159 | 4047.0813 | 15161 | 19740.4816 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 6 | 809968 | 2006-09-01 | 375 | 500 | NO | YES | NO | NO | NO | NO | DWIGHT ELLIS | 4055566458 | DELLIS@ONG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 8 | 0.17 | API 5L | 42 | ERW |  | UNKNOWN |  | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 8 | 21 |  |  | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | SUPPLEMENTAL REPORT FILED DUE TO REEVALUATION OF DAMAGE COST.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060124 | 2006-10-03 13:17 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 630 | 2006-09-13 | 2006 | DELHI | MADISON | LA |  | 3.3 |  | 32.4570910 | 91.4652240 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247900 | 143359.1206 | 309224.6148 | 15000 | 5975.6098 | 232900 | 303249.005 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 15 | 811256 | 2006-09-13 | 863 | 935 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 30 | 0.5 |  | 52000 | EFW |  | AOSMITH | 1953 | OTHER | INSIDE CASING |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | ATMOSPHERIC INSIDE OF CASING | YES | 1954 | NO | [57 empty] | SUPPLEMENTAL FACILITY PATROL NOTED GAS COMING FROM A CASING VENT. GAS SAMPLE TAKEN CONFIMRED PIPELINE GAS. LINE WAS ISOLATED AND REMOVED FROM SERVICE. REPAIRS STARTED ON 9/17. APPROXIMATELY 215' OF PIPE WAS REPLACE IN THE CASING. LINE RETURNED TO SERVICE ON 9/23.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060125 | 2006-10-10 | ORIGINAL FINAL | 13782 |  | NORTHERN STATES POWER COMPANY | 825 RICE STREET | ST PAUL | RAMSEY | MN | 55117 | 1041 | 2004-04-22 | 2004 | MAPLEWOOD | RAMSEY | MN | 55109 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 46622.925 | 100378.5989 | 4000 | 2063.1579 | 31000 | 42926.4602 | 40000 | 55388.9808 | NO | NO | NO | NO | 0 |  | 9 | 9 | 719600 | 2004-04-22 | 215 | 220 | NO | NO | YES | NO | NO | NO | DAN WOEHRLE | 6512292211 | DANIEL.J.WOEHRLE@XCELENERGY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 30 | 0.31 | API5LX-42 | 42000 |  |  | NATIONAL TUBE | 1957 | UNDER PAVEMENT |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GOVERNMENT | ROAD WORK |  | YES | 4 | 20 | 2004 | ONE-CALL SYSTEM | NO | [40 empty] | A MINNESOTA D.O.T. SOIL DENSITY SURVEY TRUCK DRILLED THROUGH THE 30" 220 PSIG LINE WHILE CONDUCTING SOIL DENSITY TESTING. EMERGENCY RESPONDERS CONRDONED OFF THE AREA UNTIL THE PIPELINE COULD BE VALVED OUT OF SERVICE AND BLOWN DOWN TO ATMOSPHERE. THE SURVEY TRUCK WAS REMOVED AND REPAIRS WERE MADE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20060126 | 2006-10-11 09:41 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1030 | 2006-09-29 | 2006 | MOUND VALLEY | LABETTE | KS | 66056 | 19 | SERIES 110, STA. 100817 | 37.146756837 | -95.40314942 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 6 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 397000 | 220298.2461 | 429259.2859 | 97000 | 38642.2764 | 180000 | 234370.2057 | 120000 | 156246.8038 | NO | NO | YES | YES | 10 | PRECAUTIONARY | 1 | 49 | 813103 | 2006-09-29 | 670 | 720 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 20 | 0.25 | API-5L | 42000 | ERW |  | YOUNGSTOWN | 1948 | UNDER GROUND |  | 40 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | NON-SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) CONTRACTOR EXCAVATING WITHOUT ONE CALL NOTIFICATION HIT THE SSCGP 20 INCH GAS PIPELINE WITH A ROCK TRENCHER CAUSING A RUPTURE AND GAS IGNITION. THE PIPELINE WAS PROPERLY MARKED WITH PIPELINE MARKERS PER PHMSA REGULATIONS BUT WAS NOT FLAGGED FOR CONSTRUCTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060127 | 2006-10-11 17:30 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1935 | 2006-09-16 | 2006 |  |  | LA |  | 527A-301A+16.52 |  | 29* 04 | 89*35'55 | OFFSHORE |  | WEST DELTA | 47 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 128667.6654 | 270370.6892 | 25000 | 9959.3496 | 200000 | 260411.3396 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 811686 | 2006-09-16 | 1100 | 1264 | NO | NO | YES | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 30 | 0.5 | API | 60000 |  |  | US STEEL | 1981 | UNDER WATER |  | 120 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1981 | NO | [57 empty] | DIVERS CONFIRMED A PINHOLE LEAK ON THE 30-IN. TGP LINE NO. 527A-300, IN WEST DELTA BLOCK 47, GULF OF MEXICO. LEAK OCCURRED IN A FIELD JOINT AT THE APPROX. 7:00 O'CLOCK PIPE POSITION. A CLAMP WAS INSTALLED TO EFFECT REPAIR AND THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060128 | 2006-10-12 | ORIGINAL FINAL | 19730 |  | TRUNKLINE GAS COMPANY, LLC | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1654 | 2006-09-05 | 2006 | [6 empty] | 28 38' 32" | 90 30' 22" | OFFSHORE |  | SOUTH TIMBALIER | #140 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209900 | 122376.3721 | 268873.6556 | 4900 | 1952.0325 | 205000 | 266921.6231 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 19 | 810413 | 2006-09-05 | 1021 | 1200 | YES | NO | NO | NO | NO | NO | BRIAN JIMENEZ, ASSOCIATE ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 2 | 0.22 | API 5L | 35000 | SMLS |  |  |  | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | DIVE BOAT WORKING ON SUB SEA ASSEMBLY PULLED ANCHOR INTO 10 INCH PIPELINE. WHEN THE ANCHOR WAS RELEASED, THE CABLE MADE CONTACT WITH THE PIPE AND WRAPPED AROUND A 2 INCH VALVE, WHICH CAUSED THE CIRCUMFERENTIAL SEPARATION WHEN THE CABLE WAS REELED IN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060129 | 2006-10-16 | SUPPLEMENTAL FINAL | 31531 |  | ONEOK WESTEX TRANSMISSION, L.P. | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103 | 1430 | 2006-08-29 | 2006 | MONAHANS | CRANE | TX |  | BLOCK B-26, SECTION 21 | LINE # 4100-003 | N31 31.214' | W102 35.772' | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 10 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381093 | 194085.0428 | 288562.8049 | 229773 | 91535.5854 | 151320 | 197027.2196 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 809626 | 2006-08-29 | 650 | 960 | NO | YES | NO | NO | NO | NO | KATHLEEN KELLY | 9185887871 | KAKELLY@ONEOK.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.25 | X-56 | 1400 | ERW |  |  |  | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | A THIRD PARTY CONTRACTOR WAS EXCAVATING A TRENCH WITH A LINK BELT 330 TRACK HOE OVER THE ONEOK WESTEX(OWT) 20-INCH PIPELINE RIGHT-OF-WAY IN PREPARATION FOR THE INSTALLATION OF ANOTHER OPERATOR'S 4 1/2 INCH STEEL NATURAL GAS PIPELINE . THE TRACK HOE STRUCK THE OWT 20-INCH PIPELINE, PUNCTURING THE WALL OF THE PIPE, CAUSING THE LINE TO RUPTURE. THE RUPTURE DID NOT RESULT IN ANY FIRE AND THE TRACK HOE OPERATOR SUSTAINED ONLY MINOR INJURIES. OWT DID NOT RECEIVE ADVANCE NOTICE OF THE PLANNED EXCAVATION AND DID NOT RECEIVE A DIG-TESS NOTICE (TEXAS ONE-CALL SYSTEM). THE OWT PIPELINE WAS CLEARLY MARKED WITH PERMANENT PIPELINE MARKERS VISIBLE UPSTREAM AND DOWNSTREAM OF THE RUPTURE SITE. 1APR10 - REVISED COST OF INCIDENT, ADDED ESTIMATED RUPTURE LONGITUDINAL LENGTH, FINALIZED REPORT. PATTI FORD, ONEOK PARTNERS, SR. PIPELINE SAFETY ENGINEER, (918) 588-7131, PATTI.FORD@ONEOK.COM
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060130 | 2006-10-16 14:03 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1000 | 2006-10-12 | 2006 | BUFFALO | WRIGHT | MN | 55313 | 21.1 |  | 45.18027 | -93.84917 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | 2 INCH BYPASS HOSE REACHED CRITICAL FLOW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 292996.1089 | 651028.3491 | 0 | 0 | 0 | 0 | 500000 | 651028.3491 | NO | NO | NO | NO | 0 |  | 0 | 0 | 814469 | 2006-10-12 | 50 | 125 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | 2 INCH BYPASS HOSE REACHED CRITICAL FLOW | STEEL |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | OTHER | BUFFALO, MN TOWN BORDER STATION #1 |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | NORTHERN NATURAL GAS HAD INSTALLED A 2 INCH BYPASS HOSE AT THE BUFFALO, MN # 1 TBS TO ENABLE CENTERPOINT ENERGY TO BE ABLE TO COMPLETE MODIFICATIONS/UPGRADING ON THEIR FACILITIES. COLD WEATHER RESULTED IN GAS CONSUMPTION INCREASING AND THE 2 INCH BYPASS HOSE REACHED CRITICAL FLOW AS IT WAS INSUFFICENT IN SIZE AND CAPACITY TO SUPPLY THE REQUIRED PRESSURES AND FLOWS. GAS CONSUMPTION BY END USERS PULLED THE UTILITIES PRESSURES DOWN TO A POINT THAT DUE TO CONCERN OF POTENTIALLY PULLING AIR INTO THEIR DISTRIBUTION SYSTEM, CENTERPOINT ENERGY CLOSED THEIR VALVE TO THE CITIES DISTRIBUTION SYSTEM. APPROXIMATELY 5,500 METER SETTINGS, WITHIN THE CITY HAD TO BE PURGED AND RELIT. SUPPLEMENTAL/FINAL REPORT: THE CAUSE OF THE OUTAGE WAS HUMAN ERROR ON THE PART OF NORTHERN NATURAL GAS COMPANY PERSONNEL, RESULTING IN INADEQUATE TEMPORARY FACILITIES BEING INSTALLED TO FACILITATE ROUTINE MAINTENANCE ON THE TOWN BORDER STATION THAT SERVES AS THE NATURAL GAS TRANSFER POINT FROM NORTHERN NATURAL GAS COMPANY TO CENTERPOINT ENERGY. THERE WAS NO RELEASE OF GAS TO ATMOSPHERE, NO PUBLIC OR PRIVATE PROPERTY DAMAGE. ESTIMATED COST INCURRED WAS RELATED TO THE ACTIONS AND ACTIVIITES REQUIRED IN RE-ESTABLISHING GAS SERVICE AND RELIGHTING OF THE APPROXIMATE 5,500 METER SETTINGS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060132 | 2006-10-27 | ORIGINAL | 19235 |  | TEXAS EASTERN TRANSMISSION, LP | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | -7-7056 | 1200 | 2006-09-30 | 2006 |  |  | LA |  | 11.38 (40-B-3-B) |  | 29.3692 | 88.4670 | OFFSHORE |  | MAIN PASS | 93 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255000 | 148791.8988 | 327506.0445 | 5000 | 1991.8699 | 250000 | 325514.1745 | 0 | 0 | NO | NO | NO | NO | 0 |  | 45 |  | 813217 | 2006-09-30 | 972 | 1440 | NO | YES | NO | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@DUKE-ENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 12 | 0.5 | ANSI 900 RTJ | 42000 | NA (SWIVEL FLANGE) |  | TUBE TURN (SWIVEL FLANGE) | 1983 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | SWIVEL FLANGE | [10 empty] | NO | YES | 5 | 18 | 1983 | WATER |  | 12 | 2175 | [12 empty] | FLANGE BOLTS IN A SUBSEA SWIVEL FLANGE SEPARATED SLIGHTLY CAUSING A NATURAL GAS LEAK TO OCCUR. THE BUBBLES AT THE SRUFACE CAUSED BY THE LEAK WERE DISCOVERED BY COMPANY PERSONNEL IN A HELICOPTER. THE BOLTS WERE REPLACED AND TORQUED TO 1645 FT-LBS ELIMINATING THE LEAK.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060133 | 2006-10-31 | ORIGINAL FINAL | 31557 |  | CROSSTEX CCNG TRANSMISSION LTD. | 2501 CEDAR SPRINGS, SUITE 100 | DALLAS | DALLAS | TX | 75201 | 1245 | 2006-09-27 | 2006 | SOUTH OF CORPUS CHRISTI | NUECES | TX |  |  |  | 27.63603 | 97.51733 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7100 | 3448.094 | 4183.9794 | 5600 | 2230.8943 | 1500 | 1953.085 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 |  |  | 691 | 1050 | NO | NO | YES | NO | NO | NO | LEONARD STROMAN, CROSSTEX AREA SUPERINTENDENT | 3612994000 | LEONARD.STROMAN@CROSSTEXENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 8.63 | 0.26 | 22.6 |  |  |  |  | 1968 | UNDER GROUND |  | 32 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1968 | NO | [57 empty] | AT 1245 ON WEDNESDAY, SEPTEMBER 27, 2006, DURING A ROUTINE INSPECTION, A SMALL LEAK WAS DISCOVERED UPON SEEING GASEOUS BUBBLING FROM STANDING RAINWATER IN A FARMER'S FIELD. THE AFFECTED UNDERGROUND NATURAL GAS TRANSMISSION LINE WAS SHUT-IN BY 1315 WHILE PROPER NOTIFICATIONS TO THE CROSSTEX EH&S DEPARTMENT AND SUBSEQUENT NOTIFICATIONS TO BOTH THE STATE EMERGENCY RESPONSE COMMISSION (SERC)[INCIDENT NO. 20063278] AS WELL AS THE RAILROAD COMMISSION OF TEXAS (TRRC) PIPELINE SAFETY DIVISION [INCIDENT NO. 07-CA-061] WERE MADE AT 1331 AND 1325, RESPECTIVELY. UPON DISCOVERY AND INVESTIGATIO, THE CAUSE OF THE LEAK WAS DETERMINED TO BE INTERNAL CORROSION AS DESCRIBED IN SECTION F1 OF THIS FORM. MEASURES WERE TAKEN TO NOTIFY THE AFFECTED PROPERTY OWNER AND MAKE THEM AWARE OF THE INCIDENT WHILE INVESTIGATION, EXCAVATION, AND REPAIR OF THE LINE WERE MADE. THE AFFECTED AREA OF THE POPLEINE WAS ISOLATED, DEGASSED AND REPAIRED WITH A NEW SECTION OF PIPE. THIS INITIAL/FINAL REPORT IS BEING SUBMITTED IN ACCORDANCE WITH 16 TAC 8.210(A)(4)(A).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060134 | 2006-11-01 | SUPPLEMENTAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1148 | 2006-10-04 | 2006 | DECATUR | WISE | TX | 76234 |  | 1867 + 07 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626000 | 306908.9331 | 389452.9346 | 471000 | 187634.1463 | 150000 | 195308.5047 | 5000 | 6510.2835 | NO | NO | NO | YES | 19 | PRECAUTIONARY | 1 | 52 |  | 2006-10-04 | 701 | 800 | NO | YES | NO | NO | NO | NO | MICHAEL E. ARCHER - COMPLIANCE ANALYST | 2142062879 | MICHAEL.ARCHER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 24 | 0.34 | API 5LX | 42000 | DSAW |  |  | 1960 | UNDER GROUND |  | 18 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | AN ATMOS CONTRACTOR DAMAGED THE FACILITY AND BEFORE ATMOS WAS ADVISED, THE PIPE RUPTURED. UPDATED BY PHMSA ON 12/17/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060135 | 2006-11-06 19:07 | ORIGINAL FINAL | 12576 |  | MISSISSIPPI RIVER GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 750 | 2006-10-06 | 2006 | STE GENEVIEVE | STE. GENEVIEVE | MO | 63670 |  | 74+28 | 37.97490 | -90.07595 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100316 | 58744.1928 | 130331.556 | 316 | 125.8862 | 100000 | 130205.6698 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 813867 | 2006-10-06 | 270 | 290 | NO | NO | YES | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | 1" VALVE LEAKING AT THREADS ON A NIPPLE | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 1 |  |  |  |  | GATE VALVE | CRANE | 1960 | UNDER GROUND |  | 24 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | DURING EXCAVATION FOR AN ECDA DIG, THE CREW DISCOVERED A LEAK. UPON FURTHER INVESTIGATION IT APPEARED THAT THE THREADS ONA PIPE NIPPLE UNDER A 1¿ VALVE WERE CRACKED. AFTER WE WERE ABLE TO REMOVE THE GAS FROM THE PIPE, IT WAS DISCOVERED TO BE ONLY A LOOSE VALVE ON THE NIPPLE. THERE WAS A CABLE THAT HAD APPARENTLY BEEN USED TO ALIGNED UP THE PIPE ON INSTALLATION. THE CABLE WAS LEFT WRAPPED AROUND THE PIPE AND ALSO THE 1¿ NIPPLE AND VALVE. WHEN THE EXCAVATION WAS PERFORMED THE CREW APPARENTLY GRABBED THE CABLE AND BENT OVER THE NIPPLE, LOOSENING THE VALVE SCREWED INTO THE NIPPLE AND CREATED THE LEAK. LINE PRESSUE WAS LOWERED FROM 270 PSIG TO 110 PSIG. EMERGENCY RESPONSE ACTIONS WERE TAKEN. A STOPPLE JOB WAS PERFORMED, THE VALVE REMOVED, AND THE LINE WAS REPAIRED AND RETURNED TO NORMAL OPERATIONS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060136 | 2006-11-13 | SUPPLEMENTAL FINAL | 4900 |  | KINDER MORGAN TEJAS PIPELINE | 500 DALLAS STREET SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1800 | 2006-10-12 | 2006 |  | HARRIS | TX |  |  |  | 29.37.212 | 095.03.115 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50053 | 29310.6944 | 65029.9657 | 157 | 62.5447 | 49896 | 64967.421 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 81523 | 2006-10-12 | 601 | 1000 | YES | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | [7 empty] | UNDER GROUND |  | 120 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | ON OCTOBER 9, 2006, REPRESENTATIVES FROM KINDER MORGAN RESPONDED TO A REPORT OF A POTENTIAL LEAK IN A PIPELINE CORRIDOR WHICH CONTAINED THE KINDER MORGAN TEJAS BAYPORT LATERAL, AS WELL AS MULTIPLE OTHER OPERATORS' PIPELINES. KINDER MORGAN OPERATIONS PERSONNELL IMMEDIATELY MOBILIZED A HYDROEXCAVATION CONTRACTOR TO PROACTIVELY UNCOVER THE SOURCE OF THE SUSPECTED LEAK AND THEREBY DETERMINE THE ORIGIN OF SAID-SAME SUSPECTED LEAK. DUE TO THE PRESENCE OF SEVERAL OTHER PIPELINES WITHIN THE CORRIDOR AND THE UNUSUAL DEPTH OF THE PIPELINES WITHIN THE CORRIDOR, IT WAS NOT UNTIL OCTOBER 12, 2006 AT 6:00 P.M. THAT THE SOURCE OF THE POTENTIAL LEAK COULD BE DETERMINED AND THEREBY TRIGGER "DISCOVERY"/ BETWEEN OCTOBER 9TH AND OCTOBER 12TH THE BAYPORT #8 LATERAL REMAINED IN SERVICE AND CONTINUED TO PROVIDE GAS SERVICE TO OUR CUSTOMERS. AT THE POINT OF "DISCOVERY" ON OCTOBER 12TH AT APPROXIMATELY 6:00 P.M., KINDER MORGAN FIELD OPERATIONS PERSONNEL SHUT-IN AND BLEW DOWN THE BAYPORT 8" LATERAL WITH APPROXIMATELY 48 PSIG LEFT IN THE PIPELINE. WHEN THE PIPELINE WAS REMOVED FROM SERVICE ON OCTOBER 12TH AT 6:00 P.M. THE FIRST CRITERIA FOR REPORTING UNDER THE TEXAS ADMINISTRATIVE CODE TITLE 16, PART 1, CHAPTER 8, SUBCHAPTER C RULE SECTION 8.210 WAS MET AND THE TELEPHONIC REPORT WAS MADE ON OCTOBER 12TH AT APPROXIMATELY 6:55 P.M.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060137 | 2006-11-15 07:28 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC. | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1000 | 2006-10-16 | 2006 | WICHITA | SEDGWICK | KS | 67207 | 3 | SERIES 110 STA. 14276 | 37.67926665 | -97.17712658 | ONSHORE | 1 |  |  |  | NO | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 70319.0661 | 156246.8038 | 0 | 0 | 118000 | 153642.6904 | 2000 | 2604.1134 | NO | NO | NO | NO | 0 |  | 0 | 0 | 815073 | 2006-10-17 | 172 | 180 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 20 | 0.26 | API5L | 56000 | ERW |  |  |  | UNDER GROUND |  | 55 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | DISBONDED COATING IN AREA SHIELDED BY CASING | YES | 1971 | NO | [57 empty] | THIS SMALL LEAK WAS DISCOVERED DURING AN ANOMALY INVESTIGATION AFTER A SMART PIG RUN. THE GAS IN THE CASING WAS DISCOVERED USING A PRAGMATIC GAS DETECTION INSTRUMENT. THE COST TO REPLACE THE PIPE INSIDE THE CASING DROVE THE DECISION TO CALL THIS AN INCIDENT. THIS LEAK WAS DECLARED AN INCIDENT AS SOON AS WE DETERMINED THE COST WOULD REACH THE $50,000 THRESHOLD.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060138 | 2006-11-06 | ORIGINAL | 32113 |  | CROSSTEX NORTH TEXAS PIPELINE, L.P. | 2501 CEDAR SPRINGS, SUITE 100 | DALLAS | DALLAS | TX | 75201 | 2130 | 2006-10-06 | 2006 | BETWEEN PARIS & COOPER | LAMAR | TX |  |  |  | 33.51703N | 95.63733W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28023 | 13492.1969 | 15682.0477 | 23023 | 9171.7642 | 5000 | 6510.2835 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 |  |  | 1000 | 1100 | NO | YES | NO | NO | NO | NO | MICKEY KING - CROSSTEX AREA SUPERINTENDENT | 9184240335 | MICKEY.KING@CROSSTEXERERGY.COM | TRANSMISSION | OTHER | GASKET SEAL | PLASTIC |  | NO | YES | NO | OTHER | PIGGING RECEIVER FLANGE | 2006 | 24 |  | 600 SERIES | [5 empty] | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | MATERIAL DEFECT |  | NO | YES | 3 | 1 | 2006 | WATER |  | 8 | 1100 | [12 empty] | AT 2130 HOURS ON FRIDAY, OCTOBER 6. 2006, A PIPELINE OPERATOR WAS DISPATCHED TO THE NGPL SALES STATION TO INVESTIGATE A PRESSURE DROP ON THE LINE. AT THIS TIME, IT WAS DISCOVERED THAT THE GASKET FAILED ON THE PIPELINE FLANGE LOCATED BETWEEN THE COALESCER AND PIG RECEIVER ON THE 24-INCH PIPELINE, CAUSING THE PRESSURE DROP ON THE LINE (SEE SECTION F5 OF THIS FORM) TWENTY (20) FEET OF THE AFFECTED OPERATING CONDITION BY 0630 HOURS ON OCTOBER 7, 2006. THE PROPER NOTIFICATIONS OF THIS INCIDENT WERE MADE TO THE CROSSTEX EH&S DEPARTMENT AND SUBSEQUENT NOTIFICATIONS WERE MADE TO BOTH THE STATE EMERGENCY RESPONSE COMMISSION (SERC) {INCIDENT NO. 20063399} AS WELL AS THE RAILROAD COMMISSION OF TEXAS (TRRC) PIPELINE SAFETY DIVISION [INCIDENT NO. 07-CA-092} THIS INITIAL/FINAL REPORT IS BEING SUBMITTED IN ACCORDANCE WITH 16 TAC 8.210(A)(4)(A)
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060139 | 2006-11-14 | SUPPLEMENTAL FINAL | 2596 |  | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR | COLUMBUS | FRANKLIN | OH | 43215 | 2210 | 2006-10-10 | 2006 | COLUMBUS | FRANKLIN | OH | 43211 |  |  | 40.02 | -82.95 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64156 | 36449.9066 | 75401.6051 | 9000 | 3585.3659 | 20000 | 26041.134 | 35156 | 45775.1053 | NO | YES | NO | NO | 0 |  | 0 | 5 | 814299 | 2006-10-10 | 170 | 190 | NO | NO | YES | NO | NO | NO | ROB R. SMITH COMPLIANCE SPECIALIST | 6148182110 | RRSMITH@NISOURCE.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 18 | 0.38 | UNKNOWN |  | UNKNOWN | N/A | UNKNOWN |  | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | MECHANICAL JOINT | [6 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | NO | [19 empty] | COLUMBIA GAS OF OHIO INC. WAS RESTORING GAS PRESSURE TO A PARTIALLY REPLACED GAS DISTRIBUTION TRANSMISSION PIPELINE ON DENUNE AVE. IN COLUMBUS OHIO WHEN AN UNEXCAVATED MECHANICAL JOINT COUPLING SEPARATED. THE SEPARATION OF THE COUPLING CAUSED A RELEASE OF GAS THAT LIFTED A STREET PLATE AND DEBRIS INTO OVERHEAD POWERLINES THAT CAUSED AN ELECTRIC SERVICE DISRUPTION. THE DEBRIS ALSO CAUSED DAMAGE TO SEVERAL NEARBY HOMES AND VEHICLES. THE GAS WAS PROMPTLY SHUT DOWN AND THE SITUATION MADE SAFE. THE UNEXCAVATED MECHANICAL JOINT COUPLING THAT SEPARATED WAS LOCATED APPROXIMATELY 11 FEET OUTSIDE ON OF THE TIE-IN HOLES FOR THE PIPELINE REPLACEMENT. PLEASE NOTE: THIS INCIDENT DOES NOT MEET THE CRITERIA OF A "HIGH CONSEQUENCE AREA" BASED ON 49CFR PART 192 SUBPAR "O-PIPELINE INTEGRITY MANAGEMENT." COLUMBIA GAS OF OHIO INC. PROMPTLY REPLACED THE 18" BARE STEEL PIPE AND REPLACED IT WITH 1378 FEET OF NEW WELD TREATED STEEL MAIN. THE MATERIAL SPECIFICATIONS OF THE BARE STEEL MAINLINE THAT WAS REMOVED FROM SERVICE IS UNKNOWN AS REFERECED IN PART "D" OF THIS FORM
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060140 | 2006-11-16 11:03 | ORIGINAL FINAL | 20044 |  | PRAXAIR. INC. | 39 OLD RIDGEBURY RD | DANBURY | FAIRFIELD | CT | 06810 | 930 | 2006-10-20 | 2006 | PASADENA | HARRIS | TX | 77506 | LHR PARKING LOT VALVE STA | PACS ENG STA 761.4 | 29.7138 | -95.2265 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110000 | 61278.5604 | 120634.1689 | 25000 | 9959.3496 | 25000 | 32551.4175 | 60000 | 78123.4019 | YES | NO | YES | NO | 0 |  | 2 | 30 | 815459 | 2006-10-20 | 425 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. RYAN | 8154675412 | JIM_R_RYAN@PRAXAIR.COM | TRANSMISSION |  |  |  |  | NO | NO | NO | [11 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 3 |  |  | THE OPERATORS INVOLVED HAD BEGUN WORK TO PURGE A NEW 6" LINE INTO SERVICE, BY BRINGING H2 INTO THE 6" LINE FROM AN ADJACENT 8" LINE, WHICH WAS ALREADY IN SERVICE. THE REQUIRED PRE-WORK HAD BEEN COMPLETED, AND ONE OPERATOR WAS AT THE BELTWAY 8 AND HWY 225 VALVE STATION PREPARING TO SLOWLY LET H2 INTO THE LINE. THE SECOND OPERATOR WAS AT THE LHR PARKING LOT VALVE STATION VENT TO MONITOR PURGE GAS FLOW AND PURITY. THE SECOND OPERATOR MISTAKENLY THOUGHT THAT THE PURGE HAD STARTED, AND HE THOUGHT THAT THERE WAS INSUFFICIENT PURGE FLOW AT THE VENT. HE DECIDED TO OPEN THE ISOLATION VALVE TO THE PRESSURIZED 8" LINE AT HIS END. HE OPENED THE VALVE, CAUSING A HIGH-VOLUME FLOW OF HYDROGEN THROUGH THE ADJACENT VENT PIPE, WHICH IGNITED. THE SECOND OPERATOR RECEIVED BURNS TO HIS HANDS AND FACE. A COMPANY TRUCK WAS DESTROYED AND OTHER VEHICLES WERE DAMAGED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060141 | 2006-11-17 09:13 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1200 | 2006-10-18 | 2006 | [6 empty] | 29.08703 | 091.69764 | OFFSHORE |  | EUGENE ISLAND | 95-F |  | YES | NO | INTERSTATE | OTHER | WELD FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 351595.3307 | 781234.0189 | 0 | 0 | 600000 | 781234.0189 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 815240 | 2006-10-18 | 915 | 1440 | NO | YES | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@GULFSOUTHPL..COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2006 | 10 | 0.5 |  | 42000 |  |  |  |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | WELD FAILED FROM EXCESSIVE STRESS |  | PRODUCER AT THE EUGENE ISLAND 95-F PLATFORM REPORTED BUBBLING NEAR THE PLATFORM. ALL AFFECTED PRODUCERS WERE CONTACTED AND ASKED TO SHUT-IN AND CONTACTED SEVERAL REPAIR CONTRACTORS FOR VESSEL AND CREW AVAILABILITY. ONCE ON LOCATION A CRACKED WELD, CAUSED BY EXCESSIVE STRESS, WAS FOUND ON PREVIOUSLY DAMAGED/REPAIRED SUB SEA TIE-IN PIPING. SUBSEA ASSEMBLY WAS REPLACED AND ADDITIONAL BRACING WAS INSTALLED TO PREVENT REOCCURRENCE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060142 | 2006-11-17 14:25 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1030 | 2006-10-29 | 2006 |  |  | LA |  |  |  | 28 22.615 | 91 39.688 | OFFSHORE |  | EUGENE ISLAND | 286 | LA | NO | NO | INTERSTATE | OTHER | VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 131848.249 | 292962.7571 | 0 | 0 | 225000 | 292962.7571 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 816429 | 2006-10-29 | 1100 | 1250 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | [5 empty] | 16" BALL VALVE | CAMERON |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | GREASE ZERK ON 16" BALL VALVE SHEARED OFF |  | GREASE ZERK ON 16" BALL VALVE SHEARED OFF. GAS SLOWLY LEAKING FROM ZERK. GREASE ZERK WAS REPAIRED ON 11/02/06
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060143 | 2006-11-17 14:46 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1510 | 2006-10-29 | 2006 |  |  | LA |  |  |  | 29.0520 | 92.2080 | OFFSHORE |  | VERMILLION | 116 | LA | NO | NO | INTERSTATE | OTHER | VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 585992.2179 | 1302056.6982 | 0 | 0 | 1000000 | 1302056.6982 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 816445 | 2006-10-29 | 850 | 1253 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | [5 empty] | 16" BALL VALVE |  |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | BODY BLEED VALVE ON 12" GROVE VALVE SHEARED OFF BY UNKNOWN FORCES |  | BODY BLEED VALVE ON 12" GROVE VALVE SHEARED OFF BY UNKNOWN FORCES. REPAIR ACCOMPLISHED BY INSTALLING NIPPLE AND NEW VALVE. REPAIR COMPLETED ON 11/13/06.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060144 | 2006-11-28 13:20 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO. OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1540 | 2006-11-15 | 2006 | SAYRE | BECKHAM | OK | 73662 | OK EXTENSION MP 100 | RECHAIN #13,030+69 | 3523.236 | 9953.126 | ONSHORE |  |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87071 | 39988.975 | 34995.8806 | 86729 | 34550.5772 | 242 | 315.0977 | 100 | 130.2057 | NO | NO | NO | NO | 0 |  |  | 45 | 818312 | 2006-11-15 | 492 | 720 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 | 0.25 | 5LX52 | 52000 | ERW |  | AO SMITH | 1957 | UNDER GROUND |  | 52 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | HF ERW |  | MATERIAL DEFECT |  | NO | NO | [19 empty] | SEAM PENATRATOR CAUSED BY CORROSION IN THE LONG SEAM OF THE PIPE. LEAK WAS DISCOVERED BY INVESTIGATION OF DEAD VEGETATION DURING ROUTINE CONTINUING SURVEILANCE ACTIVITIES. LINE WAS BLOWN DOWN AND SECTION OF PIPE WAS REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060145 | 2006-12-01 11:45 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 801 | 2006-11-03 | 2006 | NORPHLET | UNION | AR | 71730 |  | 16550 | 33.33861 | -92.65310 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31632 | 18381.5295 | 40088.683 | 1215 | 484.0244 | 30417 | 39604.6586 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 816983 | 2006-11-03 | 170 | 250 | NO | NO | YES | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1928 | 8 | 0.28 | UNKNOWN | 24000 | UNKNOWN | UNKNOWN | UNKNOWN | 1928 | UNDER GROUND |  | 4 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | OTHER | CLEARING WELL SITE | NO |  |  |  |  | YES |  | YES | [38 empty] | ON NOV. 3, AT 8:01 AM CEGT SYSTEM CONTROL OFFICE WAS NOTIFIED OF A POSSIBLE PIPELINE RUPTURE. THE LOCATION WAS OFF OF GAS PLANT ROAD IN NORPHLET, AR. THE CALL WAS MADE BY A FIELD SUPERINTENDENT FOR TRI-STATE DRILLING COMPANY. CEGT FIELD PERSONNEL WERE DISPATCHED TO THE SCENE AND UPON ARRIVAL FOUND A BULLDOZER HAD HIT THE PIPELINE [HM-1] AND THERE WAS A 2X6 INCH GOUGE IN THE PIPELINE. THE ENTIRE PIPELINE HAD BLOWN FLAT ALONG WITH 7 LATERAL LINES WHICH AFFECTED 583 CUSTOMERS. THE LINE WAS REPAIRED AND SERVICE RESTORED BY 4 PM, THAT AFTERNOON. THERE WAS NOT A ONE-CALL MADE ON THIS LOCATION BY THE DRILLING COMPANY, NOR THE DOZER OPERATOR. THERE WAS A CARSONITE PIPELINE MARKER VISIBLE 120 FOOT FROM THE INCIDENT. WHILE THIS INCIDENT DID NOT MEET THE GENERAL DEFINITION OF AN INCIDENT, IT WAS REPORTED BECAUSE IN THE JUDGMENT OF THE OPERATOR IT WAS CONSIDER SIGNIFICANT DUE TO AFFECTING 583 CUSTOMERS.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20060146 | 2006-12-01 12:31 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE GAS | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 930 | 2006-11-11 | 2006 | BORIE | LARAMIE | WY |  | MP 12 -30+58 |  | 41* 1' 1 | -105* 0' 1 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | YES | NO | 0 |  | 1 | 20 | 817882 | 2006-11-11 | 788 | 1000 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | OTHER | UNKNOWN | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 36 | 0.36 | API | 70000 | DSAW |  | VALOUREC | 1982 | UNDER GROUND |  | 26 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 10 | 11 | 2006 | ONE-CALL SYSTEM | YES |  | YES | ACCURATE | [37 empty] | THE WIC 124A PIPELINE (OPERATED BY COLORADO INTERSTATE GAS PIPELINE), NEAR CHEYENNE, WY RUPTURED FOLLOWING APPARENT THIRD-PARTY DAMAGE BY AN EXCAVATION CONTRACTOR WORKING FOR KINDER MORGAN ON THE ROCKIES EXPRESS PROJECT. THERE WAS A FIRE AND EXPLOSION, AND ONE FATALITY RESULTED FOLLOWING THE INCIDENT. ** AFTER EXCAVATION BY KINDER MORGAN CONTRACTOR AND SUBSEQUENT RUPTURE, PIPELINE COVER WAS MEASURED AT 26.40 INCHES. AFTER COMPLETING THE INTERNAL INVESTIGATION, IT WAS DETERMINED THAT THIS INCIDENT WAS CAUSED BY A CONFLUENCE OF EVENTS BY A VARIETY OF ACTIONS, AND MORE SPECIFICALLY THAT: 1. CONSTRUCTIONG PARTY DID NOT LOCATE AND MARK THE LOCATION OF WIC'S PIPELINE PRIOR TO STARTING CONSTRUCTION AS REQUIRED BY ITS FERC CERTIFICATE OF PUBLIC CONVENIENCE AND NECESSITY. 2. SURVEY COMPANIES DID NOT PHYSICALLY LOCATE NEARBY EXISTING UNDERGROUND FACILITIES, INCLUDING THE WIC PIPELINE, WHEN CREATING SURVEYS USED IN THE REX PROJECT. WHEN STAKING THE EDGE OF REX'S TEMPORARY CONSTRUCTION RIGHT-OF-WAY, SURVEY COMPANIES REPEATEDLY PLACED STAKES NEAR, ON AND TO THE NORTH OF THE WIC PIPELINE. THE CONSTRUCTION INSPECTION COMPANY DID NOT DETECT AND/OR CORRECT THE DEFICIENCIES IN THE SURVEY OR THE STAKING OF THE RIGHT-OF-WAY. 3. CONSTRUCTION CONTRACTOR DID NOT PHYSICALLY LOCATE OR MARK EXISTING UNDERGROUND FACILITIES, INCLUDING THE WIC PIPELINE, WHEN THOSE FACILITIES WERE PARALLEL TO THE NEW PIPELINE BEING CONSTRUCTED (REX) NOR DID CONSTRUCTION USE POTHOLING TO DISCOVER THE LOCATION OF THE PARALLEL WIC PIPELINE ONCE THE ENCROACHMENTS BY THE REX TEMPORARY CONSTRUCTION RIGHT-OF-WAY HAD BEGUN TO OCCUR. CONSTRUCTION CONTRACTOR DID NOT UNDERTAKE EFFORTS PRIOR TO INVESTIGATE THE NATURE OF THE HARD SUBSURFACE MATERIAL ENCOUNTERED IN THE AREA OF THE RUPTURE. 4. DECEASED EMPLOYEE OF CONSTRUCTION CONTRACTOR WAS PROBABLY UNAWARE OF THE LOCATION OF THE WIC PIPELINE WHILE USING THE BULLDOZER TO RIP THE GROUND BETWEEN THE WESTERN AND EASTERN PERMANENT WIC PIPELINE MARKERS OF THE RUPTURE SITE. 5. EMPLOYEE OF CONTRACTOR HIRED TO LOCATE, AND WHEN NECESSARY FLAG THE LOCATION OF THE WIC PIPELINE DID NOT FLAG THE LOCATION OF THE PIPELINE BETWEEN THE WESTERN AND EASTERN PERMANENT WIC PIPELINE MARKERS NEAR THE RUPTURE SITE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060148 | 2006-12-06 13:26 | ORIGINAL FINAL | 1734 |  | BRIDGELINE GAS DISTRIBUTION LLC | 4800 FOURNACE PLACE | BELLAIRE | HARRIS | TX | 77401-2324 | 1527 | 2006-11-15 | 2006 | RESERVE | ST. JOHN THE BAPTIST | LA | 70068 | MILE POST 16.5 | 874+00 | N 3005.800 | W 9035.500 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90000 | 51467.0662 | 108148.2757 | 10000 | 3983.7398 | 80000 | 104164.5359 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 817308 | 2006-11-15 | 700 | 1000 | NO | YES | NO | NO | NO | NO | HENRY L. LEGER | 3376548915 | HENRYLEGER@CHEVRON.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 20 | 0.34 | API 5LX | 52000 | ERW | N/A | UNKNOWN | 1962 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | LF ERW |  | MATERIAL DEFECT |  | NO | YES | 12 | 10 | 1962 | WATER |  | 24 | 1250 | [12 empty] | THE CAUSE OF THE SUBJECT INCIDENT WAS DUE TO A SEAM FAILURE IN A JOINT OF 20-INCH PIPE LOCATED AT MILE POST 16.5 ON BRIDGELINE GAS DISTRIBUTION LLC'S RIVERLANDS NATURAL GAS PIPELINE SYSTEM. THE SUBJECT PIPELINE WAS INSTALLED IN CY 1962 AND WAS CONSTRUCTED WITH ERW PIPE. THE SEAM FAILURE WAS BARELY VISIBLE TO THE NAKED EYE. THE LEAK WAS CLASSIFIED AS A PINHOLE LEAK. THE LEAK WAS REPAIRED PER CODE ON 11/15/06 VIA WELDING A FULL ENCIRCLEMENT SPLIT SLEEVE AROUND THE LEAK AREA. PLEASE NOTE THAT ON 11/6/06 AT 1300HRS A CALL WAS MADE TO THE NRC (REPORT NO. 817308) REPORTING THE SUBJECT LEAK AS AN UNKNOWN. ON 11/15/06 IT WAS DETERMINED THAT THE LEAK WAS ON THE SUBJECT PIPELINE AND A SUBSEQUENT CALL WAS MADE TO THE NRC AT 1527HRS REPORTING IT. THE NRC PUT THE SUBSEQUENT INFORMATION ON THE SAME REPORT (REPORT NO. 817308)WITH A REFERENCE NOTE INCLUDED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060149 | 2006-12-07 15:52 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC. | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302- | 1344 | 2006-11-09 | 2006 | JANE LEW | LEWIS | WV | 26378 | SNYDER JCT. |  |  |  | ONSHORE |  |  |  |  | NO | NO | INTERSTATE | OTHER | BREAK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 20004.6584 | 27682.8346 | 27000 | 10756.0976 | 13000 | 16926.7371 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 31 | 817690 | 2006-11-09 | 904 | 944 | YES | NO | NO | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN_A_MILLER@DOM.COM | TRANSMISSION | OTHER | DRIP SYPHON | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 1 | 0.18 |  | 35000 |  |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | DISPATCHER PAGED SUPERVISOR AT 1:44 PM ON NOVEMBER 9, 2006 TO REPORT THAT SOMEONE HAD HIT A PIPELINE IN SWEENEY STORAGE FIELD. SUPERVISOR TRAVELLED WITH UTILITY AND FIELD PERSON TO DISCOVER THAT A BRUSH HOG HAD BROKEN A 1" SYPHON ON A DRIP. THE PRESSURE ON THE PIPELINE AT THE TIME WAS 904 PSIG. THE PIPELINE SECTION WAS ISOLATED, AND BLOWN DOWN BY 5:15 PM. REPAIRS WERE PERFORMED, AND THE LINE WAS PURGED AND PLACED BACK INTO SERVICE AROUND 10:00 PM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060150 | 2006-12-12 | SUPPLEMENTAL FINAL | 14210 |  | OKLAHOMA NATURAL GAS COMPANY | 401 N. HARVEY AVENUE | OKLAHOMA CITY | OKLAHOMA COUNTY | OH | 73102-3470 | 1330 | 2006-11-08 | 2006 | OKLAHOMA CITY | OKLAHOMA | OK | 73131 |  |  | 35.582 | -97.4907 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 12 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94872 | 46704.3953 | 60382.9897 | 69876 | 27836.7805 | 24996 | 32546.2092 | 0 | 0 | NO | NO | NO | YES | 156 | PRECAUTIONARY |  | 45 | 817572 | 2006-11-08 | 400 | 500 | YES | NO | NO | NO | NO | NO | TRACY ROWLETT - REGULATORY COMPLIANCE SPECIALIST | 4055516458 | TRACYROWLETT@ONG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 16 | 0.25 | API 5L | 35000 |  |  |  |  | UNDER GROUND |  | 42 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | CORRECTED TIME OF INCIDENT
2022-01-31 10:32 | YES | YES | GG (Gas Gathering) | 20060151 | 2006-12-14 18:59 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC COMPANY | PO BOX 770000 MAIL CODE H15E | SAN FRANCISCO | SAN FRANCISCO | CA | 94117 | 1245 | 2006-11-20 | 2006 | STOCKTON | SAN JOAQUIN | CA | 95206 |  |  | 37.986463 | -121.473852 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | BRAIDED HOSE FAILED | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 350 | 205.0973 | 455.7198 | 0 | 0 | 350 | 455.7198 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 1 | 818797 | 2006-11-21 | 2069 | 2160 | NO | YES | NO | NO | NO | NO | RICHARD ARITA | 9259744313 | RTA2@PGE.COM | GATHERING | OTHER | STEEL BRAIDED FLEX TUBING | OTHER | STEEL BRAIDED FLEX TUBING | NO | NO | NO | OTHER | FACILITY BLOW-DOWN SYSTEM | 2005 | 1 | [5 empty] | HOSEMASTER; ANNUFLEX | 2005 | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | STAINLESS STEEL FLEX HOSE | [8 empty] | CONSTRUCTION DEFECT | PROCEDURE NOT FOLLOWED | NO | NO | [19 empty] | OUR INVESTIGATION DETERMINED THAT ON MONDAY, NOVEMBER 20, 2006 A TWO PERSON CREW AT THE FACILITY WAS IN THE PROCESS OF CONDUCTING AN ANNUAL GAS WELL UP-HOLE SAFETY VALVE CHECK WHEN THERE WAS A RELEASE OF GAS. THE FACILITY OPERATOR AND ASSISTANT HAD COMPLETED TAGGING AND CLOSING THE GAS WELL UP-HOLE SAFETY VALVE AND THE BLOCK VALVE FROM THE FACILITY ON A 4-INCH STEEL LINE. AFTER OPENING A 1-INCH VALVE OFF OF THE 4-INCH LINE TO INITIATE THE BLOW-DOWN AND UP-HOLE SAFETY VALVE CHECK, A 1-INCH STEEL BRAIDED FLEX LINE WHICH IS PART OF AN INTEGRAL BLOW-DOWN SYSTEM FOR THE FACILITY FAILED. THE FAILURE OF THE STEEL BRAIDED LINE CAUSED GAS TO ESCAPE IN THE VICINITY OF THE OPERATOR AND ASSISTANT. THERE WAS NO FIRE OR EXPLOSION WITH THE RELEASE OF GAS. IT WAS DETEMINED THAT DURING A FIELD CONSTRUCTION CHANGE, A STEEL BRAIDED FLEX HOSE ONLY RATED FOR 718 PSIG WAS INSTALLED IN A 2160 PSIG SYSTEM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060152 | 2006-12-20 13:22 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORPORATION | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1215 | 2006-12-18 | 2006 | HYNER | CLINTON | PA | 17738 |  | 0+00 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160000 | 93758.7549 | 208329.0717 | 0 | 0 | 160000 | 208329.0717 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 0 | 821377 | 2006-12-18 | 608 | 720 | NO | NO | NO | NO | YES | NO | DAVID D. ANDERSON | 7242232766 | DDANDERSON@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | CATHODIC PROTECTION GAS FIRED GENERATOR | 2000 | [8 empty] | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | A FIRE INVOLVING A GAS FIRED ELECTICAL GENERATOR USED FOR CATHODIC PROTECTION PURPOSES WAS DETECTED ON 12/18/06 BY A RIGHT OF WAY CLEARING CREW. THE ELECTRICAL GENERATING EQUIPMENT AND BUILDING WERE DESTROYED. THERE WAS NO DAMAGE TO THE MAIN PIPELINE. THE FIRE WAS EXTINGUISHED BY SHUTTING OFF GAS SERVICE TAP TO THE THE GENERATOR. THE CAUSE OF THE FIRE WAS DUE TO A LIGHTNING STRIKE. THIS IS A VERY REMOTE LOCATION IN THE SPROUL STATE FOREST. NO INJURIES. CAUSE WAS DETERMINED TO BE AN OIL LEAK ON THE ENGINE IGNITED BY HOT ENGINE PARTS. GENERATOR UNIT WAS REPLACED AND IN SERVICE BY 12/28/2007.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060153 | 2006-12-21 | SUPPLEMENTAL FINAL | 117 |  | AIR PRODUCTS L.P. | 1002 STRANG ROAD | LA PORTE | HARRIS | TX | 77571 | 1048 | 2006-11-24 | 2006 | PORT NECHES | JEFFERSON | TX | 77651 |  |  | 29 58.515 | 93 56.105 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | BOOSTER COMPRESSOR FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 263569.2747 | 585021.8315 | 1000 | 398.374 | 449000 | 584623.4575 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 15 | 819026 | 2006-11-24 | 614 | 860 | NO | YES | NO | NO | NO | NO | KERRY J. STERNER GLOBAL OPERATIONS / PIPELINE MAINT. | 6104818422 | STERNEKJ@APCI.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | H2 BOOSTER COMPRESSOR | 2004 | [8 empty] | INSIDE/UNDER BUILDING |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060154 | 2006-12-21 15:54 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 730 | 2006-11-30 | 2006 | ROMEVILLE | ST. JAMES | LA | 70086 | 66.22 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201000 | 703649.4304 | 1562866.4118 | 1000 | 398.374 | 1200000 | 1562468.0378 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 55 | 820321 | 2006-12-07 | 800 | 887 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | TRANSMISSION | OTHER | FAB ASSEMBLY AND FITTING (WELD CAP) | STEEL |  | NO | NO | NO | OTHER | VALVE SETTING HEADER | 1968 | 36 | 0.5 | API 5L | 60000 | SEAMLESS | ANSI 600 | US STEEL | 1958 | UNDER GROUND |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | GAS CONTROL RECEIVED A CALL TO REPORT GAS LEAKING NEAR HWY 18. SCHRIEVER PERSONNEL CONTACTED INDIVIDUAL, WHO REPORTED THE LOCATION AS THE VALVE SETTING ALONG HIGHWAY 18. PERSONNEL WERE DISPATCHED FROM SCHRIEVER TO INVESTIGATE. PERSONNEL DISCOVERED A GAS LEAKING FROM UNDERGROUND AND VISIBLE AT THE SURFACE UNDER THE DEPARTING PIG LAUNCHER. PERSONNEL ISOLATED THE VALVE SETTING HEADER AND CROSSOVER PIPING AND BLEW DOWN THE GAS AND THE LEAK STOPPED. THE LEAK WAS ORIGINALLY JUDGED TO BE NON-REPORTABLE. COST ESTIMATES FOR THE REPAIR LATER REVEALED IT DID MEET REPORTABLE CRITERIA. THE DOT SW REGION DIRECTOR, ROD SEELEY, WAS NOTIFIED. NO REGULATORY ENFORCEMENT ACTION WAS RECOMMENDED. THE LEAK WAS DETERMINED TO BE IN A 36" HEADER AND THE HEADER WAS EXCAVATED IN THE VICINITY OF THE LEAK. THE LEAK WAS DETERMINED TO HAVE BEEN CAUSED BY SIGNIFICANT INTERNAL CORROSION IN THE 6 O'CLOCK POSITION AT THE WELD CAP ON THE WEST END OF THE HEADER. THE HEADER ADJACENT TO THE LEAK WAS INTERNALLY INSPECTED AND ALL PIPE WITH SIGNIFICANT INTERNAL CORROSION WAS REMOVED BY CUTTING PIPE FROM THE END OF THE HEADER. REPAIR WAS COMPLETED BY WELDING A CAP ONTO THE CUT END. THE OPPOSITE END OF THE HEADER WAS EXCAVATED AND EXAMINED BY X-RAY AND ULTRASONIC MEANS TO VERIFY ITS INTEGRITY. THE REPAIRED HEADER WAS HYDROSTATICALLY TESTED BEFORE RETURNING THE HEADER TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060155 | 2006-12-22 11:56 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 2707 NORTH LOOP WEST | HOUSTON | HARRIS | TX | 77382 | 1300 | 2006-11-25 | 2006 | MIRANDO CITY | WEBB | TX | [5 empty] | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225000 | 128667.6654 | 270370.6892 | 25000 | 9959.3496 | 200000 | 260411.3396 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 | 820636 | 2006-12-11 | 886 | 1104 | YES | NO | NO | NO | NO | NO | JAMES R. MCDONALD | 7133812494 | JMCDONALD@EPROD.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 20 | 0.24 | API 5L - X 65 | 65000 | ERW |  | UNKNOWN |  | UNDER GROUND |  | 72 | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | LEAK WAS REPORTED ON OUR WEBB COUNTY 20" PIPELINE ON NOVEMBER 25, 2006. THE LEAK WAS AT THE LOCATION OF A NEW HOT TAP INSTALLATION WE HAD MADE ON THIS PIPELINE EARLIER IN 2006 AND THE LEAK RATE WAS MINIMAL. AFTER INITIAL REVIEW, A DECISION WAS MADE TO TAKE THE PIPELINE OUT OF SERVICE SO IT COULD BE FURTHER EVALUATED. THIS ACTION WAS THE INITIAL ACTION THAT MADE THE INCIDENT REPORTABLE TO THE RAILROAD COMMISSION OF TEXAS. THE NOTIFICATION TO THE STATE OCCURED WITHIN TWO HOURS OF THAT DECISION AND WAS MADE ON NOVEMBER 25, 2006 BY DOUG MENKE, OPERATIONS SUPERVISOR. OUR INITIAL ASSUMPTION WAS PROVEN TO BE CORRECT IN THAT WE CONFIRMED THAT WE HAD A LEAKING HOT TAP CLAMP. THE CLAMP VENDOR TRAVELLED TO THE LOCATION TO INJECT SEALANT IN THE HOT TAP FITTING TO TRY AND STOP THE LEAK. IT WAS CONFIRMED AT THAT TIME THAT THE PIPE WAS ALSO LEAKING AND THAT A REPAIR OF A LEAKING SEAL WOULD NOT HANDLE THE REPAIR. A DECISION WAS MADE THAT WE WOULD HAVE TO CUT OUT PIPE AND REPLACE THE HOT TAP ASSEMBLY AND LEAKING PIPE. THIS DECISION CAUSED THE REPAIR COST ESTIMATE TO NOW EXCEED THE $50,000 REPORTING THRESHOLD. OPERATIONS NOTIFED COMPLIANCE OF THIS DECISION VIA AN EMAIL ON THE MORNING OF DECEMBER 11, 2006. BASED ON THIS NEW INFORMATION NOTIFICATION OF THIS BEING A REPORTABLE INCIDENT WAS MADE TO THE NRC. THE FITTING ASSEMBLY AND PIPE WERE SENT TO A METALLURGIST FOR EXAMINATION. THE METALLUGICAL ANALYSIS REPORTED THAT ONE OF THE SEALS ON THE HOT TAP CLAMP DID NOT SEAT PROPERLY AND OVER A PERIOD OF TIME BEGAN TO LEAK GAS INTO THE CAVITY BETWEEN THE PRIMARY AND SECONDARY SEAL. IN TIME, THE SECONDARY SEAL FAILED AND GAS BEGAN JETTING TOWARD THE BODY OF THE PIPE UNTIL SUCH TIME THAT THE MAIN 20" PIPELINE WAS CUT AND STARTED TO LEAK. THE VENDOR REPORTED THAT THIS WAS THE FIRST FAILURE OF ITS TYPE ON THIS TYPE OF HOT TAP CLAMP INSTALLATION AND IS TAKING ACTIONS TO IMPROVE THEIR SEAL DESIGN. THE PIPELINE WAS PLACED BACK INTO SERVICE AFTER A TEE WAS WELDED INTO THE PIPELINE ELIMINATING THE NEED FOR A BOLT ON CLAMP AT THIS TIE IN CONNECTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20060156 | 2006-12-28 09:14 | SUPPLEMENTAL FINAL | 2748 |  | CONSUMERS ENERGY | 1945 W PARNALL ROAD | JACKSON | JACKSON | MI | 49201 | 2349 | 2006-11-30 | 2006 | MARION | OSCEOLA | MI | 49665-9555 |  |  | 44.0920 | 85.0996 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | FAILURE AT TANK DIVERTER PLATE SUPPORT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137100 | 80326.8107 | 178421.605 | 100 | 39.8374 | 137000 | 178381.7676 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 59 | 819667 | 2005-12-01 | 55 | 70 | YES | NO | NO | NO | NO | NO | JOAQUIN J AFFONSO JR | 5177881835 | JJAFFONSO@CMSENERGY.COM | TRANSMISSION | OTHER | BODY OF BRINE SURGE TANK | STEEL |  | NO | NO | NO | OTHER | BRINE SURGE TANK | 2003 | 120 | 0.38 | ASME SECTION IX | 25000 | WELDED |  | QB JOHNSON | 2003 | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VESSEL | [9 empty] | MATERIAL DEFECT |  | NO | YES | 11 | 1 | 2003 | WATER |  | 8 | 105 | [12 empty] | THE ANALYSIS OF THE BRINE SURGE TANK FAILURE REVEALED THAT THE CAUSE WAS DUE TO A LARGER THAN EXPECTED LIQUID SURGE INTO THE TANK. THE SURGE DAMAGED THE DIVERTER PLATE RESULTING IN THE DIVERTER PLATE SUPPORTS TEARING AWAY FROM THE WALL OF THE TANK. THE LIQUID SURGE CONTINUED UNTIL THE TAKE WAS FORCE FROM ITS SUPPORT FOUNDATION. AS THE TANK FELL FROM ITS SUPPORTS THE VESSEL CONTINUED TO CATASTROPHICALLY FAIL.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20060157 | 2006-12-28 11:59 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1000 | 2006-12-07 | 2006 |  |  |  |  | 0.20 |  | 29.14.638 | 93.10.707 | OFFSHORE |  | WEST CAMERON | 215 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396500 | 232282.3027 | 515813.6395 | 500 | 199.187 | 396000 | 515614.4525 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 820575 | 2006-12-11 | 930 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 10 | 0.37 | API 5L | 35000 | SEAMLESS | ANSI 600 | US STEEL | 1983 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1983 | NO | [57 empty] | A LEAK IN THE FORM OF BUBBLES WAS DISCOVERED OFFSHORE ON 12/6/06 IN THE WC 215 AREA. NORTHERN NATURAL INITIALLY REPORTED THE LEAK TO THE NRC (#820103). WEATHER CONDITIONS INITIALLY REQUIRED A DELAY FOR A DIVE BOAT TO INVESTIGATE THE SOURCE OF THE LEAK. DIVERS EVENTUALLY DETERMINED THE LEAK WAS ON THE WGP OPERATED 10" WC 215A TO WC 222 PIPELINE THAT IS OWNED BY NORTHERN NATURAL. AFTER DISCOVERY, THE LEAK WAS REPORTED TO THE NRC ON 12/11/06 BY TRANSCO GAS CONTROL (REPORT # 820575). THE LEAK WAS CLAMPED AND RETURNED TO SERVICE ON 12/12/06
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20060158 | 2006-12-28 16:57 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1510 | 2006-12-27 | 2006 | FORT DODGE | WEBSTER | IA | 50530 | 3.24 | 17106 | 42.2970 | -94.1059 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20253 | 11736.6787 | 25437.0501 | 1033 | 411.5203 | 19220 | 25025.5297 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 822145 | 2006-12-27 | 367 | 500 | NO | NO | NO | NO | YES | NO | JOHN A GORMLEY | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1931 | 4.5 | 0.24 |  | 24000 | ERW |  | NATIONAL TUBE | 1931 | UNDER GROUND |  | 30 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | NO | [40 empty] | ON DECEMBER 27, A TILING CONTRACTOR STRUCK THE 4" LAKE CITY BRANCH LINE NEAR DAYTON, IA. THE CONTRACTOR DID NOT MAKE A ONE-CALL. THE CONTRACTOR STRUCK THE PIPELINE, THOUGHT IT WAS A ROCK AND THEN USED A BACKHOE TO TRY AND REMOVE THE ROCK. THIS INCIDENT WILL PROBABLY NOT MAKE THE $50,000 BUT IT IS THOUGHT TO BE SIGNIFICANT TO THE OPERATOR. SUPPLEMENTAL/FINAL REPORT - REPAIRS WERE COMPLETED BY INSTALLING 34 FEET OF NEW TESTED PIPE, THE FINAL TOTAL COST OF REPAIR WAS CALCULATED AT $20,253. ALTHOUGH COST DID NOT EXCEED THE $50,000 THRESHOLD, IT WAS THOUGHT TO BE SIGNIFICANT TO THE OPERATOR THEREFORE IT WAS REPORT. NO FURTHER ACTIONS ARE PLANNED OR NECESSARY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070001 | 2007-01-08 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 915 | 2006-12-12 | 2006 | ELLICOTT CITY | HOWARD | MD | 21042 | 1628.78 | 1310+45 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 87898.8327 | 195308.5047 | 0 | 0 | 150000 | 195308.5047 | 0 | 0 | NO | NO | YES | NO | 0 |  |  |  | 820693 | 2006-12-12 |  |  | NO | NO | NO | NO | NO | NO | JOHNNY LOPEZ | 7132152995 | JOHNNY.LOPEZ@WILLIAMS.COM | TRANSMISSION | OTHER | NO COMPONENT FAILURE INVOLVED. |  |  | NO | NO | NO | COMPRESSOR | [10 empty] | INSIDE/UNDER BUILDING |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | INCIDENT WAS THE RESULT OF ACCIDENTAL IGNITION OF GAS ACCUMULATED IN AN ENGINE'S CRANK CASE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070002 | 2007-01-08 11:06 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1330 | 2006-12-15 | 2006 | OPAL | LINCOLN | WY | 83124 | 51.17 | N/A | 41.69815 | 110.38262 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150500 | 75469.4943 | 105591.2616 | 100000 | 39837.3984 | 48000 | 62498.7215 | 2500 | 3255.1417 | NO | NO | NO | NO | 0 |  | 2 | 0 | 821182 | 2006-12-15 | 666 | 792 | NO | NO | YES | NO | NO | NO | LISA A. MORGAN | 8015846543 | LISA.MORGAN@WILLIAMS.COM | TRANSMISSION | COMPONENT |  | OTHER | INSULATED FLANGE GASKET | NO | NO | NO | PIPELINE |  | 1958 | 24 | 0.41 | API 5L | 52000 | N/A | N/A | N/A | 1958 | UNDER GROUND |  | 38 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | GAS LEAKAGE WAS HEARD BY BLOUT FENCING CREW AS THEY WERE BEGINNING TO REPAIR THE FENCE AT THE N2 SITE. LEAK WAS VERIFIED BY FIELD PERSONNEL AT 1:30 PM. REPAIR HAS BEEN COMPLETED. GASKET WAS FOUND TO BE LEAKING AT THE INSULATING FLANGE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070003 | 2007-01-09 | ORIGINAL | 32005 |  | CROSSTEX LIG, LLC | 311 PATTERSON ST. | LAFAYETTE | LAFAYETTE PARISH | LA | 70501 | 640 | 2006-11-06 | 2006 | GOLDEN MEADOW | LAFOURCHE PARISH | LA | 70537 | BAY MARCHAND 12" RECEIVER |  | 29.1956N | 90.1458W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132500 | 62059.1092 | 61821.38 | 122500 | 48800.813 | 10000 | 13020.567 | 0 | 0 | NO | NO | NO | NO | 0 |  | 18 |  | 817344 | 2006-11-06 | 903 | 1250 | NO | YES | NO | NO | NO | NO | OKSANA HOWARD, MGR OF ENVIRONMENTAL COMPLIANCE | 2147219300 | OKSANA.HOWARD@CROSSTEXENERGY.COM | TRANSMISSION | OTHER | 2' COMPONENT PIPE | STEEL |  | NO | NO | NO | OTHER | DRAIN LINE ON PIG TRAP | 1977 | 2 | 154 | ASTM A106 | 35000 | SEAMLESS | N/A | UNKNOWN | 1976 | UNDER WATER |  | 60 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | CORROSION UNDER CRACKED COATING | OTHER | ATMOSPHERIC | NO |  | NO | [57 empty] | DUE TO EBB/TIDE FLUCTUATION OF THE BRACKISH MARSH WATERS, THE FIELD APPLIED COATING ON THE 2-INCH PIPE CRACKED THUS ALLOWING CORROSION TO OCCUR UNDER THE COATING AND MAKING IT IMPOSSIBLE TO DETECT DURING THE VISUAL INSPECTIONS OF THE INSTALLATION. THE LEAK WAS DETECTED WHEN THE PIPE WAS SUBMERGED UNDER ABOUT 2 FEET OF WATER. THE CLOSEST BLOCK VALVES WERE CLOSED OFF TO PREVENT THE INFLOW OF GAS INTO THE AFFECTED AREA. THE REPAIR OF THE PIPE WAS MADE POSSIBLE AFTER THE OPERATING PRESSURE WS REDUCED TO SAFE CONDITIONS AND THE WATER LINE RECEDED. THE TOTAL VOLUME OF GAS LASOT DUE TO THE LEAK WAS DETERMINED BASED ON THE RECONCILIATION OF SCADA DATA. THE FINANCIAL LOSS OF PRODUCT WAS CALCULATED BASED ON THE MARKET PRICE OF $5 PER MSCF OF NATURAL SWEET GAS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070004 | 2007-01-09 | SUPPLEMENTAL FINAL | 18536 |  | SOUTHWEST GAS CORPORATION | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | CLARK | NV | 89150-0002 | 2328 | 2006-12-06 | 2006 | LAS VEGAS | CLARK | NV | 89109 |  | N/A | 36.10093318 | -115.1762111 | ONSHORE | 4 |  |  |  | NO | NO | INTRASTATE | OTHER | CRACK NEAR FILLET WELD AT BRANCH CONNECTION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59784 | 32224.3762 | 57892.458 | 22076 | 8794.5041 | 37708 | 49097.954 | 0 | 0 | YES | NO | NO | YES | 20 | COMPANY POLICY | 9 | 29 | 820228 | 2006-12-07 | 240 | 310 | NO | YES | NO | NO | NO | NO | HOLLY J. LOYD, SPECIALIST COMPLIANCE | 7023652080 | HOLLY.LOYD@SWGAS.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | OTHER | CRACK ON 16 INCH PIPE NEAR FILLET WELD AT BRANCH | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 16 | 0.25 | API SPECIFICATION 5L | 52000 | ERW | N/A | UNITED STATES STEEL CORPORATION | 1979 | UNDER PAVEMENT |  | 120 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | ON 12/6/06 A SOUTHWEST GAS CREW WAS EXCVATING AROUND PIPELINE FACILITIES LOACTED IN TROPICANA AVE, 645 FEET EAST OF FRANK SINATRA DRIVE, LAS VEGAS. THE WORK INCLUDED INVESTIGATION OF A GRADE 3 LEAK AND ABANDONING TWO 4-INCH STEEL SUBS, ONE OF WHICH INCLUDED A 2-INCH STEEL SIDE-TAP VALVE. BOTH STUBS WERE WELDED TO A 16-INCH STEEL TRANSMISSION PIPELINE. AT 23:28 ON 12/6/06, WHILE THE SOUTHWEST GAS CREW WAS REMOVING DIRT, DAMAGE OCCURED ON THE 16-INCH PIPE NEAR THE FILLET WELD FOR THE 2-INCH SIDE-TAP VALVE STUB, CAUSING LEAKAGE TO OCCUR. SOUTHWEST IMMEDIATELY IMPLEMENTED THE INCIDENT MANAGEMENT SYSTEM. ATMOSPHERIC GAS DETECTED IN THE PARKING GARAGE AT THE NEW YORK-NEW YORK HOTEL DURING THE INITIAL PERIMETER SURVEY RESULTED IN CLOSURE OF THE GARAGE. THE INCIDENT PERIMETER WAS SECURED AT 01:15 ON 12/07/06. THE PERIMETER WAS LATER EXPANDED AT 03:20 ON 12/7/06 DUE TO SHIFTING WINDS. CONTINUAL SURVEILLANCE OF THE AFFECTED AREA CONFIRMED THAT NO UNDERGROUND LEAK MIGRATION WAS OCCURRING. ATTEMPTS TO MAINTAIN THE LINE PRESSURE IN THE 16-INCH PIPELINE WHILE REPAIRING THE DAMAGE FAILED SO SOUTHWEST CREWS CLOSED VALVES TO ISOLATE THE AFFECTED AREA. SOUTHWEST COMPLETED BLOW-DOWN OF THE AFFECTED LINES ON 12/7/06 AT 08:57 AND BEGAN REPAIRS. THE DAMAGE TO THE 16-INCH STEEL LINE WAS REPAIRED BY REMOVING THE 2-INCH SIDE-TAP VALVE SUB AND BOLTING ON A 16-INCH REPAIR CLAMP. ON 12/7/06, SOUTHWEST COMPLETED THE REPAIRS AT 14:50 AND THE RELIGHTS AT 23:45. THE INVESTIGATION OF THE DAMAGED 16-INCH BY 2-INCH CONNECTION INDICATES EARTH MOVEMENT DURING EXCAVATION NEAR THE 2-INCH SIDE TAP VALVE STUB CAUSED A CRACK TO OCCUR ON THE 16-INCH PIPE NEAR THE 2-INCH FILLET WELD TO THE 16-INCH PIPELINE. A PRESSURE TEST OF THE 4-INCH PIPE INCLUDING THE 2-INCH VALVE CONFIRMED THAT THE GRADE 3 LEAK WAS ON THE 2-INCH SIDE TAP VALVE AND WAS UNRELATED TO THE FAILURE. THIS INCIDENT AFFECTED 66 CUSTOMERS. GAS LOSS INCLUDED 27873 THERMS. ESCAPING GAS DID NOT IGNITE. NO INJURIES OR FATALITIES RESULTED FROM THE INCIDENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070005 | 2007-01-09 13:02 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1200 | 2007-01-01 | 2007 | SATANTA | HASKELL | KS | 67870 |  |  | N37.42409 | W100.98044 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83994 | 47828.3732 | 105617.9327 | 1000 | 420.3431 | 82994 | 105197.5896 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 822505 | 2007-01-01 | 150 | 500 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | HYDRATE FREEZE IN LINE | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1960 | [8 empty] | UNDER GROUND |  | 40 | NATURAL FORCES | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [14 empty] | FROZEN COMPONENTS | [50 empty] | ON JANUARY 1, 2007, AT APROXIMATELY 1200, SERVICE TO THE TOWN OF SATANTA, KANSAS WAS INTERRUPTED DUE TO THE FORMATION OF A HYDRATE FREEZE IN THE 4-INCH INLET SUPPLY LINE TO THE SATANTA TOWN BORDER STATION. THE HYDRATE FREEZE WAS FOUND TO HAVE DEVELOPED DOWNSTREAM OF THE HASKELL COUNTY DEHYDRATION UNIT AND UPSTREAM OF THE SATANTA TBS. THE DEHYDRATION UNIT AND THE TBS ARE OWNED AND OPERATED BY NORTHERN NATURAL GAS AND DELIVER TO THE LOCAL DISTRIBUTION COMPANY, AQUILA, INC. AQUILA PROVIDES GAS SERVICE TO APPROXIMATELY 500 HOMES AND BUSINESS IN SATANTA, WHICH WERE IMPACTED BY THE LOSS OF SERVICE. AT THE TIME OF THE INCIDENT THE STATE OF KANSAS WAS INCURRING A VERY SEVERE WINTER STORM WHICH PRODUCED LOW TEMPERATURES AND A SIGNIFICANT AMOUNT OF ICE WHICH RESULTED IN A BUILDUP OF ICE ON POWER LINES AND POWER POLES RESULTING IN MANY POLES AND LINES BREAKING DUE TO EXCESS WEIGHT CREATING WIDESPREAD POWER OUTAGES. SUPPLEMENTAL/FINAL REPORT - THE ROOT CAUSE OF THE SERVICE INTERRUPTION TO THE TOWN OF SATANTA,KS IS DETERMINED TO BE FROM A HYDRATE FREEZE IN THE GAS LINE.THE HYDRATE FREEZE WAS DETERMINED TO BE CAUSED BY SEVERAL CONTRIBUTING FACTORS. WATER SATURATED GAS IN COMBINATION WITH HYDROCARBON LIQUIDS, MULTIPLE SYSTEM CONFIGURATIONS, MULTIPLE ELECTRICAL POWER OUTAGES WHICH SHUTDOWN THE TBS HEATER AND THE BYPASS OF THE DEHYDRATION UNIT ON 1/1/2007 GENERATED THE CONDITIONS REQUIRED TO FORM A HYDRATE FREEZE. THE FORMATION OF THE HYDRATE FREEZE BLOCKED OFF THE GAS FLOW TO THE TOWN OF SATANTA, KS, RESULTING IN A LOSS OF NATURAL GAS SERVICE TO THE TOWN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070006 | 2007-01-09 14:26 | ORIGINAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH ST | LOS ANGELES | LOS ANGELES | CA | 90013 | 1405 | 2006-12-11 | 2006 | LOS ANGELES | LOS ANGELES | CA |  | 437' S MLV ID756 N |  | 34.323281 | -118.487611 | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 103203.8757 | 161006.241 | 110000 | 43821.1382 | 90000 | 117185.1028 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 38 | 820653 | 2006-12-13 | 200 | 228 | YES | NO | NO | NO | NO | NO | JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1998 | 22 | 0.3 | TBD | 24000 |  |  |  |  | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | OTHER | GOLF COURSE | YES | 9 | 1 | 2006 | ONE-CALL SYSTEM | YES | FLAGS |  | ACCURATE | YES | [36 empty] | CONTRACTOR STRUCK 22" HIGH PRESSURE MAIN WHILE GRADING FOR GOLF COURSE. FACILITIES HAD BEEN PREVIOUSLY MARKED AND POT-HOLED. INCIDENT BECAME REPORTABLE AT 18:00 WHEN ESTIMATED GAS LOST AND REPAIRS EXCEEDED $50K.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070007 | 2007-01-17 17:46 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS PIPELINE | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 930 | 2006-12-19 | 2006 |  |  | LA |  | MAIN PASS 313, MP 3.9 |  | 29* 06' 21.5 | -88*43'16.5 | OFFSHORE |  | SOUTH PASS | 62 |  | YES | NO | INTERSTATE | OTHER | PIPELINE DAMAGED BY BOAT DRAGGING ACROSS LINE. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105000 | 60893.0662 | 132197.5397 | 5000 | 1991.8699 | 100000 | 130205.6698 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 821451 | 2006-12-19 | 1104 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | NEAR A SUB-SEA ASSEMBLY | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 8.63 | 0.5 | 5L | 35000 |  |  | US STEEL | 1982 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE LEAK OCCURRED ON THE 8-INCH MAIN PASS 313 LINE, OPERATED BY SOUTHERN NATURAL GAS IN SOUTH PASS BLOCK 62, GULF OF MEXICO, OFFSHORE LOUISIANA. THE LEAK WAS CONFIRMED BY A DIVE BOAT AND OCCURRED NEAR A SUB-SEA CONNECTION. THE LEAK WAS APPARENTLY CAUSED BY A DIVE VESSEL, WORKING IN THE AREA, DRAGGING AN ANCHOR ACROSS THE PIPELINE. THE SUBSEA TIE-IN (SSTI) HAS BEEN REPAIRED AND THE MAIN PASS 313 PIPELINE HAS BEEN PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070008 | 2007-01-17 23:14 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE COMPANY | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 955 | 2006-12-19 | 2006 | MASON | CASS | MI |  | MLV 82/MP 86.5 | 560+20 | 41.7682650 | -85.9140150 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1730000 | 880182.0252 | 1303691.2377 | 1050000 | 418292.6829 | 680000 | 885398.5548 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 821455 | 2006-12-19 | 658 | 858 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS.SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 24 | 0.25 | 5L | 60000 | DSAW |  | US STEEL | 1968 | UNDER GROUND |  | 40 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | YES | 11 | 30 | 2006 | ONE-CALL SYSTEM | YES |  | YES | ACCURATE | [37 empty] | THE 24 INCH ANR PIPELINE, LINE 1-504, NEAR MASON TOWNSHIP, MI. RUPTURED, APPARENTLY DUE TO THIRD-PARTY EXCAVATION DAMAGE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070009 | 2007-01-22 17:37 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1300 | 2006-12-18 | 2006 | [6 empty] | 93.33.51 | 28.11.38 | OFFSHORE |  | HIA | 312 |  | YES | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149887 | 87540.0019 | 193082.9021 | 2300 | 916.2602 | 147587 | 192166.6419 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 821368 | 2006-12-18 | 869 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | VALVE | 1979 | [5 empty] | BALL | CAMERON | 1979 | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | SECURED DIVE VESSEL AND DIVERS TO INVESTIGATE AND MAKE REPAIRS TO GREASE FITTING ON 16" SUBSEA VALVE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070010 | 2007-01-24 | ORIGINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 900 | 2006-10-09 | 2006 | BUFFALO | LEON | TX | 75831 | MM17 | 900+05 | 31.375188 | 95.952498 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 49809.3385 | 110674.8193 | 0 | 0 | 0 | 0 | 85000 | 110674.8193 | NO | NO | NO | NO | 0 |  | 2 | 30 |  |  | 350 | 490 | NO | NO | YES | NO | NO | NO | ELLEN WEAVER, DIRECTOR, REGULATORY AND COMPLIANCE | 2142062875 | ELLEN.WEAVER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1936 | 18 | 0.28 | ASTM A53 | 30000 |  |  |  |  | UNDER GROUND |  | 42 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | OTHER | INTERNAL CORROSION | YES |  | NO | [57 empty] | A LEAK RELEASED CONDENSATE INTO A STOCK POND
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070011 | 2007-01-26 11:32 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1000 | 2006-12-29 | 2006 | EMPIRE | LAFOURCHE | LA |  | MP527A-201 + |  | 29*18'12 | -89*36'50 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 201916.6927 | 433127.7765 | 25000 | 9959.3496 | 325000 | 423168.4269 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 822311 | 2006-12-29 | 900 | 1235 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 7134204169 | LOUIS.SALINAS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 12.75 | 0.31 | API 5L | 35000 | SEAMLESS |  |  | 1967 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | A LEAK WAS DISCOVERED ON THE 12-INCH TGP 527A-200 LINE, IN THE BASTIAN BAY AREA, NEAR EMPIRE, LA. THE LEAK WAS LOCATED NEAR A PIPELINE RISER IN APPROXIMATELY 4 FEET OF WATER. INVESTIGATION REVEALED THAT A 1/2 INCH VALVE HAD BEEN DAMAGED BY AN UNKNOWN SOURCE. THE VALVE WAS REPLACED AND THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070012 | 2007-02-13 | SUPPLEMENTAL FINAL | 6141 |  | PUBLIC SERVICE COMPANY OF NEW MEXICO | 414 SILVER AVENUE, SW | ALBUQUERQUE | BERNALILLO | NM | 87102-1007 | 1110 | 2007-01-08 | 2007 | RIO RANCH | SANDOVAL | NM | [5 empty] | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146229 | 73486.4181 | 87960.5085 | 114956 | 48320.9657 | 31273 | 39639.5429 | 0 | 0 | YES | NO | NO | YES | 84 | COMPANY POLICY | 1 | 25 | 823142 | 2007-01-08 | 511 | 600 | NO | YES | NO | NO | NO | NO | GARY G. ROYBAL, P.E. MANAGER, DOT COMPLIANCE & TECHNICAL | 5056973636 | GARY ROYBAL@NMGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2005 | 16 | 0.38 | X52 | 52000 |  |  |  |  | UNDER GROUND |  | 10 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 1 | 3 | 2007 | ONE-CALL SYSTEM | NO | [40 empty] | CONTRACTOR HIT 16" MAIN LINE WHILE PERFORMING ROAD WORK AT THE INTERSECTION OF UNSER AND IDALIA IN RIO RANCHO, NM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070013 | 2007-02-13 16:39 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1640 | 2007-01-16 | 2007 | HEALDSBURG | SONOMA | CA |  | LINE 21E MP 69 |  |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 285227.2727 | 633766.2338 | 0 | 0 | 500000 | 633766.2338 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 823894 | 2007-01-17 | 420 | 720 | NO | YES | NO | NO | NO | NO | RICHARD ARITA | 9259744313 | RTA2@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 12.75 | 0.25 | API-5LX-X52 | 52000 | ERW |  |  |  | UNDER GROUND |  | 42 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | POSSIBLE SHIELDING OF CP | YES | 1967 | NO | [57 empty] | THERE WAS A 1/4" CORROSION PIT ON OUR PIPELINE. THE LEAK WAS NOT CONSIDERED HAZARDOUS. BECAUSE OF INSTALLATION OF A TEMPORARY BYPASS LINE, THE COST TO REPAIR EXCEEDED $500,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070014 | 2007-02-16 15:52 | SUPPLEMENTAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 1000 | 2007-01-20 | 2007 | BRAWLEY | IMPERIAL | CA |  | 1320+78 |  | 32.986513 | -115.509269 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175000 | 86871.6578 | 94739.7823 | 150000 | 63051.4706 | 25000 | 31688.3117 | 0 | 0 | NO | NO | NO | YES | 30 | PRECAUTIONARY | 13 | 10 | 824210 | 2007-01-20 | 680 | 720 | YES | NO | NO | NO | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 10 | 0.19 | API-5LX-X42 | 49 |  |  |  |  | UNDER PAVEMENT |  | 42 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 12 | 21 | 2006 | ONE-CALL SYSTEM | YES | PAINT | NO | ACCURATE | YES | [36 empty] | CONTRACTOR EXCAVATING TO INSTALL WATER MAIN WITH TRACK HOE STRUCK 10" TRANSMISSION MAIN. THE DAMAGED TRANSMISSION MAIN SERVED VARIOUS INDUSTRIAL CUSTOMERS, AS WELL AS THE CITY OF MEXICALI DISTRIBUTIN SYSTEM. BY BACKFEEDING FROM FROM ANOTHER LINE, IT WAS POSSIBLE TO KEEP KEEP THE CITY OF MEXICALI ONLINE WHILE DAMAGED SECTION WAS SHUT FOR REPAIRS. INVESTIGATION DETERMINED THAT CONTRACTOR HAD A CURRENT USA TICKET, AND FACILITIES WERE PROPERLY MARKED. THIS JOB HAD 100% STANDBY DURING EXCAVATION, EXCEPT FOR THE DATE OF THE DAMAGE. THE DAMAGE OCCURRED ON A SATURDAY, AND THE CONTRACTOR SPECIFICALLY STATED HE WOULD NOT BE WORKING ON THIS PARTICULAR DATE. ALL REPAIRS HAVE BEEN COMPLETED, AND INVOLVED CUSTOMERS RESTORED. THIS INCIDENT BECAME REPORTABLE WHEN DAMAGE ESTIMATES EXCEEDED $50K, AND MEDIA ARRIVED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070015 | 2007-02-20 09:56 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS COMPANY | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 850 | 2007-01-23 | 2007 | WETUMPKA | ELMORE | AL |  | 224.3 |  | N32.52090 | W86.27422 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1356496 | 707034.3559 | 1064440.6508 | 773100 | 324967.2794 | 583396 | 739473.3714 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 45 | 824407 | 2007-01-23 | 1129 | 1200 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 16 | 0.31 | API 5L | 52000 | FLASH WELD |  | A.O. SMITH | 1951 | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | LEAK WAS DISCOVERED ON SNG'S 16" SOUTH MAIN PIPELINE IN ELMORE COUNTY, AL AT APPROXIMATE MILEPOST 224.3 DUE TO PRESSURE DROP SEE IN COMPANY'S GAS CONTROL. PIPE FAILED IN CIRCUMFERENTIAL WELD, BELIEVED TO BE CAUSED BY POROSITY AT TIME OF CONSTRUCTION (1951). FAILURE WAS A COMPLETE SEPARATION WITH IGNITION OCCURRING ABOUT 15 MINUTES AFTER THE INITIAL GAS RELEASE. AN INVESTIGATION INCLUDING METALLURGICAL LAB TESTING OF FAILED PIPE HAS BEEN COMPLETED. THE INVESTIGATION CONFIRMED THAT THE WELD FAILED DUE TO IT BEING OF LESS THAN TOP QUALITY WORKMANSHIP, TAKING INTO ACCOUNT ITS VINTAGE, IN CONJUNCTION WITH LONGITUDINAL STRESSES ON THE WELD, THE SOURCE OF SUCH STRESSES REMAINING UNKNOWN.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070016 | 2007-02-22 07:24 | SUPPLEMENTAL FINAL | 26330 |  | ENOGEX INC | 515 CENTRAL PARK DRIVE, SUITE 600, PO BOX 24300 | OKLAHOMA CITY | OKLAHOMA | OK | 73124 | 100 | 2007-01-23 | 2007 | WEATHERFORD | CUSTER | OK | 73096 | KIRKLAND CRP |  | N3559732 | W9868087 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | PSV FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 25499.2201 | 33724.9968 | 35000 | 14712.0098 | 0 | 0 | 15000 | 19012.987 | NO | NO | NO | NO | 0 |  | 9 | 45 | 824431 | 2007-01-23 | 260 | 1050 | NO | NO | NO | NO | NO | NO | MIKE REED | 4055584685 | REEDMD@OGE.COM | GATHERING | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | OTHER | RELEIF VALVE | [6 empty] | PILOT OPERATED | AXELSON |  | ABOVE GROUND |  |  | NATURAL FORCES | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [14 empty] | FROZEN COMPONENTS | [50 empty] | ON JANUARY 23, 2007 A PILOT OPERATED PSV THAT PROVIDES OVER PRESSURE PROTECTION FOR A CLASS III REGULATED GAS GATHERING SEGMENT ACTUATED PREMATURELY DUE TO MOISTURE FREEZING IN THE PILOT SENSING LINE AND/OR PILOT BODY. THE PSV FAILED TO THE OPEN POSITION RESULTING IN AN UNPLANNED RELEASE OF NATURAL GAS AND DISTILLATE TO THE ATMOSPHERE FOR A PERIOD OF 9 HOURS 45 MINUTES. THE PSV WAS REPLACED WITH A SPRING OPERATED RELIEF VALVE. SIGNIFICANT ENVIRONMENTAL REMEDIATION OF THE AFFECTED AREA ADJACENT TO THIS GAS RELEASE WAS INITIATED IMMEDIATELY AND CONTINUES AT THIS TIME. THE ESTIMATED REMEDIATION COSTS WILL EXCEED $50,000. A SUPPLEMENTAL REPORT WILL BE SUBMITTED FOLLOWING THE DETERMINATION OF TOTAL COST. 08/12/08 UPDATE: ENVIRONMENTAL DAMAGES WERE REMEDIATED AT A TOTAL COST OF $80,000.00.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070017 | 2007-02-23 | ORIGINAL | 1552 |  | BLUE DOLPHIN PIPE LINE COMPANY | 801 TRAVIS, SUITE 2100 | HOUSTON | HARRIS | TX | 77002 | 1550 | 2007-01-25 | 2007 | [6 empty] | 28.54.30 | 94.47.42 W | OFFSHORE |  | GALVESTON | 286 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 824670 | 2007-01-25 | 360 | 600 | NO | YES | NO | NO | NO | NO | LARRY J. TURPIN | 7132277660 | LTURPIN@BLUE-DOLPHIN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS |  |  |  | UNDER GROUND |  | 10 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | CO2 AND WATER | YES | 1965 | NO | [57 empty] | PINHOLE GAS LEAK CAUSED AN APPARENT LOCALIZED INTERNAL CORROSION. LEAK WAS REPAIRED BY INSTALLATION OF 1000 PSIG WP BOLTED PIPELINE CLAMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070018 | 2007-02-23 16:08 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS COMPANY | 1900 5TH AVE NORTH | BIRMINGHAM | JEFFERSON | AL | 35202 | 945 | 2007-01-29 | 2007 | [6 empty] | 29 DEG 17.171 MIN | 88 DEG 54.966 MIN | OFFSHORE |  | MAIN PASS | 72 |  | YES | NO | INTERSTATE | OTHER | LEAK ON 8 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5598000 | 3193059.0018 | 7092257.9959 | 4000 | 1681.3725 | 5594000 | 7090576.6234 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 824917 | 2007-01-29 | 809 | 1736 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | SUB SEA TIE IN ASSEMBLY | STEEL |  | NO | NO | NO | PIPELINE |  | 1985 | 8 | 0.32 | AP 5L | 35000 |  | 8 | GROVE | 1985 | UNDER WATER |  | 36 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A DIVE VESSEL WORKING FOR A PRODUCER APPARENTLY DAMAGED THE SOUTHERN NATURAL GAS SUBSEA TAP ASSEMBLY IN MAIN PASS BLK. 72 WITH ONE OF IT¿S ANCHOR CABLES. A LEAK WAS NOTICED AT THE SURFACE. THIS SUBSEA TAP ASSEMBLY IS LOCATED ON SNG¿S 18¿ SOUTH PASS 60 PIPELINE AT MP 20.313. THIS ASSEMBLY HAS TWO PIPELINES THAT TIE IN SUBSEA, ONE BEING THE 8¿ MAIN PASS 61 PIPELINE, WHICH IS THE SUBJECT OF THIS REPORT. REPAIRS HAVE BEEN MADE AND THE PIPELINE IS BACK IN SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070019 | 2007-02-23 16:47 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1745 | 2007-02-05 | 2007 | HUTCHINSON | RENO | KS | 67501 |  | SERIES 140, STA. 9162+79 | 37.99156570 | -98.04474640 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6221217 | 3020393.7238 | 2702306.3723 | 6118217 | 2571750.5282 | 100000 | 126753.2468 | 3000 | 3802.5974 | NO | NO | NO | NO | 0 |  | 11 | 0 | 852617 | 2007-02-05 | 856 | 900 | NO | NO | YES | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | OTHER | GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 26 | 0.31 | 2030-D (SMITH) | 52000 | FLASH WELD |  | A. O. SMITH | 1947 | UNDER GROUND |  | 78 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | GIRTH WELD |  |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | THE LEAK WAS REPORTED TO GAS CONTROL AT 5:45 PM, FEBRUARY 5, 2007 BY TWO PERSONS (NON-COMPANY) DRIVING BY ON THE NEARBY HIGHWAY. THE LEAK WAS CONFIRMED BY SSCGP PERSONNEL AT 6:25 PM. THE LOCAL DISTRICT MANAGER CALLED IN TANK TRUCKS TO SUPPLY GAS TO THE CITIES OF PARTRIDGE AND HEADING. THE HUTCHINSON FRACTIONALIZATION PLANT WAS NOTIFIED THEY WOULD LOSE THEIR GAS. THE RENO COUNTY SHERIFF'S DEPARTMENT ASKED BNSF RAILROAD TO SHUT DOWN OPERATIONS IN THE AREA OF THE LEAK. THE TANK TRUCKS BEGAN HOLDING UP THE TWO CITIES AT 1:00 AM ON FEBRUARY SIXTH AND THE FRACTIONALIZATION PLANT WAS SHUT IN. THE MAIN LINE GATES WERE CLOSED AND THE BLOW DOWN BEGAN. THE RAILROAD TRACKS WERE RE-OPENED AT 4:45 AM. THE LINE WAS DUG UP AND IT WAS DETERMINED THAT A CRACKED WELD WAS THE CAUSE OF THE LEAK. THE LINE WAS CAPPED ON THE NORTH SIDE OF THE BNSP RAILROAD TRACKS AND ON THE SOUTH SIDE OF HIGHWAY 50 LEAVING THE SECTION UNDER THE RAILROAD TRACKS AND HIGHWAYS ISOLATED FOR MORE INSPECTIONS. 3/12/08 A SUPPLEMENTAL AND FINAL REPORT OF THIS INCIDENT IS BEING MADE TO CHANGE THE COST OF GAS LOSS ONLY. THE COST IS BEING RAISED FROM $500,000 TO $6,118,217. ON REVIEW OF SYSTEM BALANCE DATA, IT WAS DISCOVERED GAS LOSSES BEGAN ON JANUARY 22ND AND CONTINUED UNTIL THE LEAK WAS DISCOVERED ON FEBRUARY 5TH. THIS GAS COST IS BASED ON ACTUAL GAS LOSSES AT A SYSTEM AVERAGE COST OF $5.50/MCF IN JANUARY 2007 AND $7.01/MCF IN FEBRUARY 2007. THIS UNDETECTABLE LEAK RESULTED FROM A FAILED GIRTH WELD WHICH CREATED A NARROW CRACK-LIKE OPENING ON THE BOTTOM OF THE PIPE LOCATED IN A REMOTE AREA. THE GAS ESCAPED INTO THE ATMOSPHERE THROUGH NUMEROUS SMALL HOLES AND CRACKS IN THE GROUND. THE PRESSURES MONITORED UP AND DOWN STREAM OF THE LEAK VIA THE SCADA SYSTEM ALSO DID NOT INDICATE THAT ANYTHING WAS ABNORMAL ON THAT LINE. THE LEAK REMAINED UNDETECTED UNTIL A VOLUNTEER FIREMAN NOTICED FROM HIS TRUCK TRAVELING ON A NEARBY HIGHWAY (WHEN ATMOSPHERIC CONDITIONS WERE RIGHT) A VISIBLE CONDENSATION IN THE CLEAR GASES ESCAPING FROM THE GROUND. THE COMPANY HAS INSTITUTED A NEW REAL-TIME MODELING APPLICATION TO ASSIST IN REVIEWING OVERALL PIPELINE EFFICIENCIES, INCLUDING RECEIPT AND DELIVERY VOLUMES AND PRESSURES WHICH SHOULD ASSIST IN BEING ABLE TO IDENTIFY SIMILAR SITUATIONS EARLIER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070020 | 2007-02-26 09:54 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATUAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 1700 | 2007-02-06 | 2007 | CLEAR LAKE | CERRO GORDO | IA | 50428 | 8.22 | 434.06 | 43.1555229 | -93.3495445 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53780 | 27210.5645 | 34152.3973 | 40151 | 16877.1973 | 13629 | 17275.2 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 825737 | 2007-02-06 | 664 | 800 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | FARMTAP (RURAL SALES FACILITY) | STEEL |  | NO | NO | NO | REGULATOR/METERING |  |  | 2.38 | 0.22 | API 5L | 35000 | SEAMLESS |  |  |  | ABOVE GROUND |  | 60 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON FEBRUARY 6, 2007, AT APPROXIMATELY 5:33 P.M., NORTHERN'S OPERATIONS COMMUNICATION CENTER (OCC) RECEIVED A CALL FROM THE CLEAR LAKE, IOWA POLICE DEPARTMENT. THEY REPORTED THAT A VEHICLE HAD LEFT THE ROAD AND STRUCK A FARMTAP SETTING NORTH OF HIGHWAY 122/18 ON HICKORY AVENUE. THIS IS SECTION 5, TOWNSHIP 96N, RANGE 22W OF CERRO GORDO COUNTY. THE VEHICLE LEFT THE RAOD AND STRUCK THE FARM TAP SETTING, RESULTING IN BLOWING GAS TO ATMOSPHERE. THERE WAS NO INJURIES OR FIRE. THE CLEAR LAKE POLICE DEPARTMENT AND THE CERRO GORDO COUNTY SHERIFF'S DEPARTMENT RESPONDED TO THE SITE. THE AREA IS NOT DENSELY POPULATED, HOWEVER PUBLIC OFFICIALS DID BLOCK OFF THE ROAD. NORTHERN PERSONNEL ISOLATED A PORTION OF THE LINE (IAB7002)AND BLEW THE PRESSURE DOWN TO ENABLE EXCAVATION AND REPAIR. UPON EXCAVATION IT WAS FOUND THAT THE UNDERGROUND PLUG VALVE WAS NOT DAMAGED. THE VALVE WAS CLOSED, A NEW ONE INCH PRESSURE TESTED RISER WAS INSTALLED.THE AREA WAS BACKFILLED, THE LINE WAS RE-PRESSURIZED, A NEW FARM TAP SETTING AND FENCE WAS INSTALLED, GAS SERVICE WAS RESTORED TO THE DAMAGED FARMTAP CUSTOMER (DAVID MCDEVITT). THERE WERE NO OTHER SERVICE INTERRUPTIONS. WEATHER CONDITIONS AT THE TIME WERE 2 DEGREES FARENHIT, WITH A WIND OF 2 MPH OUT OF THE NORTH/NORTHEAST. THE ROAD CONDITION WAS SNOW PACKED. SUPPLEMENTAL/FINAL REPORT. THE COST OF THE INCIDENT WAS UPDATED AS MORE ACCURATE FIGURES WERE OBTAINED. 9/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN PHMSA.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070021 | 2007-02-28 10:03 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 735 | 2007-02-02 | 2007 | [6 empty] | N 28.16.48 | W 93.57.37 | OFFSHORE |  | HIGH ISLAND | 469 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229272 | 130412.6983 | 286916.8056 | 4359 | 1832.2757 | 224913 | 285084.5299 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 825328 | 2007-02-02 | 880 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 8.63 | 0.32 | API 5LX42 | 42000 | ERW |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1980 | NO | [57 empty] | OPERATIONS PERSONNEL SPOTTED GAS BUBBLES AT THE SURFACE NEAR HIGH ISLAND BLOCK 469. NOTIFICATIONS WERE MADE TO APPROPRIATE AGENCIES. A DIVE VESSEL AND DIVERS WERE SECURED AND PROCEEDED TO THE OFFSHORE SITE. LOCATION OF THE SUBSEA LEAK WAS FOUND AND REPAIRED WITH A PIPELINE CLAMP. PIPELINE WAS PRESSURED UP TO CONFIRM NO LEAKS, AND THE CLAMP WAS COVERED WITH THREE FEET OF SAND BAGS.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070022 | 2007-02-28 10:21 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 737 | 2007-02-06 | 2007 | [6 empty] | N 28.16.179 | W 93.57.164 | OFFSHORE |  | HIGH ISLAND | 469 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226999 | 129312.4103 | 285961.3657 | 2086 | 876.8358 | 224913 | 285084.5299 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 825640 | 2007-02-06 | 880 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 8.63 | 0.32 | API 5LX42 | 42000 | ERW |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1980 | YES | 0 | 1 | [55 empty] | OPERATIONS PERSONNEL SPOTTED GAS BUBBLES AT THE SURFACE NEAR HIGH ISLAND BLOCK 469. NOTIFICATIONS WERE MADE TO APPROPRIATE AGENCIES. A DIVE VESSEL AND DIVERS WERE SECURED AND PROCEEDED TO THE OFFSHORE SITE. LOCATION OF THE SUBSEA LEAK WAS FOUND AND REPAIRED WITH A PIPELINE CLAMP. PIPELINE WAS PRESSURED UP TO CONFIRM NO LEAKS AND THE CLAMP WAS COVERED WITH THREE FEET OF SAND BAGS. A PREVIOUS LEAK WAS REPORTED ON THIS PIPELINE VIA NRC REPORT NUMBER 825328.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070023 | 2007-02-28 10:33 | ORIGINAL | 18626 |  | STARR COUNTY GAS SYSTEM | 413 1/2 E MAIN | RIO GRANDE CITY | STARR | TX | 78582 | 1430 | 2007-02-02 | 2007 | RIO GRANDE CITY | STARR | TX | 78582 | VALVE STATION |  |  |  | OFFSHORE |  | RIGSBY FIELD |  | TX | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 180 |  | NO | NO | NO | NO | NO | NO | TOMAS CANTU | 9564872400 | STARR_GAS@YAHOO.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | OTHER | VALVE CLOSED BY 3RD PARTY | STEEL |  | NO | NO | NO | OTHER | VALVE |  | 2 | [7 empty] | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | CONSTRUCTION DEFECT | PROCEDURE NOT FOLLOWED | NO | NO | [19 empty] | 3RD PARTY CLOSED VALVE TO LINE THAT FEED GAS TO STARR COUNTY GAS SYSTEM. THIS WAS DONE AT PRODUCER GAS GATHERING CO STATION. APPROXIMATELY 3/4 MILES WEST OF HIGHWAY 755. 3 1/2 MILES EAST OF CITY LIMIT TO RIO GRANDE CITY, TX AND STARR COUNTY GAS SYSTEM STATION #14.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070025 | 2007-03-01 18:50 | ORIGINAL | 31296 |  | VENOCO INC. | 6267 CARPINTERIA AVE. | CARPINTERIA | SANTA BARBARA | CA | 93013 | 1431 | 2006-06-05 | 2006 | PITTSBURG | CONTRA COSTA | CA |  | 35 |  | N 35 | E 55 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 40383.3385 | 86625.5553 | 5000 | 1991.8699 | 55000 | 71613.1184 | 10000 | 13020.567 | YES | NO | NO | NO | 0 | [5 empty] | 770 | 1020 | NO | NO | NO | NO | NO | NO | KEITH WENAL | 8057452259 | KWENAL@VENOCOINC.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1991 | 12 | 0.25 | [6 empty] | UNDER PAVEMENT |  | 228 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1991 | NO | [57 empty] | THE PIPELINE WAS EXCAVATED AND TWO SHOVEL BLADES WERE FOUND CONTACTING THE PIPELINE AT A 5 O'CLOCK ORIENTATION. OVER TIME THE SHOVEL BLADES CUT THE PIPE COATING AND MAKING CONTACT WITH THE PIPE WALL CREATING A LOCALIZED CORROSION CELL WHICH DEVELOPED INTO A PIN HOLE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070026 | 2007-03-05 10:32 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1205 | 2007-02-03 | 2007 | VICKSBURG | WARREN | MS | 39180 | 77.40 | 4086+65 | 32.288968 | 90.868572 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 83758.6898 | 107480.1375 | 120000 | 50441.1765 | 45000 | 57038.961 | 0 | 0 | YES | NO | NO | YES | 200 | PRECAUTIONARY | 8 | 55 | 825437 | 2007-02-03 | 300 | 475 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BOARDWALKPIPELINES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1939 | 18 | 0.25 |  | 35000 | SEAMLESS | N/A | NATIONAL | 1939 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | WRINKLE BEND | [11 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | INCIDENT RESULTED FROM A CRACK IN A WRINKLE BEND FROM FATIGUE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070027 | 2007-03-05 13:54 | ORIGINAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS COMPANY | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 1400 | 2007-02-05 | 2007 | VENTURA | VENTURA | CA |  | 47.22 |  | 34.341731 | -119.292589 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 41661.074 | 84051.4738 | 13000 | 5464.4608 | 62000 | 78587.013 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 0 | 825616 | 2006-02-05 | 300 | 716 | NO | NO | YES | NO | NO | NO | JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 20 | 0.34 | X-52 | 52000 |  |  |  |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | YES |  | YES | [38 empty] | CONTRACTOR STRUCK 20" TRANSMISSION LINE WHILE GRADING MUD OFF OF DIRT ROAD. LINE MARKED WITH PERMANENT LINE MARKERS. NO USA REQUEST BY CONTRACTOR. NO INJURIES, INGNITION, OR OUTAGES FROM THIS INCIDENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070028 | 2007-03-07 | SUPPLEMENTAL FINAL | 15931 |  | PUBLIC SERVICE CO OF COLORADO | 200 W/ 6TH ST. P.O. BOX 1819 | SILVERTHORNE | SUMMIT | CO | 80498 | 1515 | 2007-01-04 | 2007 | CRESTED BUTTE | GUNNISON | CO | 81224 | MM 22.73 | 1251+65, PLAT 36-S | 38.492 | -106.550 | ONSHORE | 1 |  |  |  | NO | YES | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41703 | 23406.1988 | 49099.2331 | 4439 | 1865.9032 | 37264 | 47233.3299 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 822842 | 2007-01-04 | 615 | 1636 | NO | NO | NO | NO | NO | NO | RON SMITH | 9702624077 | RON.SMITH@XCELENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 4 | 0.16 | 42 | 42000 | SEAMLESS |  |  |  | UNDER GROUND |  | 48 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | PIPE WAS PARTIALLY FLATTENED BY GUARDRAIL POST BEING DRIVEN DOWN ON TO THE TOP OF THE PIPE IN 1997. THIS WEAKENED THE PIPE OVER THE TIME UNTIL IT RUPTURED. THIS IS THIRD PARTY DAMAGE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070029 | 2007-03-08 16:07 | SUPPLEMENTAL | 31983 |  | ENERGY PARTNERS LTD | 201 ST. CHARLES AVENUE | NEW ORLEANS | PLAQUEMINES | LA | 70170 | 1300 | 2007-02-09 | 2007 |  | PLAQUEMINES | LA |  |  |  | 29°3'25 | 89°18'12 | OFFSHORE |  |  |  | LA | NO | NO | INTRASTATE | N/A |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | YES | NO | 0 |  |  |  | 826059 | 2007-02-09 | 1180 | 1050 | NO | NO | NO | NO | NO | YES | DERRIK MALONE | 2813518801 | DERRIK@THECOMPGROUP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 10 |  | SCHEDULE 40 | [5 empty] | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | UNKNOWN | [6 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | INCOMING 10" HIGH PRESSURE SALES PIPELINE TO VALVE PLATFORM #2, ACROSS CANAL FROM STATION #1 RUPTURED AND CAUGHT FIRE AT VP 2, ENGULFING VP 2 AND PART OF VP 3. RUPTURE SEEMED TO BE DUE TO AN INCREASE IN SYSTEM PRESSURE. (NORMAL 990 TO 1050 PSI). PRESSURE NEVER GOT HIGH ENOUGH TO TRIP PSH'S ON SHUTDOWNS FOR WELLS #192 AND #193 THAT ARE SET AT 1270 PSI, HOWEVER PSL'S TRIPPED SHUTDOWN AT 842 PSI WHEN LINE RUPTURED, WHICH IN TURN SHUT WELLS # 192 AND # 193 IN. FLUID HAD FILLED V2 SCRUBBER AND RELIEF VALVES WERE RELIEVING PRESSURE TO FLARE SCRUBBERS. SCRUBBER AND FLARE SYSTEM COULD NOT HANDLE FLUID RESULTING IN AN INCREASE IN PRESSURE IN THE PIPELINE. (1180 PSI WHEN PIPELINE RUPTURED) ENTIRE FIELD SHUT IN WAS REQUIRED (24 / 27), BLOCKED AND ISOLATED AT ALL POSSIBLE LOCATIONS AND HAD TO LET FIRE BURN ITSELF OUT.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070030 | 2007-03-13 10:24 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1537 | 2007-02-17 | 2007 | CYPRESS | HARRIS | TX | 77429 | 387+33 |  | 29.90085 | 95.73204 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 9 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1079486 | 552434.834 | 746882.0401 | 733486 | 308315.8064 | 110000 | 139428.5714 | 236000 | 299137.6623 | NO | NO | YES | NO | 0 |  | 3 | 0 | 826795 | 2007-02-17 | 580 | 750 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 31 | 0.31 | API 5L | 52000 | DSAW |  | CONWES | 1948 | UNDER GROUND |  | 40 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | A THIRD PARTY CONTRACTOR WAS RELOCATING A D-6 DOZER FROM ONE SIDE OF A PIPELINE RIGHT OF WAY TO THE OTHER, CROSSING TENNESSEE GAS PIPELINE COMPANY¿S 100-2 PIPELINE. THE DOZER SANK IN VERY WET SOIL SUCH THAT THE DOZER TRACK CONTACTED THE 31-INCH DIAMETER PIPELINE. THE PIPELINE BEGAN TO LEAK NATURAL GAS FOLLOWING CONTACT OF THE DOZER TRACK AND RUPTURED LATER WITH GAS IGNITION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070031 | 2007-03-23 08:29 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1258 | 2007-03-20 | 2007 | SUNRAY | MOORE | TX | 68124 | 16.857 |  | 35.974 | -101.82 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE RELEASED GAS TO ATMOSPHERE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58377 | 28258.4743 | 24538.3713 | 58377 | 24538.3713 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 26 | 829782 | 2007-03-20 | 572 | 594 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | RELIEF VALVE ACTIVATED | STEEL |  | NO | NO | NO | PIPELINE | [7 empty] | MODEL 70/270 RELIEF VALVE | ANDERSON-GREENWOOD |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ELECTRICAL POWER TO THE SUNRAY COMPRESSOR STATION WAS LOST DUE TO A POWER LINE BEING STRUCK BY A TRUCK HAULING A LARGE VESSEL ON HIGHWAY FM 119, WHICH GOES BY THE COMPRESSOR STATION. |  | A TRUCK HAULING A LARGE VESSEL, TRAVELING ON HIGHWAY FM 119, WHICH GOES BY THE COMPRESSOR STATION, STRUCK THE ELECTRICAL POWER LINE, WHICH SUPPLIES ELECTRICAL POWER TO THE COMPRESSOR STATION, RESULTED IN A LOSE OF ELECTRICAL POWER TO THE STATION. THE SUCTION PRESSURE TO THE STATION, COMING FROM EL PASO AND CIG WAS CLOSE TO 500 PSIG. AT THE TIME OF THE INCIDENT THERE WAS ABOUT 354 MMCF OF GAS GOING THROUGH THE SUNRAY PLANT, 224 MMCF FROM CIG, 100 MMCF FROM EL PASO AND 30 MMCF FROM BP. THE POWER LOSE CAUSED ALL COMPRESSOR ENGINES TO SHUT DOWN. NORTHERN'S GAS CONTROL IMMEDIATELY NOTIFED ALL THREE CUSTOMERS (CIG, EL PASO AND BP)REQUESTING THEY REDUCE HORSEPOWER AND FLOW DELIVERIES UNTIL THE SUNRAY COMPRESSOR STATION COULD BE PLACED BACK IN SERVICE. THE TXM-15701 SUCTION PRESSURE VERY QUICKLY REACHED 572 PSIG, WHICH IS THE SET POINT OF THE RELIEF VALVE FOR THAT PIPELINE. THE RELIEF VALVE STAYED OPEN, BLOWING GAS TO ATMOSPHERE, FOR APPROXIMATELY 26 MINUTES UNTIL EL PASO AND CIG WERE ABLE TO REDUCE FLOW ENOUGH TO ALLOW IT TO CLOSE. ELECTRICAL POWER WAS RESTORED BY EXEL ENERGY AT 1327 AND THE SUNRAY COMPRESSOR UNITS WERE PUT BACK IN SERVICE. THE RELIEF VALVE FUNCTIONED PROPERLY. THE DOT, TCEQ AND NRC WERE NOTIFIED OF THE GAS RELEASE. A RSPA 7100.2 INCIDENT REPORT IS BEING FILED AS THE GAS LOSS WAS ESTIMATED AT 9,979 MCF AND BASED ON A $5.85 PER MCF THE VALUE OF THE GAS RELEASE EXCEEDED THE REQUIRED $50,000 REPORTING LIMIT. A SUPPLEMENTAL REPORT IS BEING FILED TO CLARIFY THAT THE PART OF THE SYSTEM INVOLVED IN THE INCIDENT (RELIEF VALVE) IS CONSIDERED PIPELINE INSTEAD OF COMPRESSOR STATION. SUPPLEMENTAL/FINAL REPORT - NO FURTHER ACTIONS OR REQUIRED. THIS INCIDENT REPORT IS CONSIDERED COMPLETE AND CLOSED.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070032 | 2008-08-04 | SUPPLEMENTAL FINAL | 999 |  | BREITBURN ENERGY CORP | 515 S. FLOWER STE 4800 | LOS ANGELES | LOS ANGELES | CA | 90071 | 1 | 2007-03-09 | 2007 | LOS ANGELES | LOS ANGELES | CA | 90073 |  |  |  |  | ONSHORE | 4 |  |  |  | NO | NO | INTRASTATE | OTHER | CORROSION RUPTURE, < 0.5 IN. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 34227.2727 | 76051.9481 | 0 | 0 | 60000 | 76051.9481 | 0 | 0 | YES | NO | NO | NO | 0 |  |  |  | 829231 | 2007-03-14 | 200 | 720 | YES | NO | NO | NO | NO | NO | MARTHA L. BROCK | 2132255900 | MBROCK@BREITBURN.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 6 | 0.25 | GRADE B | 2642 | SEAMLESS | BALL & BUTTEFLY | KUKA |  | UNDER GROUND |  | 80 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1969 | NO | [57 empty] | METALURGICAL FAILURE ANALYSIS INDICATED FAILURE WAS DUE TO BOTH EXTERNALAND INTERNAL CORROSION BUT MAINLY EMANATING FROM THE INNER WALL AND CORRODING OUTWARDS. DEPOSITS RICH IN SULFUR SPECIES WERE PRESENT ON BOTH OUTER AND INNER DIAMETER SURFACES OF THE PIPE AND IT WAS CONSIDERED LIKELY THAT THESE DEPOSITS MAY HAVE BEEN ASOCIATED WITH PREVIOUS OILFIELD USAGE OF PIPE AND HAD EVENTUALLY CONVERTED TO ACID CONSTITUENTS IN THE PRESENCE OF MOISTURE, CAUSING CORROSION AND DETERMIOATION OF THE PIPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070033 | 2007-03-30 12:21 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 200 | 2007-03-26 | 2007 | MULLINVILLE | KIOWA | KS | 67109 | 6.82 |  | 37.6107026 | -99.3396722 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120455 | 64750.5436 | 113809.8825 | 45882 | 19286.1838 | 74573 | 94523.6987 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 830355 | 2007-03-26 | 756 | 800 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 26 | 0.31 | 5LX | 48000 | SML |  | NATIONAL TUBE |  | UNDER GROUND |  | 40 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | GIRTH WELD |  |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | ON MARCH 26, 2007 AT APPROXIMATELY 12:28 A.M. BLOWING GAS AND DUST WAS REPORTED BY A PASSERBY LOCATED IN SECTION 25, T27S, RANGE 19W IN KIOWA, COUNTY, KANSAS. IT WAS DETERMINED BY NORTHERN PERSONNEL THAT THE GAS LEAK WAS ON THE M670C KSM20603)PIPELINE. THE LINE WAS REMOVED FROM SERVICE AND THE LEAK AREA WAS INSPECTED WITH THE DETERMINATION THAT THE CAUSE OF THE LEAK WAS A CRACK IN THE GIRTH WELD. ANALYSIS AND REPAIR OF THE PIPELINE IS IN PROGRESS. ADDITONAL INFORMATION AND FINDINGS FROM THE ANALYSIS AND REPAIRS WILL BE REPORTED IN SUPPLEMENTAL REPORTS. SUPPLEMENTAL REPORT: PRELIMINARY MILE POST INDICATED WAS CORRECTED WITH MORE PRECISE MILE POST. SUPPLEMENTAL/FINAL REPORT: REPAIRS WERE MADE BY REPLACING APPROXIMATELY 40 FEET OF PIPE WITH NEW 26 INCH, .375, DSAW, API5L, X65 PIPE AND INSTALLATION OF A 26 INCH X 36 INCH PLIDCO SLEEVE. A FINAL COST OF REPAIR WAS CALCULATED AT $120,455. THE CAUSE OF THE INCIDENT WAS DUE TO A LACK OF FUSION IN THE ROOT PASS DURING CONSTRUCTION. THE LACK OF FUSION CRACKED INTO THE FILL PASSES AND EVENTUALLY PENETRATED THE CAP PASS TO BECOME A LEAK. THE ROOT CAUSE HAS BEEN DETERMINED TO MOSTLY LIKELY BE PIPE BENDING STRESSES ON THE PIPELINE CAUSING THE WELDS TO CONTINUE TO CRACK OVER A LONG PERIOD OF TIME. LONG TERM ADDITIONAL ACTIONS ARE BEING FOLLOWED THROUGH WITH HOWEVER THESE COST ARE CONSIDERED TO BE COST ASSOCIATED WITH THE LONG TERM INTEGRITY OF THE LINE AND NOT REPAIR COSTS. SUPPLEMENT TO FINAL REPORT - THIS SUPPLEMENT IS SUBMITTED TO INDICATE THAT THE CAUSE OF THE INCIDENT WAS A WELD FAILURE ON A GIRTH WELD. LABORATORY ANALYSIS AND CONFIRMATION REVIEW BY P-PIC (A CONSULTANT) INDICATE THAT A CONTRIBUTING FACTOR WAS THE QUALITY OF THE WELD AS IT INDICATED INADEQUATE PENTETRATION IN THE ROOT PASS. WHY IT FAILED AFTER 50 PLUS YEARS IS STILL UNCERTAIN BUT NORTHERN IS INSTALLING SOME GROUND MOVEMENT MONITORING DEVICES TO DETERMINE IS THIS COULD BE A CONTRIBUTING FACTOR. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070034 | 2007-03-14 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1530 | 2007-02-09 | 2007 | [6 empty] | 28.239803N | 91.69452W | OFFSHORE |  | EUGENE ISLAND | 330 |  | YES | NO | INTERSTATE | OTHER | BOAT ANCHOR DAMAGED PIPE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6353821 | 3624494.7157 | 8052974.632 | 826 | 347.2034 | 6352995 | 8052627.4286 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 826088 | 2007-02-09 | 130 | 1440 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT ASSOCIATE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | US STEEL |  | UNDER WATER |  | 0 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | PIPE WAS STRUCK BY ANCHOR FROM THIRD PARTY VESSEL (BOAT). BUBBLES WERE NOTICED WHILE PRESSURIZING THE LINE INDICATING A LEAK. THE PIPELINE WAS IMMEDIATELY SHUT IN AFTER THE CREW NOTICED THE BUBBLES. PIPE WAS REPLACED (1200 FEET).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070035 | 2007-04-03 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1910 | 2007-03-26 | 2007 | SUPERIOR | DOUGLAS | WI | 54880 | 20.27 |  | 46.5669068 | -92.1913489 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203062 | 115837.6409 | 257387.6779 | 0 | 0 | 203062 | 257387.6779 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 830419 | 2007-03-26 | 851 | 1080 | NO | NO | YES | NO | NO | NO | JOHN A. GORMLEY - SR. CORROSION SPECIALIST | 4023987494 | JOHN.GORMLEY@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | [8 empty] | ABOVE GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | OTHER | BARE TRANSITION ZONE | YES | 1965 | NO | [57 empty] | ON MARCH 26, 2007 A PASSERBY, CALLED NORTHERN TO REPORT GAS BLOWING NEAR NORTHERN'S PIPELINE WHERE IT CROSSES STATE HIGHWAY 35 JUST SOUTH OF SUPERIOR, WISCONSIN. THIS IS APPROXIMATELY NINE MILES SOUTH OF SUPERIOR, WI IN SECTION 10, TOWNSHIP 47N, RANGE 14W, DOUGLAS COUNTY, WISCONSIN. NORTHERN PERSONNEL RESPONDED AND FOUND A 1/4 INCH VALVE ON A ONE INCH PRESSURE TAP LEAK. IN ORDER TO REPAIR THE LEAK AND MAINTAIN SERVICE, STOPPLES WERE INSTALLED TO ENABLE ROUTING THE GAS AROUND THE LEAKING ONE INCH PRESSURE TAP PIPE AND ISOLATE THE ONE INCH PIPE. THE ONE INCH PRESSURE TAP WAS EXCAVATED DOWN TO THE PIPELINE AND IT WAS DETERMINED THAT THIS TAP WAS NO LONGER NECESSARY SO THE ONE INCH RISER WAS REMOVED AND A ONCE INCH BULL PLUG WAS INSTALLED. THE BULL PLUG WAS LEAK CHECKED AND PROTECTIVE COATING WAS APPLIED. THE STOPPLES WERE REMOVED AND THE NORMAL OPERATIONAL SERVICE WAS RESTORED. THIS REPAIR IS BEING REPORTED AS THE UTILIZATION OF CONTRACTOR AND THE REQUIREMENT TO UTILZIE STOPPLING IS EXPECTED TO EXCEED THE $50,000 REPORTING THRESHOLD. NO FURTHER REPAIRS OR ACTIONS ARE REQUIRED AND THIS REPAIR IS CONSIDERED COMPLETE. ONCE ALL COST ASSOCIATED WITH THE REPAIR ARE CALCULATED A SUPPLEMENTAL/FINAL REPORT WILL BE COMPLETED. SUPPLEMENTAL/FINAL REPORT - ENTERED UPDATE TO FINAL COST WHICH WAS $203,062.00. NO FURTHER ACTIONS ARE PLANNED OR NECESSARY. ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA UPDATED BY PHMSA ON 12/3/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070036 | 2007-02-26 | SUPPLEMENTAL | 31994 |  | PANTHER PIPELINE LTD | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1530 | 2006-12-18 | 2006 |  | MAAGORDA | TX |  |  |  | N28.28.239 | W96.00.332 | OFFSHORE |  | BRAZOS | 480 L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72500 | 42166.3774 | 92139.9038 | 2500 | 995.935 | 70000 | 91143.9689 | 0 | 0 | NO | NO | NO | NO | 0 |  | 12 | 0 | 821493 | 2006-12-18 | 750 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | APISL | 52 | ERW |  | UNK | 1958 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | INCIDENT DESCRIPTON - ON OR ABOUT DECEMBER 18, 2006, PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN SHUT OFF INTO THE SEGMENT OF PIPELINE HAVING THE LEAK. THE LEAK WAS CLAMPED OFF ON 12/31/06 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 1/1/07.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070037 | 2007-04-03 | SUPPLEMENTAL FINAL | 15105 |  | PANHANDLE ENERGY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 815 | 2007-02-16 | 2007 | HLSTEAD | HARVEY | KS | 67056 | 8.6 | 983+98 | 37.97 N | 97.48 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BROKEN 1/2 PIPE NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205800 | 100087.8075 | 91081.44 | 200400 | 84236.7647 | 5400 | 6844.6753 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 25 | 826712 | 2007-02-16 | 750 | 900 | NO | NO | NO | NO | YES | NO | BRIAN JIMENEZ ASSOCIATE ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | OTHER | 1/2PIPE NIPPLE ON MAINLINE GATE VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 0.5 | 0.19 | UNK | 24000 | UNK | GATE | GROVE 26 | 1963 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | PIPE NIPPLE BROKEN FROM CATTLE RUBBING ON 1/2 VALVE AND NIPPLE ON VENT OF MAIN LINE VALVE. |  | CATTLE ENTERED THE GATE VALVE COMPLEX AND RUBBED ON A 1/2INCH VENT VALVE ASSEMBLY CAUSING A THREAADED PIPE NIPPLE TO BREAK ALLOWING GAS TO ESCAPE OUT THE BODY VENT. LEAKAGE WOULD NOT ALLOW FOR SAFE OPERATION OF THE BLOCK VALVE. HAVEN 300 LINE WAS SHUT IN AND BLOWN DOWN FROM THE HAVEN COMPRESSOR STATION TO THE NEXT SECTIONALIZIGN BLOCK VALVE TO FACILITATE REPAIRS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070038 | 2007-04-03 14:12 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 1142 | 2007-03-29 | 2007 | BERESFORD | LINCOLN | SD | 57004 | 62.08 |  | 43.15686 | -96.70907 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476430 | 271004.1858 | 596265.7895 | 9000 | 3783.0882 | 465930 | 590581.4026 | 1500 | 1901.2987 | NO | NO | NO | NO | 0 |  | 1 | 0 | 830729 | 2007-03-29 | 400 | 446 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1932 | 14 | 0.25 | 5L | 25000 | ERW |  | REPUBLIC |  | UNDER WATER |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1971 | NO | [57 empty] | AT APPROXIMATELY 11:42 A.M. ON MARCH 29, 2007 A LEAK ON THE SIOUX FALLS 14 INCH MAINLINE, APPROXIMATELY 20 MILES SOUTH OF HARRISBURG, SOUTH DAKOTA, WAS DISCOVERED BY A NORTHERN NATURAL GAS COMPANY EMPLOYEE. THE EMPLOYEE WAS CONDUCTING A LINE LOCATE WHEN HE NOTICED 5-6 BUBBLES IN A CREEK, IMMEDIATELY ABOVE NORTHERN'S PIPELINE. THIS IS SDM-90201 AT APPROXIMATE MILE POST 62.08, SECTION 2 TOWNSHIP 96N, RANGE 50W, LINCOLN COUNTY, S.D.. THE LINE WAS INSTALLED IN 1932 AND IS DRESSER COUPLED AND ACETYLENE WELDED AT DIFFERENT LOCATIONS. THE LINE HAS A 446 PSIG MAOP AND WAS OPERATING AT APPROXIMATELY 400 PSIG WHEN THE LEAK WAS DISCOVERED. THE AREAS IS A CLASS 1 LOCATION AND THIS IS NOT A SAFETY RELATED CONDITION. PRESSURE ON THE LINE WAS REDUCED AND IS BEING MAINTAINED AT 275 PSIG PENDING REPAIRS. THE AREA HAS RECEIVED APPROXIMATELY 3 1/2 INCHES OF RAIN AND HAS INCURRED SOME SNOW. A CONTRACTOR AND MATERIALS HAVE BEEN ASSEMBLED AND HOPE TO BE ABLE TO ACCESS THE AREA TO INVESTIGATE THE LEAK ON APRIL 4, WEATHER PERMITTING. THIS ORIGINAL INCIDENT REPORT IS BEING FILED AS COST ARE EXPECTED TO EXCEED THE $50,000 REPORTING THRESHOLD LEVEL. A FOLLOW UP SUPPLEMENTAL AND FINAL REPORT WILL BE FILED WITH UPDATED FINDINGS AS THEY BECOME KNOWN. SUPPLEMENTAL/FINAL REPORT: REPAIRS WERE COMPLETED ON MAY 15, 2007 BY REPLACING APPROXIMATELY 444 FEET OF 14 INCH OUTSIDE DIAMETER X 0.375 WALL THICKNESS. THE CAUSE OF THE LEAK WAS DETERMINED TO BE EXTERNAL CORROSION CAUSED BY LOCALIZED, GALVANIC CORROSION.TOTAL COST OF REPAIRS INCLUDING DAMAGES, LABOR, MATERIALS, ETC ARE $476,430.00. THIS INCIDENT IS CONSIDERED CLOSED WITH NO FURTHER ACTIONS PLANNED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070039 | 2007-04-04 10:15 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1325 | 2007-03-10 | 2007 |  |  |  |  | 0.00 |  | 29.435410 | -93.013215 | OFFSHORE |  | WEST CAMERON | 141 |  | YES | NO | INTERSTATE | OTHER | FITTING ON VALVE DAMAGED BY SHRIMP TRAWL NET | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 85568.1818 | 190129.8701 | 0 | 0 | 150000 | 190129.8701 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 828782 | 2007-03-10 | 950 | 1440 | YES | NO | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12.75 | 0.38 | API 5L | 52000 |  | ANSI 600 BALL VALVE | CAMERON | 1967 | UNDER WATER |  | 38 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A SUBSEA VALVE ON TENNESSEE GAS PIPELINE'S (TGP) 507K-800 PIPELINE APPEARED TO HAVE BEEN DAMAGED BY A SHRIMP TRAWLER NET. PIECES OF NETTING WERE FOUND ON THE BROKEN FITTING. THE NET APPARENTLY SNAGGED ON A GREASE FITTING, BREAKING THE FITTING AND RESULTING IN A VERY SMALL GAS RELEASE. REPAIR WAS MADE BY INSERTING A PLUG. THE VALVE ASSEMBLY WAS COVERED WITH SAND BAGS AND THE PIPELINE WAS PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070040 | 2007-04-05 11:24 | SUPPLEMENTAL FINAL | 3 |  | ACADIAN GAS PIPELINE SYSTEM | 338 WAVERLY ROAD | THIBODAUX | LAFOURCHE | LA | 70301 | 1500 | 2007-03-09 | 2007 | MORGAN CITY | ST. MARTIN | LA |  | MILE MARKER #31 |  | N 29 53.779 | W 91 19.363 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348075 | 198258.6152 | 438231.201 | 3500 | 1471.201 | 344575 | 436760 | 0 | 0 | NO | NO | NO | NO | 0 |  | 24 | 0 | 828727 | 2007-03-09 | 800 | 970 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 20 | 0.31 | API 5L | 52000 | ERW |  |  |  | UNDER WATER |  | 84 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1966 | YES | 17 | 0 | [55 empty] | AN EXISTING SEAL CLAMP STARTED LEAKING AROUND THE AREA OF THE SEAL AND RELEASED NATURAL GAS INTO THE WATER. THE LOCATION OF THE LEAK WAS IN A SECLUDED CANAL IN THE ATCHAFALAYA BASIN. THE PIPELINE WAS SECURED, THE PRESSURE WAS REDUCED ON THE PIPELINE WITH THE USE OF A COMPRESSOR, AND THE EXISTING SEAL CLAMP WAS REMOVED AND A NEW SEAL CLAMP WAS INSTALLED. NOTE: CORRECTED #8(B) MAOP TO 970 PSIG.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070041 | 2007-04-10 10:14 | SUPPLEMENTAL FINAL | 31264 |  | AQUILA NETWORKS | 1815 CAPITOL AVENUE | OMAHA | DOUGLAS | NE | 68102-4914 | 1700 | 2007-03-06 | 2007 | LYONS | RICE | KS | 67554 | T1A TOBIAS GATE VALVE | 7+80 | 38*16'37.443 | -98*9'55.725 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 4 | 8 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 28425 | 15478.6441 | 28806.4742 | 8526 | 3583.8456 | 19899 | 25222.6286 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 5 | 830401 | 2007-03-26 | 182 | 266 | NO | NO | YES | NO | NO | NO | JERRY WATKINS | 3169411642 | JERRY.WATKINS@AQUILA.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1937 | 8 | 0.2 | UNKNOWN | 24000 | ERW | N/A | UNKNOWN |  | OPEN DITCH |  | 28 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | NO |  | NO | [57 empty] | LANDOWNER HAD CALLED IN A LEAK IN HIS WHEAT FIELD. THE CONSTRUCTION CREW EXCAVATED AND FOUND AN EXISTING LEAK CLAMP LEAKING (ESTIMATED INSTALLATION PRIOR TO 1971). THE CREW STARTED TO LOOSEN BOLTS ON CLAMP TO REPLACE IT AND THE LINE RUPTURED ALONG ITS SEAM. TWO CONTRACT EMPLOYEES WERE INJURED AND TAKIN TO THE HOSPITAL WITH NON-LIFE THREATENING INJURIES. THE GAS SUPPLY WAS RE-ROUTED AND SHUT DOWN. THE DEFECTIVE PIPE WAS CUT OUT AND REPLACED. THE PIPELINE WAS PUT BACK INTO NORMAL OPERATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070042 | 2007-04-12 | SUPPLEMENTAL FINAL | 6580 |  | GRANITE STATE GAS TRANSMISSION INCORPORATED | 1700 MACCORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 310 | 2007-04-06 | 2007 | SACO | YORK | ME | 04072 |  | 3545+04 |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 684.5455 | 1521.039 | 0 | 0 | 1200 | 1521.039 | 0 | 0 | YES | YES | NO | YES | 100 | THREAT TO THE PUBLIC | 1 | 5 | 831483 | 2007-04-06 | 380 | 492 | NO | NO | NO | NO | YES | YES | DAVID ANDERSON | 7242232766 | DDANDERSON@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1991 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | INCIDENT REPORTED DUE TO OPERATOR JUDGEMENT AS A SIGNIFICANT EVENT PER 191.3. ON APRIL 6, 2007, THE CONTROL AND MONITOR REGULATION AT THE MOODY ROAD M&R STATION FAILED OPEN RESULTING IN OVERPRESSURE OF DOWNSTREAM LDC FACILITIES. APPROXIMATELY 100 PEOPLE WERE EVACUATED. THERE WERE NO INJURIES. THERE WAS NO PROPERTY DAMAGE TO GRANITE STATE FACILITES. MALFUNCTION CAUSED BY ICE IN PILOT.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070043 | 2007-04-17 | SUPPLEMENTAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1207 | 2007-01-08 | 2007 | MATAGORDA | MATAGORDA | TX |  |  |  | N28 29.00 | W95 59.700 | OFFSHORE |  | BRAZOS | 480L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72500 | 41141.9898 | 89778.1306 | 2500 | 1050.8578 | 70000 | 88727.2727 | 0 | 0 | NO | NO | NO | NO | 0 |  | 12 | 0 | 824749 | 2007-01-26 | 750 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER VP-MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API 5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON ABOUT JANUARY 8, 2007, PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 480-L. THE LEAK WAS A SUB SEA PINHOLE LEAK. ALL GAS SUPPLY WAS SHUT OFF INTO SEGMENT OF PIPELINE HAVING THE LEAK. THE LEAK WAS CLAMPED OFF ON 1/26/2007 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 1/26/07.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070045 | 2007-04-19 17:31 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1300 | 2007-03-13 | 2007 | [6 empty] | 28 7.46' N | 96 39.81' W | OFFSHORE |  | MATAGORDA | 628 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98874 | 56154.8496 | 122891.1831 | 2874 | 1208.0662 | 96000 | 121683.1169 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | N/A |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7135953612 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 | N/A | N/A | N/A |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1975 | NO | [57 empty] | RRC CALL-IN NO.: 07-CA-436. LEAK WAS DISCOVERED AS REPORTED. DIVERS WERE DISPATCHED ON 3/15/07. WEATHER PREVENTED SECURING THE LEAK WITH PLIDCO SPLIT CLAMP UNTIL 4/2/07. CLAMP WAS SECURED, LEAK STOPPED, AND LINE RUN TO ENSURE NO OTHER LEAKS. DIVERS WERE RELEASED. THIS IS A PRELIMINARY REPORT WAITING ON GAS LOSS ESTIMATES(AT THIS TIME THOUGHT TO BE TOO SMALL TO MEASURE). NO INJURIES OR THIRD PARTY PROPERTY DAMAGE OCCURED.FINALIZED ON 9/19/2007 BY ADDING THE GAS LOSS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070046 | 2007-04-24 14:19 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1400 | 2006-11-08 | 2006 | [8 empty] | OFFSHORE |  | MATAGORDA | 628 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174900 | 102490.0389 | 227729.7165 | 0 | 0 | 174900 | 227729.7165 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | N/A |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7135953612 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 | N/A | N/A | N/A |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | CORROSION PIT | YES | 1975 | NO | [57 empty] | RAILROAD COMMISSION OF TEXAS CALL-IN NO. 07-CA-172. A LEAK WAS DISCOVERED ON 11/8/06. THE LEAK WAS SMALL AND WAS NOT CONSIDERED DANGEROUS. VESSELS AND DIVERS WERE NOT AVAILABLE TO SABCO TO REPAIR THE LEAK UNTIL 12/31/2006 WHEN DIVERS WERE DISPATCHED TO ASSESS THE SITUATION. THEY WERE NOT ABLE TO REPAIR THE LEAK DUE TO VESSEL'S LIMITED TIME. A SECOND GROUP OF DIVERS WERE DISPATCHED ON 1/4/2007. PLIDCO SLEEVE CLAMPS WERE INSTALLED ON THREE LEAKS AND ALL LEAKS IN THE VICINITY OF THE REPORTED FIRST LEAK WERE REPAIRED ON 1/10/2007. INVESTIGATION OF CAUSE: THIS LINE HAS BEEN USED AS A SALES LINE BY THE PREVIOUS OPERATOR PRIOR TO DECEMBER OF 1996 WHEN SABCO ACQUIRED THE OPERATION. THERE MAY HAVE BEEN CORROSIVE CONSTITUENTS IN THE PRODUCED GAS, WHICH WE CANNOT SUBSTANTIATE BECASUE WE DON'T HAVE ANY RECORDS OF IT. WE ANALYZED THE BUYBACK GAS AFTER WE INSTALLED THE NEW LINE THAT REPLACES THE EXISTING FAULTY LINE, BUT THE CHEMICAL ANALYSIS DATA DOES NOT INDICATE THE PRESENCE OF ANY CORROSIVE MATERIAL.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070047 | 2007-02-12 09:56 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 930 | 2007-01-15 | 2007 |  |  | LA |  |  |  | 29 16.89 | 92 21.75 | OFFSHORE |  | VERMILLION | 76 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525000 | 295169.3405 | 623095.0789 | 50000 | 21017.1569 | 475000 | 602077.9221 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 823708 | 2007-01-15 | 870 | 1253 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 36 | 0.56 |  | 60000 |  |  |  | 1980 | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | UNKNOWN |  |  |  |  | MATERIAL DEFECT |  | NO | YES | 12 | 1 | 1980 | WATER |  | 8 | 1500 | [12 empty] | LEAK DEVELOPED IN GIRTH WELD. CAUSE UNKNOWN. LEAK CLAMP USED TO REPAIR THE LEAK.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070048 | 2007-04-27 19:05 | SUPPLEMENTAL FINAL | 12576 |  | CENTERPOINT ENERGRY - MISSISSIPPI RIVER TRANSMISSION CORP. | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1327 | 2007-03-30 | 2007 | GRANITE CITY | MADISON | IL | 62040 |  | 31 | 38.74869 | 90.11641 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65646 | 31777.1691 | 27593.8456 | 65646 | 27593.8456 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | A30845 | 2007-03-30 | 391 | 400 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1989 | [5 empty] | PILOT RELIEF VALVE | ANDERSON GREENWOOD | 1989 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | PILOT RELIEF VALVE | [10 empty] | RELIEF VALVE MAINTENANCE WAS PERFORMED ON FEBRUARY 15, 2007 ON RELIEF VALVE RR9335 ON LINE A-171. THE TECHNICIAN SET THE RELIEF VALVE TO RELIEVE FULLY AT 416 PSIG (104% OF 400 MAOP). ON MARCH 29, 2007 SYSTEM CONTROL, BECAUSE OF DELIVERY DEMAND, INCREASED THE FLOW RATE ON LINE A-171 WHICH RESULTED IN A CORRESPONDING PRESSURE INCREASE TO APPROXIMATELY 390 PSIG. ON MARCH 30, 2007 SYSTEM CONTROL RECEIVED A CALL FROM A MEMBER OF THE PUBLIC TO REPORT HEARING A GAS RELEASE. SYSTEM CONTROL CALLS FIELD PERSONNEL TO RESPONSE AT 13:27 AND THEY ARRIVED AT THE LOCATION AND ISOLATED THE RELIEF VALVE AT 13:40. THE FIELD TECHNICIAN CHECKED THE RELIEF VALVE AND FOUND IT SIT AT 416 PSIG. THE RELIEF VALVE WAS THEN CHECKED AND IT WAS FOUND THAT THE RELIEF VALVE STARTED TO SEEP AT ABOUT 395 PSIG AND FULLY RELIEVED AT 416 PSIG. SYSTEM CONTROL SCADA RECORDS SHOWS THE HIGHEST PRESSURE DURING THIS TIME TO BE APPROXIMATELY 391 PSIG.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070049 | 2007-05-01 | ORIGINAL FINAL | 31852 |  | REGENCY GAS SERVICES | 201 OAK STREET | DUBACH | LINCOLN | LA | 71235 | 135 | 2007-03-18 | 2007 | BRYCELAND | BEINVILLE | LA | 71088 | EAST SIDE COMPRESSOR STAT |  | 32.40972.N | 92.97492.W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 7687.2545 | 10528.4184 | 10000 | 4203.4314 | 4990 | 6324.987 | 0 | 0 | NO | NO | YES | NO | 0 |  | 2 | 40 | 829648 | 2007-03-19 | 900 |  | NO | NO | NO | NO | NO | NO | ANGELA MORGAN | 9032436541 | ANGELA.MORGAN@REGENCYGAS.COM | TRANSMISSION | OTHER | COMPRESSOR |  |  | NO | NO | NO | COMPRESSOR |  | 2005 | [8 empty] | INSIDE/UNDER BUILDING |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | VALVE CAP | [8 empty] | MATERIAL DEFECT |  |  | NO | [17 empty] | STUD BOLT ON VALVE CAP FAILED CYLINDER DISCHARGE BOTTLE |  | STUD BOLT FAILURE RESULTED IN RELEASE OF NATURAL GAS INSIDE COMPRESSOR BUILDING. SUBSEQUENTLY IGNITED THE NATURAL GAS INSIDE THE BUILDING CAUSING THE EXPLOSION AND FIRE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070050 | 2007-05-02 18:23 | ORIGINAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 20 E. GREENWAY PLAZA | HOUSTON | HARRIS | TX | 77046 | 1930 | 2007-04-03 | 2007 | INEZ | VICTORIA | TX | 77968 | 44.130 | 2330+07 | 28.76864 | 96.79771 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK UNDER SLEEVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68404 | 36900.4257 | 65904.0985 | 24552 | 10320.2647 | 43852 | 55583.8338 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 831249 | 2007-04-03 | 455 | 780 | NO | NO | YES | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BOARDWALKPIPELINES.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 30 | 0.38 | API-5LX | 52000 | ELECTRIC FLASH WELD | N/A | A. O. SMITH | 1952 | UNDER GROUND |  | 34 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ASSUMED CRACK IN BODY OF PIPE UNDER HARD SPOT SLEEVE |  | COMPANY WAS NOTIFIED OF A POSSIBLE RELEASE ON THE PIPELINE FROM ANOTHER GAS COMPANY WHO HAS A PARALLELING PIPELINE. UPON ARRIVAL, GAS DETECTION EQUIPMENT VERIFIED SMALL GAS RELEASE. AREA WAS ISOLATED AND SECURED. RESEARCH FROM ILI LOGS INDICATED A HARD SPOT SLEEVE AT THE LOCATION. THE ASSUMPTION WAS MADE THAT A CRACK HAD OCCURRED IN THE HARD SPOT UNDER THE SLEEVE. REPAIR WAS MADE PER O&M REPAIR CRITERIA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070051 | 2007-05-07 11:23 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | -77002 | 1645 | 2007-04-12 | 2007 | [6 empty] | 29.093786 | -89.550 | OFFSHORE |  | WEST DELTA | 47 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435000 | 243828.4314 | 509017.1569 | 50000 | 21017.1569 | 385000 | 488000 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 832056 | 2007-04-12 | 975 | 1264 | NO | YES | NO | NO | NO | NO | KENNETH PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 30 | 0.5 | API 5L | 60000 |  |  | US STEEL | 1979 | UNDER WATER |  | 108 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | MMS NOTIFIED TGP OF BUBBLES IN THE WATER IN WEST DELTA BLOCK 47. UPON INVESTIGATION, TGP DETERMINED THE LEAK WAS COMING FROM ITS 527A-300 PIPELINE. LINE WAS ISOLATED AND BLOWN DOWN. DIVERS WERE DISPATCHED TO UNCOVER THE PIPELINE AND INSTALL A PLIDCO REPAIR CLAMP. REPAIR COMPLETED 4/18/07 WITH LINE BEING PLACED BACK INTO SERVICE. SINCE THE REPAIR WAS BY CLAMP AND NO PIPE WAS REMOVED FOR ANALYSIS, THE EXACT CAUSE OF THE LEAK COULD NOT BE ASCERTAINED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070052 | 2007-05-07 12:42 | SUPPLEMENTAL FINAL | 15329 |  | THE PEOPLES GAS LIGHT AND COKE COMPANY | 130 E RANDOLPH DRIVE | CHICAGO | COOK | IL | 60601 | 1225 | 2007-04-11 | 2007 | FISHER | CHAMPAIGN | IL | 61843 |  |  | 40.2671414 | -88.4212695 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | 32603.8324 | 51476.9544 | 32000 | 13450.9804 | 30000 | 38025.974 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 831939 | 2007-04-11 | 1740 | 2000 | NO | YES | NO | NO | NO | NO | THOMAS L. PURACCHIO, MANAGER GAS STORAGE | 2178977120 | TLPURACCHIO@INTEGRYSGROUP.COM | TRANSMISSION | OTHER | 6 | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 12.75 | 0.38 | API Y60 | 60000 | N/A | N/A | N/A |  | UNDER GROUND |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1967 | NO | [57 empty] | ON WEDNESDAY, APRIL 11, 2007 AT APPROXIMATELY 12:25 PM A NATURAL GAS LEAK WAS DISCOVERED ON A SECTION OF TRANSMISSION SYSTEM PIPING LOCATED NEAR THE NORTHWEST CORNER OF THE INTERSECTION OF COUNTY ROADS, 2700 NORTH AND 200 EAST, IN CHAMPAIGN COUNTY. COMPANY PERSONNEL IMMEDIATELY CLOSED VALVES AND ISOLATED THE SECTION OF PIPING THAT WAS SUSPECTED OF LEAKING. THE PIPING SECTION WAS BROUGHT TO 0 PSIG WITHIN AN HOUR BY VENTING GAS INTO THE ATMOSPHERE THROUGH CONNECTIONS AT A NEARBY GAS STORAGE WELL. THE LEAK CAUSED NO INJURIES AND THERE WAS NO DAMAGE TO ANY PROPERTY OTHER THAN THE COMPANY FACILITIES THAT WERE INVOLVED. THE AREA OF THE LEAK WAS EXCAVATED ON MONDAY, APRIL 16, 2007 AND THE LEAK WAS FOUND TO BE ASSOCIATED WITH A PIPELINE DRIP THAT WAS ATTACHED TO THE PIPELINE. THE LEAK WAS LOCATED ON A 6" 90 DEGREE ELBOW OF THE DRIP. A METALLURIGICAL ANALYSIS REVEALED THAT THE LEAK WAS DUE TO MICROBIAL CORROSION ON THE INTERIOR OF THE ELBOW. 09/27/2012: UPDATED FINAL REPORT TO INCLUDE COORDINATES FOR LOCATION OF INCIDENT. TDC
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070053 | 2007-05-08 19:22 | ORIGINAL FINAL | 12874 |  | QUESTAR PIPELINE COMPANY | P.O. BOX 45360 | SALT LAKE CITY | SALT LAKE | UT | 84145 | 1037 | 2007-04-08 | 2007 | PRICE | CARBON | UT | 84501 | 6.7 MI W OF STATE HWY 6 | NA | 39.653255 | -110.979795 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 58088.2353 | 50441.1765 | 120000 | 50441.1765 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 831646 | 2007-04-08 | 700 | 1440 | YES | YES | NO | NO | NO | NO | TROY D. SORENSEN | 8013243152 | TROY.SORENSEN@QUESTAR.COM | TRANSMISSION | OTHER | ALLEN-BRADLEY PLC | OTHER | ELECTRONICS | NO | NO | NO | COMPRESSOR |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ALLEN-BRADLEY | 2001 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | THE ALLEN-BRADLEY PLC ON THE COMPRESSOR PACKAGE FAILED. AS A RESULT OF THIS HARDWARE FAILURE THE COMPRESSOR SHUT DOWN AND THE VENT VALVE WAS OPENED. AS A RESULT OF THE COMPRESSOR PACKAGE PLC FAILURE COMMUNICATION BETWEEN GAS CONTROL AND THE COMPRESSOR WAS LOST. GAS CONTROL NOTICED A GRADUAL PRESSURE CHANGE AND DISPATCHED PERSONNEL TO THE SITE. ONCE ON SITE THE RELEASE OF GAS WAS STOPPED BY MANUALLY SHUTTING VALVES. HOWEVER, APPROXIMATELY $120,000 OF GAS HAD VENTED FROM THE ESTIMATED TIME OF FAILURE TO THE TIME THE DISCHARGE WAS STOPPED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070054 | 2007-05-15 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION COMPANY LLC | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056-5306 | 1100 | 2007-04-03 | 2007 | DELESPINE | BREVARD | FL | 32927 | MP 5.2 | 273+19 | 28.27'54N | 80.26'35W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369615 | 185433.4742 | 219252.5233 | 294204 | 123666.6324 | 75411 | 95585.8909 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 15 | 831214 | 2007-04-03 | 843 | 1087 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MARIVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12 | 0.28 | API 5LX | 42000 | ERW |  | YOUNGSTOWN SHEET AND TUBE | 1968 | UNDER GROUND |  | 32 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | SEPARATING USABLE FILL FROM CONSTRUCTION DEBRIS | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | PIPE WAS STRUCK AND PENETRATED BY THE TOOTH FROM THE BACKHOE BUCKET FROM A THIRD PARTY OPERATED TRACK BACKHOE. INVESTIGATION REVEALED THAT THE CONTRACTOR HAD STRUCK AND DAMAGED THE LINE IN SEVERAL LOCATIONS BOTH UPSTREAM AND DOWNSTREAM OF THE PUNCTURE. APPROXIMATELY 35 FEET OF PIPE WAS FOUND TO BE DAMAGED AND WAS REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070055 | 2007-08-08 | SUPPLEMENTAL FINAL | 12732 |  | MONTEZUMA NATURAL GAS DEPT, CITY OF MONTEZUMA,IOWA | 501 EAST MAIN STREET | MONTEZUMA | POWESHIEK | IA | 50171 | 2354 | 2007-04-13 | 2007 | MONTEZUMA | POWESHIEK | IA | 50171 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | 2 INCH PIPE ABOVE GROUND WAS BROKEN OFF | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63519 | 35108.1435 | 69464.1987 | 13041 | 5481.6949 | 43624 | 55294.8364 | 6854 | 8687.6675 | NO | NO | NO | YES | 36 | COMPANY POLICY | 5 | 45 | 832184 | 2007-04-14 | 575 | 863 | NO | YES | NO | NO | NO | NO | ELDON SNOOK, SUPERINTENDENT | 6416232238 | MONTEGAS@ZUMATEL.NET | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1996 | 2 | 0.15 | API 5L | 25000 | CONTINUOUS BUTT WELD |  | UNK |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A VEHICLE TRAVELING EAST ON POWESHIEK COUNTY HIGHWAY V13 TURNED NORTH ONTO MONTEZUMA SOUTH 8TH STREET. THE DRIVER LOST CONTROL OF THE VEHICLE AND FLEW APPORXIMATELY 100 FEET OVER THE ROAD SIDE DITCH AND STRUCK AN ABOVE GROUND METERING STATION THAT WAS LOCATED AT THE EAST RIGHT OF WAY FENCE. THE DRIVER OF THE VEHICLE HAD A BLOOD ALCHOL CONTENT ABOVE THE LEGAL LIMIT. THE IMPACT OF THE VEHICLE SHEARED THE 2" PIPE OF THE METERING STATION AND CAUSED A RELEASE OF NATURAL GAS. THERE WAS NO IGNITION OF GAS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070056 | 2007-05-21 23:26 | SUPPLEMENTAL FINAL | 32099 |  | ENERGY TRANSFER COMPANY | 800 E. SONTERRA BLVD. #400 | SAN ANTONIO | BEXAR | TX | 78258 | 1700 | 2007-04-21 | 2007 | MAYPEARL | ELLIS | TX | 76064 | 0+240 |  | N 32 17 56.2 | W 97 01 11.1 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | COMPRESSOR FIRE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850000 | 484886.3636 | 1077402.5974 | 0 | 0 | 850000 | 1077402.5974 | 0 | 0 | NO | YES | NO | YES | 36 | PRECAUTIONARY | 2 | 0 | 833018 | 2007-04-21 | 725 | 1050 | NO | YES | NO | NO | NO | NO | DANNY NICHOLS | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | COMPRESSOR ENGINE | OTHER | VARIOUS COMPRESSOR PARTS | NO | NO | NO | COMPRESSOR |  | 2004 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ENGINE OIL LEAK THAT IGNITED BY UNKNOWN SOURCE, RESULTING IN MELTING OF FUEL GAS REGULATOR. |  | CAUSE OF FIRE IS UNDETERMINED, BUT IS SUSPECTED TO HAVE STARTED BY A SMALL ENGINE OIL LEAK ON THE 7042 WAUKESHA COMPRESSOR (1280 HP). AS A RESULT OF AN UNDETERMINED IGNITION SOURCE, THE REGULATOR CONTROLLING THE FUEL GAS TO THE COMPRESSOR MELTED RELEASING GAS. THE TEXAS RAILROAD COMMISSION WAS NOTIFIED OF THE INCIDENT ON 4/21/2007 @ 6:30 PM. THE NATIONAL RESPONSE CENTER WAS NOTIFIED ON 4/21/2007 @ 6:35 PM (833018 WILSON) NUMBER OF EVACUATED PEOPLE WERE ESTIMATED; LOCAL FIRE DEPARTMENT REPORT STATED 12 HOMES. FINAL UPDATE: ADDED $250,000 DAMAGES TO INCLUDE OVERHEAD COMPRESSOR COVER, ELECTRICAL AND OVERHEAD CRANE. IGNITION SOURCE REMAINS UNDETERMINED, BUT IS BELIEVED TO INVOLVE THE HIGH TEMPERATURE HEAT SURFACE OF THE COMPRESSOR, IGNITING THE OIL RESIDUE, RESULTING IN DAMAGE TO THE FUEL GAS REGULATOR.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070057 | 2007-05-23 | SUPPLEMENTAL FINAL | 32099 |  | ENERGY TRANSFER COMPANY | 800 E. SONTERRA BLVD. #400 | SAN ANTONIO | BEXAR | TX | 78258 | 705 | 2007-04-23 | 2007 | FORT WORTH | TARRANT | TX | 76112 | 272.84 |  | N 32.73020 | W 97.22022 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | RELEASE OF GAS FROM RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235889 | 124552.7746 | 200817.0419 | 115889 | 48713.1458 | 0 | 0 | 120000 | 152103.8961 | YES | YES | NO | NO | 0 |  | 2 | 25 | 833123 | 2007-04-23 | 753 | 753 | YES | NO | NO | NO | NO | NO | DANNY NICHOLS | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | RELIEF VALVE | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2007 |  |  | ANSI 600 |  | FLANGED | MERCER 9500 RELIEF VALVE (6 | MERCER VALVE CO., INC. | 2007 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | VENTED GAS BY CORRECT OPERATION OF RELIEF VALVE ENCOUNTERED UNEXPECTED IGNITION SOURCE |  | MULTIPLE OCCURRENCES CONTRIBUTED TO THIS EVENT; THE HANDLEY POWER PLANT WAS NOT ON-LINE, THEREFORE GAS WAS NOT BEING DELIVERED TO THE POWER PLANT, FROM THE PIPELINE. ALSO, THE ETC COMPRESSOR #1 AT OUR MAYPEARL COMPRESSOR STATION TRIPPED OFF-LINE. THIS UNIT WAS BEING USED TO MOVE GAS FROM HANDLEY TO MAYPEARL; CONSEQUENTLY THIS CAUSED THE PIPELINE TO START BUILDING PRESSURE. THE 9500 MERCER SAFETY RELIEF VALVE, LOCATED AT THE HANDLEY STATION OPERATED CORRECTLY AND RELIEVED GAS, AT 753 PSIG, TO THE ETC SILENCER/BLOWDOWN STACK LOCATED IN THE ETC HANDLEY METER STATION YARD. THE GAS WAS EMITTED TO THE ATMOSPHERE. THE GAS ENCOUNTERED AN UNEXPECTED IGNITION SOURCE AND IGNITED, CAUSING ENOUGH HEAT SOURCES TO MELT A POWER LINE THAT FELL TO THE GROUND. AFTER A THOROUGH INVESTIGATION, IT IS BELIEVED THAT THERE WAS ARCHING AROUND THE AREA OF AN INSULATOR IN THE POWER LINE BEFORE THE RELEASE OF GAS, CAUSING THE GAS TO IGNITE. THE ETC BLOWDOWN STACK IS DESIGNED TO SPECIFICALLY DISPERSE THE RELEASE OF GAS WITHOUT INCIDENT AND DESIGNED TO PREVENT THE POSSIBILITY OF IGNITION. * TOTAL TIME UNTIL AREA WAS MADE SAFE INCLUDED TIME FOR ELECTRICITY TO BE DISCONNECTED. GAS OFF AND FIRE OUT @ 7:55 AM REPORTED TO TRRC @ 8:05 AM ON 4/23/07 REPORTED TO NRC @ 8:50 AM ON 4/23/07 (NRC 833123) OFFICER MALLICK FINAL UPDATE: 01/04/2010 ADDITIONAL MEASURES TAKEN TO PREVENT SIMILIAR REOCCURRENCES: 1. RELOCATED RV DISTANCES AWAY FROM SIMILIAR POWER SOURCES, AS SECONDARY OPP. 2. INSTALLED INDIVIDUAL PRIMARY PRESSURE CONTROL DEVICES AT EACH PRODUCER TIE-IN (INLETS)THAT WILL SHUT-IN EACH PRODUCER, IF THE LINE PRESSURE APPROACHES MAOP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070058 | 2007-05-29 09:25 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS COMPANY | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1744 | 2007-05-01 | 2007 | TUCSON | PIMA | AZ | 85735 | 500+4964 |  | 32.17747 | -111.14542 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | EXCAV. DAMAGE TO 1" TAP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223430 | 108241.8393 | 94764.4565 | 222430 | 93496.924 | 1000 | 1267.5325 | 0 | 0 | YES | NO | NO | YES | 2 | PRECAUTIONARY | 4 | 15 | 834072 | 2007-05-01 | 680 | 809 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2007 | 1 | 0.13 | [6 empty] | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | EL PASO NATURAL GAS COMPANY CONTRACTOR WAS EXCAVATING PIPELINE FOR REPLACEMENT PROJECT WHEN EQUIPMENT STRUCK A 1" METER STATION PIPELINE TAP ON EL PASO'S 1103 PIPELINE. EMERGENCY RESPONDERS CLOSED A SHORT SECTION OF STREET NEAR THE INTERSECTION OF SAN JOAQUIN & BOPP ROAD IN TUCSON, AZ AND EVACUATED ONE HOME IN THE VICINITY. GAS LOSS WAS OVER $220,000. THE LEAK WAS IN A 1" ELBOW THAT CRACKED WHEN STRUCK BY CONTRACTOR'S BACKHOE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070059 | 2007-06-07 08:32 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1430 | 2007-05-10 | 2007 | [6 empty] | 3,470,00.47 | 491,280.35 | OFFSHORE |  | HIGH ISLAND | 206 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280000 | 159295.3431 | 350673.1443 | 5000 | 2101.7157 | 275000 | 348571.4286 | 0 | 0 | NO | NO | NO | NO | 0 |  | 118 | 20 | 834989 | 2007-05-10 | 900 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.5 | API 5L | 35000 | SEAMLESS | ANSI 900 | US STEEL | 1977 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | FLANGE CONNECTION | [6 empty] | CONSTRUCTION DEFECT | PROCEDURE NOT FOLLOWED | NO | YES | 6 | 2 | 1977 | WATER |  | 8 | 2218 | [12 empty] | DURING ABANDONMENT OF 12" PIPELINE FROM HIA-68, CONTRACTOR FOR GULF SHORE MIDSTREAM UNCOVERED THE SUB-SEA ASSEMBLY TO OPERATE VALVES DURING ABANDONMENT. AFTER ABANDONMENT OF 12" LINE, THE SUB-SEA ASSEMBLY SHIFTED CAUSING A FLANGE TO START LEAKING.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070060 | 2007-06-11 | SUPPLEMENTAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 915 | 2007-04-30 | 2007 |  | MATAGORDA | TX | 77457 |  |  | N28 28.232 | W 96 00.336 | OFFSHORE |  | BRAZOS | 480L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72500 | 41141.9898 | 89778.1306 | 2500 | 1050.8578 | 70000 | 88727.2727 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 833862 | 2007-04-30 | 750 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER, VP- MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API 5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON OR ABOUT APRIL 30, 2007 PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 480-L. THE LEAK WAS DUE TO A SUBSEA HOLE IN PIPELINE. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE HAVING THE LEAK. THE LEAK WAS CLAMPED OFF ON 5/5/07 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 5/5/07.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070061 | 2007-06-18 | ORIGINAL FINAL | 18152 |  | SEA ROBIN PIPELINE COMPANY | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1945 | 2007-05-01 | 2007 | [6 empty] | 28.988164N | 92.291922W | OFFSHORE |  | VERMILION | 149 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 570363.8402 | 1266642.9187 | 1050 | 441.3603 | 998950 | 1266201.5584 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 834076 | 2007-05-01 | 14 | 99 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | OTHER | VENT PIPING | 1973 | 30 | 0.34 | 5L | 35000 | DSAW | N/A | UNK |  | OTHER | ABOVE WATER | 0 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | VENTING GAS PICKED UP A LIQUID SLUG WHICH STRUCK A DIRECTIONAL CHANGE IN THE VENT PIPING. |  | A VALVE WAS CLOSED TO REPAIR A LOOSE FITTING ON A RELIEF VALVE PILOT. THE LOOSE FITTING LEAKED SUFFICIENT GAS TO CAUSE THE RELIEF VALVE TO ACTUATE. IT IS SURMISED THAT THE VENTING GAS PICKED UP A LIQUID SLUG IN THE VENT PIPING AND THAT THE LIQUID SLUG WAS CARRIED WITH ENOUGH MOMENTUM THAT STRIKING A DIRECTIONAL CHANGE FITTING RESULTED IN SEPARATION OF THE PIPING. IN THE DARKNESS THE DAMAGE TO THE VENT PIPING WAS NOT IMMEDIATELY EVIDENT.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070062 | 2007-06-19 | SUPPLEMENTAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 820 | 2007-05-19 | 2007 |  | MATAGORDA | TX |  |  |  | N 28 27 78 | W 96 00 64 | OFFSHORE |  | BRAZOS | 480L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72500 | 41141.9898 | 89778.1306 | 2500 | 1050.8578 | 70000 | 88727.2727 | 0 | 0 | NO | NO | NO | NO | 0 |  | 12 | 0 | 835904 | 2007-05-19 | 750 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER, VP- MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API 5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON OR ABOUT MAY 19, 2007, PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 480-L. THE LEAK WAS DUE TO A SUBSEA HOLE IN PIPELINE. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE HAVING THE LEAK. THE LEAK WAS CLAMPED OFF ON 5/27/2007 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 5/27/2007.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070063 | 2007-06-25 17:46 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1030 | 2007-05-25 | 2007 | DUBACH | LINCOLN | LA | 71235 | UNIONVILLE COMPR. ST. | 0 | 32.67925 | -92.60000 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | INJURY WHILE WORKING ON COMPRESSOR | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 1 | 836940 | 2007-05-30 | 0 |  | NO | NO | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | COMPRESSOR | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1975 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | INADEQUATE SAFETY PRACTICES |  | 0 | 0 | Y | 3 |  |  | A MRT EMPLOYEE WAS INJURED WHILE ATTEMPTING TO REBUILD THE #3 COMPRESSOR HEAD END UNLOADER ON UNIT #2. WHILE DISASSEMBLING THE HEAD END UNLOADER, THE ACTUATOR PISTON BLEW OUT OF THE HEAD END UNLOADER, STRIKING THE EMPLOYEE IN THE ABDOMEN AREA ON THE BODY. THE EXTENT OF THE EMPLOYEE CAUSED HIM TO BE HOSPITALIZED. THE CAUSE OF THIS INCIDENT WAS ¿INCORRECT OPERATIONS ¿ INADEQUATE SAFETY PRACTICES.¿
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070064 | 2007-06-11 | SUPPLEMENTAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 442 | 2007-04-29 | 2007 | PAWNEE | SANGAMON | IL | 62558 | MP 3 VS 0 | 160+89 | 39.649271 | -89.577938 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445000 | 238734.7371 | 415793.8153 | 175000 | 73560.049 | 120000 | 152103.8961 | 150000 | 190129.8701 | NO | YES | NO | YES | 1 | PRECAUTIONARY | 1 | 1 | 833789 | 2007-04-29 | 788 | 800 | NO | NO | NO | NO | YES | NO | BRIAN JIMENEZ - ASSOCIATE ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1940 | 22 | 0.28 | API-5L | 46700 | SMLS |  | NATIONAL TUBE | 1940 | OPEN DITCH |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1950 | NO | [57 empty] | APPARENTLY EXTERNAL CORROSION OCCURED ON THE BODY OF THE PIPE AT AN AREA EXPOSED TO THE ATMOSPHERE. NORMINALLY BURIED PIPE HAD BECOME EXPOSED IN A WASHOUT ARED ADJACENT TO A ROAD EMBANKMENT. THE EXTERNAL COATING HAD BECOME DISBONDED ALLOWING EXTERNAL CORROSION TO OCCUR ON THE TOP OF THE PIPE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070065 | 2007-06-29 10:21 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1330 | 2007-05-30 | 2007 | [6 empty] | 28.17.462 | 93.58.003 | OFFSHORE |  | HIGH ISLAND | 468 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401700 | 229004.7348 | 507727.5703 | 1700 | 714.5833 | 400000 | 507012.987 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 836951 | 2007-05-30 | 856 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 8 | 0.32 | API 5L | 42000 | ERW |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1980 | NO | [57 empty] | OPERATIONS PERSONNEL SPOTTED GAS BUBBLES AT THE SURFACE NEAR HIGH ISLAND BLOCK 468. NOTIFICATIONS WERE MADE TO APPROPRIATE AGENCIES. PART A NUMBER 2 INCIDENT DAY IS CORRECTED TO MAY 30, 2007. THE PIPELINE HAS BEEN ISOLATED AT BOTH ENDS AND BLED DOWN. NO FUTURE SERVICE FROM PIPELINE OWNERS HAS BEEN GIVEN AT THIS TIME.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070066 | 2007-06-29 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE COMPANY | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 200 | 2007-05-25 | 2007 |  | FOND DU LAC | WI |  | 173.39 | 418+13 | 43* 51' 52 | 88* 31' 32 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93000 | 48560.205 | 73826.6743 | 52000 | 21857.8431 | 41000 | 51968.8312 | 0 | 0 | NO | NO | NO | YES | 0 | PRECAUTIONARY |  | 30 | 836455 | 2007-05-25 | 800 | 975 | NO | YES | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 10.75 | 0.25 | API | 42000 |  |  | A.O. SMITH |  | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DRAIN TILE INSTALLATION | NO |  |  |  |  | YES |  | YES | [38 empty] | THE INCIDENT ON ANR S 10 LINE 350 OCCURRED IN FOND DU LAC, COUNTY, WISCONSIN. AN APPROXIMATE 4-FOOT SECTION OF THE 10-INCH LINE RUPTURED AND CAME APART FROM THE MAIN LINE. APPARENTLY, THIRD-PARTY DAMAGE (A DRAIN TILE EXCAVATION CONTRACTOR WORKING IN THE AREA OF THE PIPELINE) WAS THE CAUSE OF THE INCIDENT. THERE WERE NO INJURIES AS A RESULT. *04/18/2014 UPDATES MADE BY PHMSA PER OPERATOR’S MOCK UP. PRIOR TO THE INCIDENT, TRANSCANADA HAD RECEIVED DIGGERS HOTLINE NOTIFICATIONS ON MAY 3 (TICKETS #20071818437 & #200711818449) WHEREBY TRANSCANADA REQUESTED A MEETING WITH THE LANDOWNER (C. SCHUMACHER)ON MAY 7 2007. THE ON-SITE DID OCCUR ON MAY 7, WHEREUPON THE PIPELINES & CATHODIC PROTECTION LEAD LINES WERE MARKED AND STAKED CONSISTENT WITH THE WINSCONSIN DIGGERS HOTLINE ONE-CALL TICKETS. TRANSCANADA EMPLOYEES WERE ON-SITE MAY 9 TO MONITOR THE INSTALLATION OF DRAIN TILE ACROSS THE CATHODIC PROTECTION LEAD LINES. TRANSCANADA EMPLOYEES WERE AGAIN ON-SITE MAY 18 2007 TO MONITOR THE INSTALLATION OF 4" & 6" DRAIN TILE ACROSS THE PIPELINES. THE INCIDENT REPORT ADDRESSES THE LINE BREAK THAT OCCURED ON MAY 25 2007 AS INVESTIGATED BY PHMSA'S CARL GRIFFITH'S. ACCORDING TO LANDOWNER, ADDITIONAL DRAIN TILE WAS INSTALLED WITHOUT HAVING SUBMITTED A ONE-CALL, IN THE ADJACENT FIELD NORTH-NORTHEAST OF THE ORIGINALLY IDENTIFIED SITES ON MAY 19, 2007 WHICH RESULTED IN THE 10" PIPELINE BEING IMPACTED & SUBSEQUENTLY FAILED.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070067 | 2007-07-02 10:46 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING L.P. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1530 | 2007-05-15 | 2007 | [6 empty] | 28.03.826 | 96.16.849 | OFFSHORE |  | MI | 558 |  | YES | YES | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 835465 | 2007-05-15 | 890 | 1440 | NO | YES | NO | NO | NO | NO | MATTHEW STRATMANN | 7133818209 | MSTRATMANN@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.32 | [6 empty] | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | UNKNOWN | OTHER | UNKNOWN | YES | 1989 | NO | [57 empty] | THIS PIPELINE HAS A HISTORY OF CORROSION LEAKS. THE PIPELINE IS ISOLATED AND SHUT IN AND REPAIR ACTIVITIES AND ANY COST ASSOCIATED WITH LEAK REPAIR ARE PENDING THE DECISION AS TO WHETHER OR NOW WE WILL MOVE TO ABANDON THIS PIPELINE. THE DECISION WAS MADE TO ABANDON THIS SECTION OF PIPELINE. THE ABANDONMENT PROCESS WAS COMPLETE IN LATE 2007. BECAUSE THE PIPELINE IS UNDERWATER IN THE GULF OF MEXICO THE ACTUAL CAUSE OF THE LEAK IS UNCLEAR. INTERNAL CORROSION IS SUSPECTED TO BE THE CAUSE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070068 | 2007-07-03 11:05 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1337 | 2007-05-13 | 2007 | [8 empty] | OFFSHORE |  | MATAGORDA | 629 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271270 | 154239.5145 | 338864.6008 | 5877 | 2470.3566 | 265393 | 336394.2442 | 0 | 0 | NO | NO | NO | NO | 0 | [5 empty] | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7135953612 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 | N/A | N/A | N/A |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1975 | NO | [57 empty] | FINALIZED ON 9/19/2007 BY ADDING PROPERTY LOSS FIGURES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070069 | 2007-07-06 09:28 | SUPPLEMENTAL FINAL | 4900 |  | KINDER MORGAN TEJAS | 500 DALLAS STREET SUITE 1000 | HOUSTON | HARRIS | TX | 77002 |  | 2007-06-05 | 2007 | GALVESTON | GALVESTON | TX |  |  | MP 349+71 | N292104.6 | W-0950142.7 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 45636.3636 | 101402.5974 | 0 | 0 | 80000 | 101402.5974 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 837764 | 2007-06-05 | 635 | 738 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | N/A | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 16 | 281 | GRADE B | 35000 |  |  |  |  | OTHER | N/A |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | FURTHER INVESTIGATION REVELED NO GAS LOSS OR REPAIR REQUIRED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070070 | 2007-07-06 09:58 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC. | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1715 | 2007-06-18 | 2007 | HUTCHINSON | RENO | KS | 67501 | 183 | 160/9666+93 | 38.02344513 | -97.87589264 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256875 | 144236.6957 | 303052.8473 | 26611 | 11185.7512 | 229264 | 290599.5636 | 1000 | 1267.5325 | NO | NO | NO | NO | 0 |  |  |  | 839212 | 2007-06-20 | 683 | 900 | NO | NO | YES | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 26 | 0.31 | OTHER | 52000 | ELECTRIC FLASH WELD |  | A O SMITH | 1947 | UNDER GROUND |  | 46 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | AT 1715, 6/18/07, STAN PARSONS, A NON-EMPLOYEE, CALLED GAS CONTROL TO REPORT A SUSPECTED LEAK IN A DRAINAGE DITCH IN A CLASS 1 AREA NEAR HUTCHINSON, KANSAS. THE LEAK WAS INVESTIGATED BY LYONS' DISTRICT PERSONNEL WHO DETERMINED THAT IT WAS A NON-HAZARDOUS LEAK. BECAUSE THE LEAK WAS IN A DRAINAGE DITCH WITH FLOWING WATER, IT WAS 6/20/07 BEFORE THE LEAK WAS UNCOVERED AND THEY DISCOVERED IT WAS A BUTT WELD LEAKING. THE LINE WAS TAKEN OUT OF SERVICE AND SAND POINTS AND PUMPS WERE USED TO LOWER THE GROUND WATER TO A LEVEL LOW ENOUGH THAT A LEAK CLAMP AND HOUSING COULD BE INSTALLED. IT CONTINUED TO RAIN OFF AND ON MAKING THE REPAIR DIFFICULT. IT WAS APPROXIMATELY 2000 ON JUNE 28, 2007 BEFORE THE REPAIR ON THE LINE WAS COMPLETED AND THE LINE PLACED BACK IN SERVICE. SSCGP IS OPERATING THIS LINE AT A REDUCED PRESSURE UNTIL A DIRECTIONAL BORE CAN BE MADE AND THE PIPE IN THIS AREA REPLACED.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070071 | 2007-07-10 | SUPPLEMENTAL FINAL | 31659 |  | BOSS EXPLORATION | 300 EAST SONTERRA BLVD., SUITE 1280 | SAN ANTONIO | BEXAR | TX | 78258 | 1115 | 2007-05-29 | 2007 | INGLESIDE | NUECES | TX | 78362 |  |  | 27.48.39 | 97.09.22.68 | OFFSHORE |  | INTERCOASTAL WATERWA |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118000 | 67227.2504 | 148721.6418 | 1000 | 420.3431 | 117000 | 148301.2987 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 836803 | 2007-05-29 | 450 | 1440 | NO | NO | NO | NO | YES | NO | DAVID MAERSH, PRODUCTION SUPERVISOR | 3615370210 |  | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.38 | [8 empty] | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | MICROBIOLOGICAL |  | YES | 1967 | NO | [57 empty] | ON 5-29-07, BOSS PERSONNEL WERE NOTIFIED BY THE CORPUS CHRISTI RRC OFFICE THAT A POSSIBLE LEAK HAS BEEN REPORTED TO THEM BY THE COAST GUARD. UPON FURTHER INVESTIGATION, IT WAS DETERMINED TO BE BOSS' 12" REDFISH BAY GAS GATHERING LINE, AND THE LEAK WAS IN THE INTERCOASTAL WATERWAY. THERE WAS SOME SHEEN ON THE WATER DUE TO THE GAS BEING FULL WELL STREAM. A PLIDCO CLAMP WAS INSTALLED ON THE PINHOLE LEAK AND ALL REPAIRS WERE COMPLETE ON JUNE 4TH.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070072 | 2007-07-10 | ORIGINAL FINAL | 12408 |  | MICHIGAN CONSOLIDATED GAS COMPANY | 2000 SECOND AVENUE | DETROIT | WAYNE | MI | 48226 | 1735 | 2007-06-07 | 2007 | ASHLEY | GRATIOT | MI | 48806 | 52.98/ MAIN VALVE 5 | 2797+28 | 43.16 | -84.56 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84490 | 43891.1074 | 64858.8885 | 49853 | 20955.3664 | 34137 | 43269.7558 | 500 | 633.7662 | NO | NO | NO | NO | 0 |  | 4 | 29 | 838000 | 2007-06-08 | 700 | 970 | NO | YES | NO | NO | NO | NO | JOHN D. LUEDERS, P.E. SUPERVISING ENGINEER, CODES AND STANDA | 6166322646 | LUEDERSJ@DTEENERGY.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 24 | 0.31 | API 5LX | 52000 | FLASH WELD |  | A O SMITH | 1948 | UNDER GROUND |  | 24 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 9 | 6 | 1966 | WATER |  | 24 | 1327 | [12 empty] | ON 7 JUNE 2007, A MICHCON CONTRACTOR PERFORMING RECONNAISSANCE FOR ENVIRONMENTAL PERMITTING REPORTED LEAKAGE INDICATIONS APPROXIMATELY 200 YARDS WEST OF BLOCK VALVE 5 ALONG THE AUSTIN-DETROIT A PIPELINE. THE PIPELINE WAS ISOLATED BETWEEN ADJACENT BLOCK VALVES, AND THE PIPLE LINE PRESSURE WAS REDUCED FROM 700 TO APPROXIMATELY 163 PSIG USING STORAGE FIELD COMPRESSORS. THE REMAINING PRESSURE WAS BLOWN TO ATMOSPHERE, THE PIPELINE WAS DE-PRESSURIZED, AND REPAIRS COMMENCED ON 8 JUNE 2007. A SEVEN FOOT SEGMENT OF PIPE WAS REMOVED AND A NEW SEGMENT OF PRE-TESTED 24" PIPE WAS INSTALLED TO ELIMINATE THE LEAK. THE PIPELINE WAS PURGED OF AIR, PRESSURIZED, AND RETURNED TO SERVICE ON 11 JUNE 2007. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AT 1543 HOURS ON 8 JUNE 2007 WHEN IT WAS DETERMINED THAT THE TOTAL COST OF THE REPAIR WOULD EXCEED $50,000, PRIMARILY DUE TO THE VOLUME OF GAS BEING BLOWN TO ATMOSPHERE BETWEEN ADJACENT ISOLATING VALVES. UPON EXCAVATING THE PIPELINE THE LEAK WAS FOUND ON AN OLD, PREVIOUS REPAIR CONSISTING OF A 2-INCH STEEL COUPLING WELDED OVER A LEAKING GIRTH WELD. THE COUPLING AND PLUG HAD BEEN INSTALLED AT THE 12 O'CLOCK (TOP) POSITION OF THE PIPELINE OVER THE FIELD GIRTH WELD AND A LONGITUDINAL WELD SEAM OF THE PIPE. THE COUPLING HAD BEEN PLUGGED WITH A TWO-INCH THREADED STEEL BULL PLUG WHERE THE THREADS HAD THEN BEEN SEALED BY WELDING. LEAKAGE WAS OBSERVED AT THE WELDED THREADS BETWEEN THE COUPLING AND THE BULL PLUG.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070073 | 2007-07-13 15:32 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1110 | 2007-06-15 | 2007 | [6 empty] | 2905.63 | 8933.28 | OFFSHORE |  | WEST DELTA | 47 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278000 | 147701.738 | 245628.1704 | 126000 | 52963.2353 | 152000 | 192664.9351 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 838744 | 2007-06-15 | 800 | 1264 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 30 | 0.5 | API 5L | 60000 | DSAW |  | US STEEL | 1980 | UNDER WATER |  | 120 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1981 | NO | [57 empty] | COMPANY (TGP) AIRCRAFT REPORTED A 3-FEET DIAMETER AREA OF BUBBLES WITH NO SHEEN IN THE VICINITY OF THE 527A-300 PIPELINE. PLOTTING GPS COORDINATES CONFIRMED THIS LOCATION TO BE CLOSE ENOUGH TO DISPATCH A DIVER TO THE SITE. INVESTIGATION REVEALED A SMALL PINHOLE IN THE GIRTH WELD OF THIS 30" PIPELINE AT THE 6 O'CLOCK POSITION. A REPAIR CLAMP WAS INSTALLED.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070074 | 2007-07-11 | SUPPLEMENTAL FINAL | 31159 |  | KANSAS GAS SERVICE | 7421 W. 129TH STREET | OVERLAND PARK | JOHNSON | KS | 66213 | 1030 | 2007-06-18 | 2007 |  | GEARY | KS | 66441 | 1002-13 | 0+23 | 39.03307 | -96.96302 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 5 |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 16922 | 8191.4093 | 7113.0466 | 16922 | 7113.0466 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 13 | 839003 | 2007-06-18 | 340 | 470 | NO | NO | YES | NO | NO | NO | BRUCE D. KUBIE | 7852713925 | BKUBIE@KGAS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 12 | 0.25 | API 5L | 42000 | ELECTRIC WELD |  | STUPP |  | UNDER GROUND |  | 42 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | COMPANY CREWS WERE EXCAVATING A BURIED BLOCK VALVE SETTING. CONCRETE WAS FOUND NEAR THE PIPE DURING THE EXCAVATION PROCESS. CREWS HAD JACKHAMMERED THE CONCRETE INTO SMALLER PIECES AND WERE REMOVING SOME OF IT WITH A BACKHOE WHEN THE RUPTURE OCCURRED. A 4-FOOT LENGHT OF 4" PIPE WAS ENCAPSULATED IN THE CONCRETE AND HAD BEEN WELDED TO THE CARRIER PIPE AS AN ANCHOR. WHEN CREWS ATTEMPTED TO REMOVE THE CONCRETE, THE 4" PIPLE WAS TORN AWAY FROM THE 12" PIPELINE LEAVING A 5" HOLE IN THE PIPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070075 | 2007-07-18 09:59 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 |  | 2007-06-18 | 2007 | [8 empty] | OFFSHORE |  | MATAGORDA | 629 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243743 | 138612.3727 | 304716.2196 | 5000 | 2101.7157 | 238743 | 302614.5039 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | N/A |  | 400 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7135953612 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.7 | 0.28 | 5LX-42 | 42000 | N/A | N/A | N/A |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1975 | NO | [57 empty] | RRC INCIDENT REPORT NO. 07-CA-623. REPORTED COORDINATES ARE 28 08.901N & 96 40.291W. DIVERS AND EQUIPMENT ON STAND-BY WAGES WAITING ON WEATHER IN ORDER TO REPAIR THE LINE. THE SUPPLY TO THIS LINE HAS BEEN SHUT OFF. LOSS COST NOT KNOWN YET. REPORT FINALIZED ON 9/19/2007 BY ADDING PROPERTY LOSS FIGURES.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070076 | 2007-07-18 14:38 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 730 | 2007-06-29 | 2007 |  |  |  |  | 0.20 |  | 29.14.638 | 93.10.707 | OFFSHORE |  | WEST CAMERON | 215 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396500 | 226142.0343 | 502153.0287 | 500 | 210.1716 | 396000 | 501942.8571 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 840657 | 2007-06-29 | 930 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 10 | 0.37 | API 5L | 35000 | SEAMLESS | ANSI 600 | US STEEL | 1983 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1983 | NO | [57 empty] | A LEAK IN THE FORM OF BUBBLES WAS DISCOVERED OFFSHORE ON 6/29/07 IN THE WC 215 AREA. A PRODUCER INITIALLY REPORTED THE LEAK TO THE NRC (#840657). INITIALLY THE LEAK WAS SUSPECTED OF ORIGINATING FROM A CLAMP FROM A PREVIOUS LEAK ON THE SAME LINE. DIVERS EVENTUALLY DETERMINED THE NEW LEAK WAS ON THE WGP OPERATED 10" WC 215A TO WC 222 PIPELINE. THE LEAK WAS CLAMPED AND RETURNED TO SERVICE ON 7/5/07.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070077 | 2007-07-18 16:07 | ORIGINAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1100 | 2007-06-29 | 2007 |  |  |  |  | 2.87 |  | 28* 35' 37.80" | 95* 12' 55.80" | OFFSHORE |  | GALVESTON | 394 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101000 | 57097.5936 | 122937.6432 | 6000 | 2522.0588 | 95000 | 120415.5844 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 840393 | 2007-06-29 | 950 | 1440 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12 | 0.31 | API 5L | 52000 | SEAMLESS | ANSI 900 | USS TUBULAR | 1990 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1990 | NO | [57 empty] | RECEIVED NOTIFICATION FROM ANOTHER OFFSHORE OPERATOR OF BUBBLES COVERING A 12 TO 15 FOOT DIAMETER AREA. GAS CONTROL NOTIFIED THE NRC, INCIDENT # 840393. DAVID L. CONTACTED LT. J.G. DAMASO WITH THE USCG AT THE MSU GALVESTON (713-671-5113). DETAILS WERE PROVIDED. PRESSURE WAS LATER REDUCED UNTIL GAS WAS BARELY LEAKING. MATERIALS AND DIVE BOAT WERE PROCURED AND THE LEAK WAS CLAMPED ON 7-15-07 AND RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070078 | 2007-07-23 10:50 | SUPPLEMENTAL FINAL | 32052 |  | SABCO OPERATING COMPANY | 1360 POST OAK BLVD SUITE 2300 | HOUSTON | HARRIS | TX | 77056-3050 | 1320 | 2007-07-22 | 2007 | [6 empty] | 28 03.008N | 96 43.3119W | OFFSHORE |  | MATAGORDA | 629 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 96545.3431 | 211244.5728 | 5000 | 2101.7157 | 165000 | 209142.8571 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | N/A |  | 450 | 1280 | NO | YES | NO | NO | NO | NO | MAX JAMESON - ENVIRONMENTAL\REGULATORY MANAGER | 7135953612 | JAMESONM@SABCOOIL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 4 | 0.28 | [6 empty] | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | PIT CORROSION | YES | 1975 | NO | [57 empty] | RRC INCIDENT NO. 07-CA-681. THE LEAK WAS CLAMPED ON 7/23/2007. LOSS COST TO BE DETERMINED.FINALIZED ON 9/24/2007 BY ADDING THE LOSS COST.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070079 | 2007-07-23 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1700 | 2007-07-03 | 2007 |  |  |  |  | 507K-801+4.07 | 214+75.8 | 29.446089 | -93.079592 | OFFSHORE |  | WEST CAMERON | 142 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208000 | 117004.5744 | 247465.437 | 19100 | 8028.5539 | 188900 | 239436.8831 | 0 | 0 | NO | NO | NO | NO | 0 |  | 120 | 0 | 840911 | 2007-07-03 | 820 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 16 | 0.38 |  | 52000 | UNKNOWN |  | US STEEL | 1972 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1974 | NO | [57 empty] | A MINERALS MANAGEMENT SERVICE (MMS) REPRESENTATIVE REPORTED THE PRESENCE OF BUBBLES TO THE COMPANY IN THE VICINITY OF TGP'S 507K-800 PIPELINE. PLOTTING THE GPS LOCATION AND SUBSEQUENT ON SITE INVESTIGATION REVEALED THE LEAK TO BE ON THIS PIPELINE. TGP PROMPTLY DISPATCHED A REPAIR CREW WITH DIVERS AND REPAIRED THE LINE BY INSTALLING A BOLT-ON LEAK CLAMP. THERE WAS NEVER A SHEEN ASSOCIATED WITH THIS LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070080 | 2007-07-25 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 50 | 2007-06-28 | 2007 | PORT SULPHUR | PLAQUEMINES | LA | 70083 | 0.00 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250653 | 127380.2679 | 164663.5215 | 180653 | 75936.2488 | 70000 | 88727.2727 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 840211 | 2007-06-28 | 980 | 1000 | NO | NO | NO | NO | YES | NO | KENNETH C PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | VALVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 2 |  |  |  | SEAMLESS | BALL | GROVE | 1967 | ABOVE GROUND |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | VARIOUS PITS, COMPONENT UNDER WATER DUE TO KATRINA | GALVANIC |  | NO |  | NO | [57 empty] | A PLATE CAME OFF THE BOTTOM OF A 2" VALVE IN A PIG LAUNCHER LOADING LINE IN TGP'S PORT SULPHUR COMPRESSOR STATION RESULTING IN A RELEASE OF NATURAL GAS AND CONDENSATE FROM THE 527A-100 LINE. ALL CONDENSATE WAS CONTAINED ON THE COMPANY'S STATION SITE. VISUAL INSPECTION REVEALED THAT THE PLATE'S BOLTS WERE NOT DAMAGED OR SHEARED BUT THE PLATE AND THE NUTS COULD NOT BE FOUND. INVESTIGATION OF THIS FAILURE CONTINUED AND RESULTED IN A CONCLUSION THAT CORROSION WEAKENED THE COMPONENT AND CAUSED THE FAILURE. THE CORROSION IS BELIEVED TO HAVE BEEN CAUSED BY THIS COMPONENT BEING UNDER WATER DUE TO HURRICANE KATRINA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070081 | 2007-07-27 11:10 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1822 | 2007-07-08 | 2007 | HUTCHINSON | RENO | KS | 67501 |  | SERIES 140, 9165+95 | 37.9910921632 | -98.043621299 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55621 | 28020.7048 | 34131.5854 | 42930 | 18045.3309 | 12691 | 16086.2545 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 53 | 841392 | 2007-07-08 | 476 | 900 | NO | NO | YES | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 26 | 0.31 | 2030-D (SMITH) | 52000 | FLASH WELD |  | A. O. SMITH | 1947 | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | OTHER | FAILED BUTT WELD |  |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | AT 18:22, 7/8/07 SSCGP GAS CONTROL WAS NOTIFIED OF GAS COMING FROM THE CASING VENTS ON STATE HIGHWAY 61 BY WARREN ETHERIDGE. (SSCGP EMPLOYEE) A CONTRACTOR PICKING UP EQUIPMENT FROM A PREVIOS CONSTRUCTION JOB NOTICE GAS COMING FROM THE CASING VENTS ON HIGHWAY 61. HE NOTIFIED RICK BENNETT (LYONS DISTRICT MANAGER). RICK NOTIFIED WARREN ETHERIDGE AND THE TWO OF THEM CHECKED IT OUT. THE DECISION WAS MADE TO SHUT IN AND BLOW DOWN THE LINE SEGMENT. THE LINE SEGMENT WAS BLOWN DOWN AT 23:15. THE LINE WAS DUG UP ON 7/9/07. THEY DISCOVERED A CRACKED WELD IN THE 6 C¿CLOCK POSITION. THE WELD WAS CUT OUT AND REPLACED WITH PIPE. THE CAUSE OF THE WELD FAILURE IS STILL UNDER INVESTIGATION. 11/7/07, THE ANALYSIS FROM THE LAB INDICATES THE FAILURE WAS CAUSED BY HYDROGEN-INDUCED CRACKING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070082 | 2007-08-01 09:39 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1813 | 2007-07-26 | 2007 | SIOUX FALLS | LINCOLN | SD | 57108 | 68.68 | SEC 16, TWPS 100N, RGE 50 | N43.47528 | W96.76367 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | SCRAPED AND DENTED WHILE PACKING DIRT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71884 | 41006.5545 | 91115.3039 | 0 | 0 | 71884 | 91115.3039 | 0 | 0 | NO | NO | NO | YES | 3 | COMPANY POLICY |  | 30 | 843487 | 2007-06-26 | 700 | 787 | NO | YES | NO | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.25 | 5LX | 42000 | SEAMLESS |  | YOUNGTOWN |  | OPEN DITCH |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | WATER |  | YES | 7 | 17 | 2007 | ONE-CALL SYSTEM | YES | FLAGS | NO | ACCURATE | YES | [36 empty] | UNDERGROUND DEVELOPERS WAS INSTALLING A 24 INCH WATER LINE FOR THE CITY OF SIOUX FALLS, S.D. A ONE-CALL WAS MADE AND RECEIVED. A NORTHERN EMPLOYEE WAS ON SITE AT THE TIME OF THE INCIDENT WHICH OCCURRED DURING BACKFILLING AND COMPACTING OF DIRT ACTIVITIES. THE PIPELINE WAS STRUCK BY THE COMPACTION DEVICE AND SCRAPED, REMOVING COATING AND SLIGHTLY DENTED THE PIPE. ALL ACTIVITIES WERE STOPPED AND NOT KNOWING THE POTENTIAL EXTENT OF DAMAGE THE PIPELINE PRESSURE WAS REDUCED. THREE HOUSES WERE WITHIN THE CALCULATED POTENTIAL IMPACT RADIUS. ONE HOUSE WAS NEW CONSTRUCTION AND NOT OCCUPIED, A SECOND HOUSE RESIDENTS WERE GONE ON VACATION. A THIRD HOUSE WAS OCCUPIED AND AS A PROCEDURAL PRECAUTION THEY WERE EVACAUATED FROM THE HOUSE WITHT HE ASSISTANCE OF THE LOCAL PUBLIC OFFICIALS. THIS INCIDENT IS BEING REPORTED AS NORTHERN CONSIDERS THE NEED TO EVACUATE THREE PEOPLE FROM A RESIDENCE AS A "SIGNIFICANT EVENT". THE INCIDENT IS UNDER COMPANY INVESTIGATION AND ONCE THE ROOT CAUSE AND COST OF REPAIRS IS DETERMINED A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED. SUPPLEMENTAL SUBMITTED TO CORRECT DATE OF INCIDENT INSTEAD OF 8/1/07 THE ACTUAL DATE OF INCIDENT WAS 7/26/07. SUPPLEMENTAL REPORT: A SEGMENT OF THE LINE WAS ISOLATED AND THE PRESSURE REDUCED TO A SAFE LEVEL TO ENABLE INSPECTION FOR ANY DAMAGE. A SMALL AREA WAS FOUND TO HAVE THE COATING DAMAGED AND SOME SCRATHING AND VERY SLIGHT DENTING. THE AREA WAS CHECKED WITH DYE PENTRATANT AND X-RAY'D FOR ANY CRACKS. NONE WERE FOUND. THE SCRATCHED AREA WAS SMOOTHED OUT AND THE PIPE WAS RE-COATED. THE PIPELINE WAS PUT BACK INTO NORMAL SERVICE OPERATION. THIS WAS COMPLETED ON JULY 27, 2007. A FINAL REPORT WILL BE SUBMITTED ON CALCULATION OF TOTAL COST OF REPAIR. SUPPLEMENTAL/FINAL REPORT - A TOTAL ESTIMATED COST OF $70,000 WAS CALCULATED TO COMPLETE REPAIRS. SUPPLEMENTAL OF FINAL REPORT: THE FINAL REPORT IS BEING SUPPLEMENTED AS A FINAL COST OF REPAIRS HAS BEEN CALCULATED TO BE $71,884.00 INSTEAD OF THE PREVIOUSLY REPORTED $70,000. THE NEW FINAL COST INCLUDES OUTSIDE SERVICES PROVIDED BY MIDWEST INDUSTRIAL X-RAY WHICH PREVIOUSLY WERE NOT INCLUDED IN THE $70,000 ESTIMATE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070083 | 2007-08-01 11:52 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 815 | 2007-07-02 | 2007 | TURKEY CREEK | EVANGELINE | LA | 70586 | INDEX 202 @ MP 49.6 | 2622+90 | 30.86543 | 92.46702 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | D8 DOZER OPERATED BY THIRD PARTY STRUCK LINE |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 138000 | 77452.1632 | 162459.0198 | 14708 | 6182.4069 | 120292 | 152474.0156 | 3000 | 3802.5974 | NO | YES | NO | YES | 10 | PRECAUTIONARY | 1 | 15 | 840684 | 2007-07-02 | 350 | 780 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1931 | 6 | 0.19 |  | 35000 | SEAMLESS |  |  |  | UNDER GROUND |  | 24 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | TREE BED PLOWING | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | ON JULY 2, 2007 A BULLDOZER STRUCK AND RUPTURED 6" INDEX 202 AT MP 49.6. THE D8 DOZER WAS PLOWING BED ROWS FOR PINE TREE PLANTING. NO "ONE-CALL" WAS TURNED IN AND GULF SOUTH PIPELINE COMPANY, LP WAS NOT NOTIFIED OF THE WORK BEING PERFORMED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070084 | 2007-08-01 16:52 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE COMPANY | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1215 | 2007-07-09 | 2007 |  |  | LA |  |  | 39+94 | 28* 19'12.9 | 91*36 | OFFSHORE |  | EUGENE ISLAND | 306 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966000 | 549331.3725 | 1207492.577 | 20000 | 8406.8627 | 946000 | 1199085.7143 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 |  | 841529 | 2007-07-09 | 760 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 16 | 0.38 | API 5L | 52000 |  |  | UNKNOWN | 1977 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1977 | NO | [57 empty] | AT APPROXIMATELY 12:20 PM ON 7/09/2007, WHILE A HELICOPTER WAS PATROLLING THE AREA OFFSHORE, A 10 FT. BUBBLE CIRCLE WAS DISCOVERED NEAR EUGENE ISLAND BLOCK 306, IN THE VICINITY OF ANR'S 16-INCH LINE 607. THERE WAS NO SHEEN ASSOCIATED WITH THE RELEASE. UPON FUTHER INVESTIGATION, WHILE OBSERVING THAT LINE PRESSSURE IN LINE 607 CONTINUED TO DROP, THE LEAK WAS CONFIRMED. THE CAUSE OF THE LEAK WAS ATTRIBUTED TO INTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070085 | 2007-08-02 08:59 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1630 | 2007-07-20 | 2007 |  | LUZERNE | PA | 18709 | 86.628 | 3007+93 |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261700 | 126680.7598 | 110003.799 | 261700 | 110003.799 | 0 | 0 | 0 | 0 | YES | NO | NO | NO | 0 |  | 48 |  | 842857 | 2007-07-20 | 980 | 1200 | YES | NO | NO | NO | NO | NO | MARIA CAMILA QUEZADA | 7132152749 | MARIA.QUEZADA@WILLIAMS.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2007 | 24 | 0.41 | API 5LX | 70000 | ERW |  | AMERICAN PIPE | 2007 | UNDER GROUND |  | 68 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | HF ERW |  | MATERIAL DEFECT |  | NO | YES | 5 | 31 | 2007 | WATER |  | 8 | 2191 | [12 empty] | LAB ANALYSIS INDICATE, THAT THE IN-SERVICE LEAK WAS DUE TO A MANUFACTORING DEFECT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070086 | 2007-08-03 07:42 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 905 | 2007-06-30 | 2007 | [8 empty] | OFFSHORE |  | WEST CAMERON | 560 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 102681.8182 | 228155.8442 | 0 | 0 | 180000 | 228155.8442 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 840493 | 2007-06-30 |  |  | NO | NO | NO | NO | NO | NO | MARK NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | SUBSEA ASSEMBLY | [9 empty] | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | FLANGE | [8 empty] | MATERIAL DEFECT |  | NO | YES | 1 | 1 | 1950 | WATER |  | 8 | 0 | [12 empty] | THIS INCIDENT WAS REPORTED BY ENBRIDGE ON 6/30/07. COLUMBIA GULF WAS NOTIFIED THAT THE LEAK WAS ON THEIR FACILITY ON 7/3/07. A LEAK ON A FLANGE AT THE SUBSEA ASSEMBLY WC-537 FROM WC560, ON PL-560A WAS THE SOURCE. THE LOCATION WAS 28'19.89N ,93' 12.94W. DIVE CREW CONFIRMED THE SOURCE OF THE LEAK ON 7/3/07 AND REPAIRS WERE MADE BY ISOLATING THE ASSEMBLY AND THEN TIGHTENING THE BOLTS ON THE FLANGE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070087 | 2006-08-16 | SUPPLEMENTAL FINAL | 6141 |  | PUBLIC SERVICE COMPANY OF NE MEXICO | 414 SILVER AVENUE, SW | ALBUQUERQUE | BERNALILLO | NM | 87102-1007 | 1030 | 2006-07-18 | 2006 | NAVAJO | MCKINLEY | NM | 87328 | 61.09 |  | 36 55 27.85"N | 107 28 03.16"W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 5 | 804901 | 2006-07-20 | 0 | 550 | NO | NO | NO | YES | NO | NO | GARY G. ROYBAL, P.E. MANAGER, DOT COMPLIANCE & TECHNICAL | 5056973636 | GARY.ROYBAL@NMGCO.COM | TRANSMISSION | OTHER | NO FAILURE N/A | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1985 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | NO IN-PATIENT HOSPITALIZATION WAS REQUIRED FOR THE INJURY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070088 | 2007-09-04 | SUPPLEMENTAL FINAL | 31531 |  | ONEOK WESTEX TRANSMISSION | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103-4298 | 1145 | 2007-07-25 | 2007 | GOLDSMITH | ECTOR | TX |  | BLOCK 43 T-1S, SECTION 1 | LINE # 4056-000 RED RIVER | N32 00.269' | W102 28.689 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403225 | 196741.1 | 184718.5482 | 385253 | 161938.4547 | 17972 | 22780.0935 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 843330 | 2007-07-25 | 961 | 1200 | NO | YES | NO | NO | NO | NO | STEVEN A. BUSTOS, EHS COORDINATOR | 8067473037 | SBUSTOS@ONEOK.COM | TRANSMISSION | OTHER | THIRD PARTY CONTRACTOR STUCK PIPELINE | STEEL |  | NO | NO | NO | PIPELINE |  | 1982 | 24 | 344 | .72 | 1720 | SEAMLESS | ANSI 600 | UNKNOWN |  | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 7 | 13 | 2007 | ONE-CALL SYSTEM | YES |  | YES | ACCURATE | NO | [36 empty] | <P>FERGUSON CONSTRUCTION COMPANY (THIRD PARTY CONTRACTOR) WAS EXCAVATING OVER THE ONEOK WESTEX 24-INCH STEEL NATURAL GAS PIPELINE WITH A TRENCHER FOR ANOTHER OPERATOR (OCCIDENTAL PETROLEUM). THE TRENCHER STRUCK THE ONEOK WESTEX 24" PIPELINE AND PUNCTURED THE WALL OF THE PIPE CAUSING THE LINE TO RUPTURE. THE RUPTURE DID NOT RESULT IN ANY FIRE OR INJURIES. ONEOK WESTEX DID RECEIVE ADVANCE NOTICE OF THE PLANNED EXCAVATION. A DIG-TESS NOTICE (TEXAS STATE ONE-CALL SYSTEM) WAS COMPLETED BY SAID CONTRACTOR ON JULY 13, 2007 FOR SCHEDULED EXCAVATION ON JULY 17, 2007 THE ONEOK WESTEX PIPELINE WAS MARKED WITH PERMANENT PIPELINE MARKERS UPSTREAM AND DOWNSTREAM OF THE RUPTURE SITE. HOWEVER, MARKERS WERE LOCATED AT THE HIGHWAYS WHICH WERE LOCATED APPROXIMATELY 1/2 MILE FROM WHERE THE INCIDENT OCCURRED. ALSO, DUE TO HEAVY RAINS DURING THE SPRING BRUSH AND OVERGROWTH WAS NOTED ON THE PIPELINE ROQ WHICH CAUSED SOME VISUAL OBSTRUCTION. 1APR10 - THE ORIGINAL INCIDENT IS REPORT 20070088. THIS SUPPLEMENTAL REPORT WAS INADVERTANTLY FILED AS ANOTHER INCIDENT. FINALIZED THIS REPORT. PATTI FORD, ONEOK PARTNERS, SR. PIPELINE SAFETY ENGINEER, (918) 588-7131, <A href="mailto:PATTI.FORD@ONEOK.COM">PATTI.FORD@ONEOK.COM</A></P> <P>UPDATED BY PHMSA 4/10/2015: ONEOK WESTEX TRANSMISSION SUBMITTED AN ORIGINAL REPORT 20070088 AND A MONTH LATER THEY MEANT TO SUPPLEMENT THAT REPORT BUT&nbsp;CREATED ANOTHER ORIGINAL REPORT 20070106.&nbsp;THE ORIGINAL REPORT 20070088 WAS RETAINED AND THE OTHER REPORTS UNDER 20070106 WERE RE-ASSOCIATED AS SUPPLEMENTAL REPORTS UNDER 20070088. THERE ARE NO MORE DUPLICATE REPORTS FOR THE 7/25/2007 INCIDENT IN ECTOR COUNTY, TX AND THE GAS TRANSMISSION INCIDENT REPORT NUMBER 20070106 IS NO LONGER IN THE DATABASE. JPENDER</P>
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070090 | 2007-08-13 16:15 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1930 | 2007-07-14 | 2007 | BEAUMONT | PERRY | MS | 39423 | MP 137.8 | 790+36 | 31.31730 | 88.93202 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LIGHTNING STRUCK METER | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 50 | 842123 | 2007-07-14 | 200 | 430 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | LIGHTNING STRUCK METER CASE CAUSING GAS TO ESCAPE AND IGNITE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070091 | 2007-08-17 10:26 | SUPPLEMENTAL FINAL | 13845 |  | WILLIAMS NORTHWEST PIPELINE | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84118 | 1552 | 2007-08-08 | 2007 | MALTA | CASSIA | ID |  | 646.25 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 45986.5196 | 39932.598 | 95000 | 39932.598 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 844916 | 2007-08-08 | 850 | 850 | NO | YES | NO | NO | NO | NO | AMANDA STIFF | 8015846859 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1993 | 24 | 0.25 | API5LX | 60000 | DOUBLE SUBMERGED ARC WELD |  |  |  | UNDER GROUND |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1993 | NO
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070092 | 2007-08-17 13:48 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 730 | 2007-08-11 | 2007 | SAUK RAPIDS | BENTON | MN | 56379 | 1.26 | SEC12, T36N, RGE31W | N45.37'.298 | W94.08'.236 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | GAS LEAK & FIRE ON FARMTAP, LIGHTNING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36568 | 20223.4584 | 40104.8003 | 7373 | 3099.19 | 27695 | 35104.3117 | 1500 | 1901.2987 | NO | YES | NO | NO | 0 |  | 1 |  | 845222 | 2007-08-11 | 805 | 940 | NO | YES | NO | NO | NO | NO | BYRON H. WOOD | 4023983796 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | FARM TAP SETTING | STEEL |  | NO | NO | NO | OTHER | FARM TAP SETTING |  | 1 | [7 empty] | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | ON AUGUST 11, 2007 @ APPROXIMATELY 07:30 A.M. NORTHERN'S OPERATIONS COMMUNICATION CENTER (OCC) RECEIVED A CALL STATING THAT THERE WAS A FIRE AT THE JOSEPH PICK RESIDENCE FARM TAP ON CO. RD 1, 3883 MAYHEW RD, SAUK RAPIDS, MN. NORTHERN EMPLOYEES FROM THE ST. CLOUD, MN LOCATION RESPONDED. LOCAL POLICE AND FIRE DEPARTMENT PERSONNEL ASSISTED. IN WAS FINALLY DETERMINED THAT REDUCTION OF LINE PRESSURE ON THE 4" SARTELL BRANCH LINE (MNB73101)WAS NECESSARY TO FACILITATE EXTINGUISHING THE FIRE. INTENSE HEAT FROM THE FIRE DETACHED THE FARMTAP METAL FENCING AND RESULTED IN EXTENSIVE DAMAGE TO METERS AND REGULATORS AT THE SETTING. A NEW RISER PIPE FROM THE UNDERGROUND SHUTOFF VALVE TO ABOVE GROUND WAS INSTALLED AS WELL AS NEW METERS AND REGULATORS. TWO CUSTOMERS LOST SERVICE WHILE THE SETTING REPAIRS WERE BEING COMPLETED. THERE WAS A FIRE, THERE WAS NO INJURIES. AN INTERNAL POST INCIDENT INVESTIGATION IS BEING CONDUCTED. IT IS NOT KNOWN AT THIS TIME WHETHER THE COST OF REPAIRS WILL EXCEED THE $50,000 REPORTING THRESHOLD BUT NORTHERN IS REPORTING THIS AS IT IS DEEMED AS A "SIGNIFICANT EVENT". SUPPLEMENTAL/FINAL REPORTS WILL BE FILED AS ADDITIONAL INFORMATION AND COST ARE CALCULATED. SUPPLEMENTAL REPORT - A COST OF REPAIR HAS BEEN CALCULATED AND ENTERED FOR THIS INCIDENT. THE COST ESTIMATE IS LESS THAN THE $50,000 THRESHOLD FOR REPORTING. ALTHOUGH IT IS BELIEVED THAT THE ROOT CAUSE OF THE INCIDENT IS LIGHTNING A FINAL INTERNAL INVESTIGATION REPORT IS NOT COMPLETE AS OF YET. THIS REPORT WILL BE FINALIZED AND CLOSED UPON FINAL DETERMINATION OF CAUSE. SUPPLEMENTAL/FINAL REPORT - INVESTIGATION INTO THE CAUSE OF THE FARMTAP FIRE INDICATES THAT IT WAS CAUSED BY LIGHTNING. A SUPPLEMENT TO THE FINAL REPORT IS BEING SUBMITTED TO UPDATE THE FINAL COST ESTIMATE WHICH HAS BEEN CALCULATED AS INCREASED BY $736 AND TO IDENTIFY LIGHTNING AS THE CAUSE UNDER SECTION F2, NATURAL CAUSES.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070093 | 2007-08-20 | ORIGINAL FINAL | 31659 |  | BOSS EXPLORATION | 300 EAST SONTERRA BLVD., SUITE 1280 | SAN ANTONIO | BEXAR | TX | 78258 | 1155 | 2007-06-29 | 2007 | INGLESIDE | SAN PATRICIO | TX | 78362 |  |  | 27.48'367" | 97.10'310" | OFFSHORE |  | REDFISH BAY | ST 397 | TX | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60000 | 34184.0798 | 75628.3534 | 500 | 210.1716 | 59500 | 75418.1818 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 | 840414 | 2007-06-29 | 450 | 1440 | YES | NO | NO | NO | NO | NO | DAVID MARESH, PRODUCTION SUPERVISOR | 3615370210 |  | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2002 | 4 | 0.38 | SCHEDULE 80 | 42000 |  |  |  |  | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON 6-29-2007, BOSS PERSONNEL WERE NOTIFIED BY THE TEXAS GENERAL LAND OFFICE THAT A FISHING GUIDE HAD REPORTED TO THEM A BARGE RAN INTO SHALLOW WATER, AND HITTING BOSS' REDFISH BAY 348, 4
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070094 | 2007-08-21 | ORIGINAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1630 | 2007-07-17 | 2007 |  | MATAGORDA | TX |  |  |  | N.28.29 | W.95.59760 | OFFSHORE |  | BRAZOS | 445L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 39931.8182 | 88727.2727 | 0 | 0 | 70000 | 88727.2727 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 0 | 842467 | 2007-07-07 | 750 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER, VP- MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API 5L |  |  |  |  | 1958 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON JULY 17, 2007, PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 445-L. THE LEAK WAS DUE TO A SUBSEA HOLE IN 12" DIAMETER SEGMENT OF GAS PIPELINE. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE HAVING THE LEAK. THE LEAK WAS CLAMPED OFF ON 7/22/07 AND SERVICE WAS REINSTATED INTO THE OFFSHORE LATERAL.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070095 | 2007-08-21 15:40 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 440 | 2007-07-17 | 2007 | MONKTON | BALTIMORE | MD | 21111 |  | 175254.0 | 39.566544 | -76.579114 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | EMPLOYEE REQUIRED OVERNIGHT HOSPITALIZATION | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 10 | 842475 | 2007-07-17 | 6 | 1000 | NO | YES | NO | NO | NO | NO | MARK NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | OTHER | FUEL HEATER | STEEL |  | NO | NO | NO | OTHER | FUEL HEATER AT MEASUREMENT STATION | 2007 | [8 empty] | OTHER | OPEN | 0 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | BACKFIRE DURING COMMISSIONING OF A NEW INDIRECT FUEL HEATER. |  | EMPLOYEE WAS ADJUSTING AIR-FUEL RATIO WHILE COMMISSIONING NEW DUAL-BURNER INDIRECT HEATER WHEN BURNER FLASHED, KNOCKING EMPLOYEE BACK SEVERAL FEET AND CAUSING BURNS TO MOUTH AND ARMS. FIRST AID WAS ADMINISTERED AND EMPLOYEE TRANSPORTED TO MEDICAL FACILITY. EMPLOYEE DID REQUIRE OVERNIGHT HOSPITALIZATION. INVESTIGATION INTO THE CAUSE OF THE INCIDENT INDICATED LOOSE FITTINGS AS THE SOURCE WHERE GAS CAUSED THE FLASHBACK. RECOMMENDATIONS INCLUDE REVIEW OF EXISTING COMMISSIONING PROCEDURES, USING MANUFACTURE TECHNICIAN TO ASSIST DURING COMMISSIONING, AND IMPROVEMENTS TO EXISTING PROCEDURES. 02/11/08 UPDATED STREET ADDRESS AND LATITUDE AND LONGITUDE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070096 | 2007-08-21 16:38 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 900 | 2007-07-28 | 2007 | MARIETTA | WASHINGTON | OH | 45750 |  | 348+25 | 39.447 | -81.518 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325000 | 158495.1655 | 148113.8091 | 311423 | 130904.5208 | 13577 | 17209.2883 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 14 | 843717 | 2007-07-29 | 180 | 720 | NO | YES | NO | NO | NO | NO | MARK NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 8.63 | 0.17 | X-42 | 42000 | ERW |  | LTV | 1981 | UNDER GROUND |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | LAB ANALYSIS | OTHER | SULFUR AND IRON FOUND IN CORROSION PRODUCT. | YES | 1981 | NO | [57 empty] | AS A RESULT OF A RUPTURE ON LINE C-40, AN INVESTIGATION WAS CONDUCTED CONSISTING OF LABORATORY ANALYSIS AND IN LINE INSPECTION. A REMEDIAL ACTION PLAN WAS FORMULATED BASED ON THE RESULTS OF THIS INVESTIGATION. REMEDIAL ACTIONS CONSISTED OF PIPE REPLACEMENT FOR THE FAILED SECTION, INSTALLATION OF A WELDED SPLIT SLEEVE FOR ONE CORROSION ANOMALY AND LOWERING THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF THE SYSTEM. THE PIPELINE WAS RETURNED TO FULL SERVICE AT A REDUCED MAOP ON 10-31-07. A COPY OF THE INVESTIGATION AND ASSOCIATED ANALYTICAL RESULTS WILL BE MADE AVAILABLE TO PHMSA, CENTRAL REGION AND THE PUCO.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070097 | 2007-08-28 11:46 | SUPPLEMENTAL FINAL | 18516 | 18516 | SOUTHERN NATURAL GAS COMPANY | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 220 | 2007-08-03 | 2007 |  | PLAQUEMINES | LA | 70085 | 39.6 |  | 29 38.501 | -89 43.864 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 10 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11237500 | 6381327.7072 | 13957969.7049 | 337500 | 141865.8088 | 10900000 | 13816103.8961 | 0 | 0 | NO | NO | YES | NO | 0 |  | 4 | 0 | 844303 | 2007-08-03 | 1088 | 1072 | NO | NO | NO | NO | YES | YES | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 20 | 0.34 |  | 52000 | FLASH WELD |  | A.O. SMITH | 1959 | UNDER WATER |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1967 | NO | [57 empty] | IN THE EARLY MORNING HOURS OF 8/3/07, ANOTHER PIPELINE OPERATOR REPORTED TO SNG'S GAS CONTROL OF HEARING AN EXPLOSION SOUTH AND EAST OF HIS LOCATION. THIS WAS CONFIRMED TO BE A RUPTURE WITH IGNITION OF SNG'S 20" MAIN PASS TO FRANKLINTON LOOP PIPELINE. AUTOMATIC CLOSING VALVES OPERATED RESULTING IN EXTINGUISHING THE FIRE WITHIN WHAT IS BELIEVED TO BE ABOUT A 3 HOUR TIME FRAME. THE RUPTURE OCCURRED IN A MARSHY AREA OF SOUTH LOUISIANA, VERY REMOTE AND DESOLATE. THERE WAS NO AFFECT ON THE GENERAL PUBLIC. FOLLOWING FIELD INVESTIGATION AND LABORATORY ANALYSES, THE PROBABLE CAUSE HAS BEEN DETERMINED TO BE EXTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070099 | 2007-08-29 14:57 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 830 | 2007-08-03 | 2007 | UNKNOWN | UNKNOWN |  | UNKNOWN | UNKNOWN | UNKNOWN | 29¿R 16¡¦ 39.00'' | 92¿R 21¡¦ 29.400¡¦¡¦ | OFFSHORE |  | VERMILION | 76 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220200 | 121294.795 | 236751.1828 | 50000 | 21017.1569 | 170200 | 215734.026 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 844332 | 2007-08-03 | 957 | 1250 | NO | NO | NO | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 36 | 0.56 | X60 | 1873 | DSAW |  |  |  | UNDER WATER |  | 336 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1979 | NO | [57 empty] | BUBBLING AREA WAS SPOTTED BY A PASSING BY HELICOPTER WHERE IT WAS REPORTED TO OUR TEAM LEADER WHO IN PLACE CONTACTED THE MONITORING CENTER. LOCATION WAS IDENTIFIED TO BE LATITUDE:29¿R 16¡¦ 39.00" LONGITUDE: 92¿R 21¡¦ 29.400", LEAK REPAIRED WITH A CLAMP.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070101 | 2007-08-30 07:37 | SUPPLEMENTAL FINAL | 31846 |  | CAROLINA GAS TRANSMISSION | 105 NEW WAY ROAD | COLUMBIA | RICHLAND | SC | 29224 | 1636 | 2007-08-11 | 2007 | GASTON | RICHLAND | SC | 29053 | 25-079 | 1345+85 | 81 DEG 1'7.5 W | 33 DEG 52'9.7 N | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68100 | 33060.098 | 29557.2759 | 67000 | 28162.9902 | 1100 | 1394.2857 | 0 | 0 | YES | NO | NO | NO | 0 |  | 1 | 6 | 845290 | 2007-08-11 | 630 | 1200 | NO | YES | NO | NO | NO | NO | LAURA COMSTOCK | 8032172199 | LCOMSTOCK@SCANA.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2001 | [5 empty] | RELIEF | FLOW SAFE | 2001 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | WHEN THE REMOTELY CONTROLLED INLET VALVE @ CALPINE M&R STATION 25-079 BRIEFLY CLOSED AS A RESULT OF A LIGHTNING STRIKE, THE STATION PRESSURE WAS REDUCED FROM ~580 PSIG TO ~150 PSIG. WHEN THE INLET VALVE REOPENED AND THE PRESSURE RETURNED, THE RELIEF DIDN'T HAVE TIME TO RELOAD TO THE SET POINT (650 PSIG) AND LIFTED PREMATURELY AT ~492 PSIG. THE RELIEF LIFTED SO ABRUPTLY THAT THE PISTON HUNG IN THE HOUSING AND WOULD NOT RESEAT. GAS CONTROL WAS UNABLE TO CLOSE THE INLET VALVE TO STOP THE RELIEF FROM BLOWING DUE TO THE LIGHTNING DAMAGE TO THE COMMUNICATIONS EQUIPMENT. THE RELIEF BLEW FOR APPROXIMATELY 66 MINUTES UNTIL MANUALLY VALVED OFF. MAOPS WERE NOT EXCEEDED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070102 | 2007-08-31 15:28 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 655 | 2007-08-06 | 2007 | WOODVILLE | TYLER | TX | 75979 | 100-2, MLV 29-2 |  | 30.733212 | -94.541798 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 145263.7812 | 126526.5358 | 299500 | 125892.7696 | 500 | 633.7662 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 55 | 844566 | 2007-08-06 | 595 | 604 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | NIPPLE | STEEL |  | NO | NO | NO | PIPELINE |  | 2003 | 0.38 |  | HEAVY DUTY |  | N/A |  |  |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | A 3/8" THREADED PIPE NIPPLE CRACKED IN THE THREADS JUST ABOVE WHERE IT CONNECTED TO A PIPELINE. THIS NIPPLE PROVIDED A CONNECTION FOR A PILOT OPERATED RELIEF VALVE SENSING LINE. REASON FOR CRACK DEVELOPING IN NIPPLE THREADS IS UNKOWN. |  | A LOCAL SHERIFF REPORTED TO COMPANY GAS CONTROL THAT A RELIEF VALVE WAS DISCHARGING ON TGP'S 100-2 PIPELINE IN TYLER COUNTY, TX NEAR WOODVILLE. UPON ARRIVING AT THE SITE, COMPANY PERSONNEL FOUND THAT A 3/8" PIPE NIPPLE WHERE A RELIEF VALVE SENSING LINE CONNECTED TO THE TRANSMISSION PIPELINE HAD CRACKED IN THE THREADS OF THE NIPPLE. THIS CAUSED THE SENSING LINE TO LOSE THE "SIGNAL" TO THE RELIEF VALVE, RESULTING IN A DISCHARGE OF GAS THROUGH AN 8" RELIEF VALVE STACK. ISOLATION VALVES UPSTREAM AND DOWNSTREAM HAD TO BE CLOSED IN ORDER TO VACATE THE GAS FROM THE VALVE SECTION. THE RESULT WAS ALMOST $300,000 IN GAS LOSS. A NEW NIPPLE WAS INSTALLED WITH THE RELIEF VALVE SENSING LINE REINSERTED. THE PIPELINE AND RELIEF VALVE WERE PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070103 | 2007-09-04 14:22 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 2010 | 2007-08-05 | 2007 | GOLDEN MEADOW | LAFOURCHE | LA | 70357 |  | 523M-100 | 28 34.0977 | -91.1934 | OFFSHORE |  | EUGENE ISLAND | 227 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120000 | 68368.1595 | 151256.7068 | 1000 | 420.3431 | 119000 | 150836.3636 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 844544 | 2007-08-05 | 990 | 1250 | NO | NO | NO | NO | YES | NO | KENNETH PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 2.38 |  |  |  |  | USAS |  | 1969 | UNDER WATER |  | 0 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | O-RING | [7 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | A LEAK OCCORRED ON A 2" BRANCH FROM TGP'S 523M-100 PIPELINE, CAUSED BY A WORN O-RING IN THE 900# RTJ FLANGE CONNECTION OF THE VALVE. THE O-RING WAS REPLACED AND THE BRANCH WAS PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070104 | 2007-09-05 13:14 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1450 | 2007-08-10 | 2007 | CORPUS CHRISTI |  | TX |  |  |  | 27.57355 | 96.3355 | OFFSHORE |  | MATGORDA ISLAND | 686 | TX | NO | NO | INTRASTATE | OTHER | CRACK ON TWO-INCH BYPASS PIPING ON SUB SEA BLOCK V | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100000 | 1733854.7237 | 3590474.9172 | 400000 | 168137.2549 | 2700000 | 3422337.6623 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 845168 | 2007-08-10 | 851 | 1250 | NO | YES | NO | NO | NO | NO | BYRON WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | GATHERING | OTHER | 2-INCH BYPASS PIPING | STEEL |  | NO | NO | NO | PIPELINE |  |  | 2 | [7 empty] | UNDER WATER |  | 60 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | CRACK IN 2-INCH BYPASS PIPING AROUND A SUB SEA BLOCK VALVE. |  | ON AUGUST 10, 2007 NORTHERN NATURAL GAS COMPLETED NSTALLATION OF A 24-INCH PIGABLE BYPASS PIPING TO FACILITATE REMOVAL OF LATERAL LINES TO THE NORTHERN NATURAL GAS COMPRESSION PLATFORM MI 686 C-CMP. ALL WORK WAS COMPLETED AND THE PIPING WAS RE-PRESSURIZED AND LEAK TESTED. LATE THAT DAY PERSONNEL IN AIRCRAFT WITNESSED BUBBLES ON THE OCEAN SURFACE IN THE WORK AREA THAT WERE INDICATIVE OF A GAS LEAK FROM THE PIPING. PRODUCER PLATFORMS WERE NOTIFIED TO SHUT-IN AND THE LINE WAS ISOLATED. THIS WAS REPORTED TO MMS AND THE COAST GUARD. PRESSURE WAS REDUCED ON THE LINE. A REPAIR PLAN WAS SUBMITTED TO & APPROVED BY MMS. INVESTIGATION FOUND THAT THERE WAS A SMALL CRACK ON A 2-INCH BYPASS LINE THAT WENT AROUND A 24-INCH SUB SEA BLOCK VALVE. WHILE WORKING ON REPAIRING THIS LEAK BY REMOVING THE 2 INCH CONNECTION PIPING TO THE 24-INCH LINE AS WELL AS THE SADDLE TO FACILITATE INSTALLATION OF A 24-INCH LEAK CLAMP, IT WAS FOUND THAT THE 2-INCH CONNECTION ON THE OTHER SIDE OF THE BLOCK VALVE WAS ALSO CRACKED. A REVISED REPAIR PLAN WAS SUBMITTED AND APPROVED BY MMS. THE REVISED PLAN CALLED FOR REMOVAL OF THE TWO INCH PIPE AND SADDLE IDENTICAL TO WHAT WAS COMPLETED ON THE OTHER SIDE OF THE VALVE AND INSTALLATION OF A HIGH PRESSURE, FULL ENCIRCLEMENT, BOLT-ON LEAK CLAMP. BOTH LEAK CLAMPS WERE INSTALLED AND A LEAK TEST AT NORMAL OPERATING PRESSURE WAS CONDUCTED FOR 2 HOURS. THERE WERE NO LEAKS OBSERVED AND THE PIPING WAS WRAPPED AND SANDBAGGED TO ORIGINAL COVER. THIS WAS COMPLETED ON AUGUST 31, 2007. THE ROOT CAUSE OF THE LEAKS IS STILL UNDER INVESTIGATION AS IT IS THOUGHT THAT THE CONTRACTOR CRACKED THE PIPE WHEN INSTALLING SANDBAGS AFTER THE 24 INCH BYPASS LINE INSTALLATION WAS COMPLETE. A METALLURGICAL ANALYSIS IS BEING CONDUCTED ON THE 2-INCH REMOVED PIPING. A SUPPLEMENTAL/FINAL REPORT IS BEING FILED WITH UPDATE TO THE COST OF GAS LOSS AND REPAIRS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070105 | 2007-09-10 10:03 | SUPPLEMENTAL FINAL | 3 |  | ACADIAN GAS PIPELINE SYSTEM | 338 WAVERLY ROAD | THIBODAUX | LAFOURCHE | LA | 70301 | 855 | 2007-08-10 | 2007 | NAPOLEONVILLE | ASSUMPTION | LA | 70341 |  |  | N 30.05618 | W 91.12619 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135679 | 69163.1872 | 91211.59 | 95334 | 40072.9926 | 40345 | 51138.5974 | 0 | 0 | NO | NO | NO | YES | 30 | PRECAUTIONARY | 17 | 35 | 845109 | 2007-08-10 | 830 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1999 | 2 | 0.22 | API 5L | 35000 | SEAMLESS |  |  |  | UNDER GROUND |  | 12 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | LULA-WESTFIELD WAS BUILDING A SMALL LEVEE NEAR OUR 20" CHICO D AND 2" SIDE TAP PIPELINE NEAR LOUISIANA HIGHWAY 996. BACKHOE STRUCK OUR 2" SIDE TAP WHICH BROKE PIPELINE. SECURED AREA, BLED DOWN PIPELINE, MADE NECESSARY REPARIS TO PIPELINE. OPENED PIPELINE TO NORMAL SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070107 | 2007-09-10 15:45 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 315 | 2007-08-16 | 2007 |  | LAFAYETTE | LA |  | VALVE SETTING 1203, VALVE |  | 30.1681111 | -92.110314 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107000 | 51795.3431 | 44976.7157 | 107000 | 44976.7157 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 50 | 845766 | 2007-08-16 | 840 | 840 | NO | YES | NO | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | OTHER | RELIEF VALVE COUPLING | STEEL |  | NO | NO | NO | OTHER | RELIEF VALVE | 2003 | [5 empty] | 8X10 F7000 RELIEF VALVE | FLOW SAFE | 2003 | ABOVE GROUND |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | MECHANICAL COUPLINGS | [9 empty] | 8" RELIEF VALVE AT VALVE SETTING OPENED AND BLEW GAS FOR 50 MINUTES. RELIEF VALVE HAD BEEN INSTALLED WITH HAMMER UNION FITTINGS. THE RELIEF VALVE ACTIVATED BELOW SET PRESSURE. THE PILOT SENSING LINE WAS LOCATED TOO CLOSE TO THE RELIEF VALVE WHICH CAUSED CYCLING OF RELIEF VALVE. CYCLIC OPENING AND CLOSING OF THE RELIEF VALVE CAUSED THE HAMMER UNION THREADS TO FAIL, DISENGAGING THE RELIEF VALVE FROM THE PIPELINE. THE CAUSE OF THE INACCURATE SET PRESSURE FOR THE RELIEF VALVE CANNOT BE DETERMINED DUE TO THE DAMAGE TO THE VALVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070108 | 2007-09-14 10:12 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 1945 | 2007-08-18 | 2007 | MCLOUTH | JEFFERSON | KS | 66054 | 100 | 6958 | 39.2350117564 | -95.1992570683 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 348 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1548870 | 775675.1504 | 905213.6741 | 1248870 | 524953.9338 | 250000 | 316883.1169 | 50000 | 63376.6234 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 4 | 0 | 846093 | 2007-08-19 | 460 | 720 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 16 | 0.25 | API 5LX | 52000 | ERW |  | STUPP CORPORATION | 1976 | UNDER GROUND |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL | OTHER | CARBONIC ACID | YES | 1978 | NO | [57 empty] | SOUTHERN STAR CENTRAL GAS PIPELINE¿S CONTROLLER WAS NOTIFIED AT 7:45 PM ON AUGUST 18, 2007 OF A BLOWING RUPTURE. THE CONTROLLER ISOLATED THE FIELD FROM THE MAINLINE TO PRESERVE SYSTEM INTEGRITY AND NOTIFIED TONGANOXIE PERSONNEL OF THE LEAK. TONGANOXIE PERSONNEL ARRIVED AT THE SITE AND THE FIRE DEPARTMENT EVACUATED A 1 MILE RADIUS AS A PRECAUTION. MCLOUTH FIELD WAS SHUT IN AND IT WAS DETERMINED AT THAT TIME THAT IT WAS THE EJC-001 16 INCH LOOP LINE THAT HAD RUPTURED. AFTER DETERMINING WHICH LINE HAD RUPTURED, SSCGP ESTIMATED THE RUPTURE WAS LIKELY TO MEET THE CRITERIA FOR A REPORTABLE INCIDENT AND A TELEPHONIC REPORT WAS MADE. THE CAUSE OF THE RUPTURE IS STILL UNDER INVESTIGATION. 12/4/07 CARBONIC ACID FORMED THRUGH DISSOLUTION OF CO2 IN THE GAS STREAM IN WATER RETAINED AT A LOW SPOT IN THE PIPELINE WAS DETERMINED TO BE THE CAUSE OF FAILURE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070109 | 2007-09-19 14:44 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS COMPANY | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1115 | 2007-09-04 | 2007 |  |  | LA |  |  |  | 29D,14'40 | 093D,09'10 | OFFSHORE |  | WEST CAMERON | 215 | LA | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460000 | 262149.9332 | 580523.3671 | 3000 | 1261.0294 | 457000 | 579262.3377 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 847779 | 2007-09-04 | 800 | 1440 | NO | YES | NO | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 16 | 0.38 | 5LX | 52000 | DSAW |  |  |  | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1980 | NO | [57 empty] | AT APPROXIMATELY 12:04 P.M. ON SEPTEMBER 4, 2007, NORTHERN NATURAL GAS COMPANY (NNG) RECEIVED NOTIFICATION OF A POSSIBLE LEAK IN THE WEST CAMERON, BLOCK 215 AREA. THIS IS THE 16-INCH, LOS11202, SEGMENT 5244 LINE WHICH BEGINS IN WEST CAMERON AREA BLOCK 222 AND CONTINUES TO A PLATFORM IN WEST CAMERON BLOCK 192. INITIAL REPORTS WERE THAT THERE WAS AN APPROXIMATE 6 FOOT AREA OF BUBBLES WITH NO VISIBLE SHEEN. NOTIFICATIONS WERE MADE TO THE NRC TICKET #847779, THE MMS AND THE COAST GUARD. IMMEDIATE ACTIONS WERE TAKEN TO SHUT IN PRODUCTION AND ISOLATE THE LINE. A BLOW DOWN AND REPAIR PLAN WAS SUBMITTED TO THE MMS FOR REVIEW AND APPROVAL. APPROVAL WAS GRANTED. PRESSURE ON THE LINE WAS REDUCED TO APPROXIMATELY 35 PSIG. THE LEAK AREA WAS EXCAVATED, APPROXIMATELY 48 INCHES OF CONCRETE WAS REMOVED AND REPAIR OF THE LEAK ACCOMPLISHED BY INSTALLATION OF A 16 INCH X 18 INCH PLIDCO HIGH PRESSURE, FULL ENCIRCLEMENT BOLT ON LEAK CLAMP RATED AT 1,500 PSIG. FOLLOWING SUCCESSFUL INSTALLATION OF THE LEAK CLAMP THE LINE WAS BROUGHT BACK UP TO NORMAL OPERATING PRESSURE AND A TWO HOUR LEAK CONDUCTED. THE PRESSURE TEST WAS COMPLETED AT 1 A.M. ON SEPTEMBER 19. FOLLOWING VERIFICATION OF NO LEAKS FOR THE TWO HOUR TEST PERIOD THE LINE WAS PROPERLY WRAPPED AND COVER RE-ESTABLISHED BY SANDBAGGING. WHEN A FINAL COST OF REPAIRS IS CALCULATED A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED. SUPPLEMENTAL REPORT: CORRECTED THAT THE CAUSE OF THE LEAK WAS LOCALIZED PITTING DUE TO MICROBIOLOGICAL. SUPPLEMENTAL FINAL REPORT: THIS REPORT HAS BEEN REVISED TO REFLECT THAT CALCULATED COST OF REPAIR. CAUSE OF THE LEAK HAS BEEN DETERMINED TO BE ATTRIBUTED TO A LOCALIZED PIT WHICH WAS DUE TO MICROBIOLOGICAL INFLUENCED CORROSION (MIC). THIS REPORT IS CLOSED WITH NO FURTHER ACTIONS PENDING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070110 | 2007-09-24 09:58 | SUPPLEMENTAL FINAL | 4900 |  | KINDER MORGAN TEJAS PIPELINE | 500 DALLAS STREET SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 15 | 2007-08-25 | 2007 | HENDERSON | RUSK | TX | 75652 |  | 1483+50 | 3211.05 | 9452.34 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 10 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654471 | 348534.1071 | 586232.6749 | 287221 | 120731.3762 | 230250 | 291849.3506 | 137000 | 173651.9481 | NO | NO | YES | YES | 20 | PRECAUTIONARY | 3 |  | 846801 | 2007-08-25 | 686 | 730 | NO | YES | NO | NO | NO | NO | SUZIE DAVIS | 7133699707 | SUZANNE_DAVIS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 20 | 0.23 | 5LX60 | 60000 | ERW |  | YOUNGSTOWN | 1967 | UNDER GROUND |  | 264 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1967 | YES | 15 | 5 | [55 empty] | UNSCHEDULED RELEASE OCCURRED DUE TO INTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20070111 | 2007-09-24 19:36 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC. | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1500 | 2007-08-27 | 2007 | [6 empty] | N28 17.538 | W93 58.028 | OFFSHORE |  | HIGH ISLAND | 469 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199223 | 113481.5458 | 250892.4757 | 1923 | 808.3199 | 197300 | 250084.1558 | 0 | 0 | NO | NO | NO | NO | 0 |  | 48 |  | 847048 | 2007-08-27 | 850 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 8.63 | 0.32 | API 5L | 42000 | ERW |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1980 | YES | 0 | 6 | [55 empty] | OPERATIONS PERSONNEL SPOTTED GAS BUBBLES AT THE SURFACE NEAR HIGH ISLAND BLOCK 469. NOTIFICATIONS WERE MADE TO APPROPRIATE AGENCIES. A DIVE VESSAL AND DIVERS WERE SECURED AND PROCEEDED TO THE OFFSHORE SITE. LOCATION OF THE SUBSEA LEAK WAS FOUND. DOWNSTREAM MANUAL SUBSEA VALVE WAS CLOSED TO COMPLETELY ISOLATE THIS SECTION OF PIPELINE. THE LEAK STOPPED. PIPELINE HAS NOT BEEN REPAIRED AT THIS TIME. PIPELINE REMAINS ISOLATED ON BOTH ENDS AND BLED DOWN. NO FUTURE SERVICE FROM PIPELINE OWNERS HAS BEEN GIVEN AT THIS TIME.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070112 | 2007-09-25 | ORIGINAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1255 | 2007-08-14 | 2007 |  | MATAGORDA | TX |  |  |  | N 28 30 322 | W 95 58 200 | OFFSHORE |  | BRAZOS | 446L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 39931.8182 | 88727.2727 | 0 | 0 | 70000 | 88727.2727 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 0 | 8455811 | 2007-08-14 | 750 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER, VP- MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API 5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON AUGUST 14, 2007 PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 446-L. THE LEAK WAS DUE TO A SUBSEA HOLE IN 12" DIAMETER SEGMENT OF GAS PIPELINE. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE HAVING THE LEAK. THE LEAK WAS CLAMPED OFF DURING 9/2-3/07 AND SERVICE WAS REINSTATED INTO THE OFFSHORE LATERAL.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070113 | 2007-09-27 15:14 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1315 | 2007-08-28 | 2007 | CHOWCHILLA | MERCED | CA |  | MP 21.07 ( L-186) |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 24979.3672 | 50261.4464 | 8000 | 3362.7451 | 37000 | 46898.7013 | 0 | 0 | NO | NO | NO | YES | 5 | THREAT TO THE PUBLIC | 10 | 15 | 847383 | 2007-08-30 | 260 | 625 | NO | NO | YES | NO | NO | NO | RICHARD ARITA | 9259744313 | RTA2@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 6 | 0.19 | API 5L GRADE B | 35000 | ERW |  |  | 1954 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | NO | [40 empty] | THIRD PARTY CALLED IN DIG-IN AROUND 1:26 PM, 8/29/07. A CONTRACTOR WAS LEVELING DIRT ROAD AND DUG-IN TO 6-INCH LINE 186. THE DIG-IN OCCURRED IN RURAL AREA SOUTHEAST OF CHOWCHILLA, CA. THE AREA AROUND THE GAS LEAK WAS MADE SAFE. CNG WAS USED TO MAINTAIN SERVICE TO TWO DIARIES. THE LINE WAS BLOWN DOWN AT 11:30 PM, 8/29. THE REPAIR COMPLETED BY INSTALLING A 74 FEET SECTION OF PIPE. THE CONTRACTOR DID NOT CALL FOR USA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070114 | 2007-09-28 10:09 | ORIGINAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1350 | 2007-08-29 | 2007 | DONNER | TERREBONNE | LA | 70352 | 16.9 |  | 29.69329 | 90.967 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | THIRD PARTY DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140500 | 72719.6747 | 105230.0293 | 86000 | 36149.5098 | 54500 | 69080.5195 | 0 | 0 | NO | NO | NO | YES | 15 | PRECAUTIONARY | 4 | 30 | 847267 | 2007-08-29 | 700 | 859 | NO | NO | NO | NO | YES | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | TAP VALVE | [9 empty] | UNDER GROUND |  | 28 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 8 | 29 | 2007 | EXCAVATOR | YES |  | YES | ACCURATE | [37 empty] | GULF SOUTH PIPELINE VISITED THE SITE AN WORKED WITH THE PRODUCER AND EXCAVATOR OVER THE PAST SEVERAL MONTHS AT THIS SITE. THE THIRD PARTY WAS SCHEDULED TO CONNECT TO A GULF SOUTH PIPELINE USING AN EXISTING TAP AT THIS LOCATION. THE CONTRACTOR HAD MADE SEVERAL DIGS IN THE AREA TO LOCATE AN OLD LINE THEY PLANNED TO USE. HOWEVER IT DID NOT PASS THE PRESSURE TEST SO A NEW LINE WAS INSTALLED. THE NEW LINE WAS A BORE THAT WAS ABOUT 20 FEET OFF THE GULF SOUTH LINE AND WAS COMPLETED MONDAY, THE 27TH. THE PLAN WAS TO HAND DIG THE AREA NEAR THE TAP VALVE TO MAKE THE FINAL TIE-IN AFTER NOTIFYING GULF SOUTH TO SCHEDULE A TIME. THE EXCAVATOR CALLED AND LEFT A MESSAGE FOR GULF SOUTH EMPLOYEE ON CELL PHONE ABOUT 15-20 MINUTES BEFORE THE INCIDENT COMMUNICATING THAT THEY WERE GOING TO HAND DIG THE TAP AND GET THEIR TIE-IN MEASUREMENTS. GULF SOUTH EMPLOYEE DID NOT GET THE MESSAGE BEFORE THE INCIDENT AND THE NEXT CALL WAS TO COMMUNICATE THEY HIT THE TAP USING EXCAVATING EQUIPMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070115 | 2007-09-28 11:22 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC COMPANY | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 730 | 2007-09-13 | 2007 | AVENAL | KINGS | CA | 93203 | MP 354.1 (L-300B) |  | 36.073N | 120.087W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 234 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122500 | 68800.8578 | 144682.8606 | 12500 | 5254.2892 | 110000 | 139428.5714 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 | 0 | 848855 | 2007-09-14 | 635 | 840 | NO | NO | YES | NO | NO | NO | RICHARD ARITA | 9259744313 | RTA2@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 34 | 0.5 | API-5LX | 46000 | DSAW |  |  | 1950 | OTHER | BELLHOLE | 48 | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 2 |  |  | THE GAS CREW WAS PLANNING TO DRILL A "SNIFF" HOLE IN A DEPRESSURIZED TRANSMISSION PIPELINE (LINE 300A) AS PART OF THE REPLACEMENT OF A STATION VALVE V-56 WITHIN KETTLEMAN COMPRESSOR STATION. LINE 300B WAS EXCAVATED BY MISTAKE. AN EMPLOYEE RELIED ON THE EXISTING ABOVEGROUND PIPELINE MARKERS AND THEIR ALIGNMENT WITH VALVE 56. EXISTING PROCEDURE REQUIRES CONDUCTIVELY LOCATING THE PIPELINE. SUBSEQUENTLY, A 0.234-INCH HOLE WAS DRILLED INTO A PRESSURIZED GAS TRANSMISSION LINE (LINE 300B).
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070116 | 2007-10-01 | ORIGINAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE COMPANY | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1435 | 2007-08-27 | 2007 | WAVERLY | MORGAN | IL | 62692 | VS 0 | 0+28 | 39.34.49 N | 89.59.26 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29535 | 15160.8261 | 20886.7279 | 19535 | 8211.4032 | 10000 | 12675.3247 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 40 | 847045 | 2007-08-27 | 787 | 845 | NO | NO | NO | YES | NO | NO | BRIAN JIMENEZ - ASSOCIATE ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1986 | 8 | 0.18 | API 5L | 42000 | ERW |  | REPUBLIC | 1986 | UNDER GROUND |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1986 | NO | [57 empty] | THE LINE WHICH IS PART OF THE WAVERLY STORAGE FIELD, HAD AN AREA OF REDUCED WALL THICKNESS AT A LOW SPOT DUE TO INTERNAL CORROSION. NOTE: THE MAOP OF THIS LINE WAS ESTABLISHED USING THE CHARACTERISTICS OF THE STORAGE FORMATION AND NOT PIPE PROPERTIES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070117 | 2007-10-05 15:16 | SUPPLEMENTAL FINAL | 19160 | 19160 | TENNESSEE GAS PIPELINE | 1001 LOUISIANA | HOUSTON | HARRIS | TX | -77002 | 1350 | 2007-09-10 | 2007 | VENICE | PLAQUEMINES | LA | 70091 | LINE 527A-200 |  | 28.18.202 | -89.36.202 | OFFSHORE |  |  |  | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121200 | 69035.4278 | 152608.3079 | 1200 | 504.4118 | 120000 | 152103.8961 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 8484000 | 2007-09-10 | 900 | 1000 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12 | 0.31 | API 5L | 60000 |  |  | ARMSCO STEEL | 1967 | UNDER WATER |  | 48 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | SMALL BUBBLES WERE REPORTED IN THE VICINITY OF TGP'S 12" 527A-200 PIPELINE IN BASTIAN BAY NEAR THE EMPIRE WATERWAY. DIVERS DISCOVERD A PIN HOLE LEAK IN THE BODY OF THE PIPE. REPAIR WAS ACCOMPLISHED BY INSTALLING A CLAMP SEPTEMBER 17, 2007. THE PIPELINE WAS RETURNED TO SERVICE. SINCE THE REPAIR WAS ACCOMPLISHED BY INSTALLING A CLAMP AND NO PIPE WAS REMOVED FOR ANALYSIS, THE EXACT CAUSE COULD NOT BE ASCERTAINED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070118 | 2007-10-09 09:08 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINES/TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1000 | 2007-09-19 | 2007 | LINDEN | MARENGO | AL | 36748 | 819.22 |  | 32.2646 | -87.8351 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302977 | 146661.6605 | 127354.3027 | 302977 | 127354.3027 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 16 | 45 | 849296 | 2007-09-19 | 617 | 800 | YES | NO | NO | NO | NO | NO | M. CAMILA QUEZADA | 7132152749 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 48 | 0.42 |  | 65000 | SPIRAL |  | HOESH-A.G. ROHRENNERKE | 1990 | UNDER GROUND |  | 62 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | LOCALIZED CORROSION | YES | 1990 | NO | [57 empty] | OUR RESULTS DEMOSTRATE THAT THE IN-SERVICE LEAK WAS A RESULT OF METAL LOSS DUE TO PITTING CORROSION IN AN AREA WHERE THE FIELD JOINT COATING WAS NOT PROPERLY BONDED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070119 | 2007-10-09 11:26 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS COMPANY | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 2235 | 2007-09-14 | 2007 | CULLODEN | CRAWFORD | GA | 31016 | 358.099 | SOUTH MAIN SYSTEM | 32.835333 | -84.07549 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LIGHTNING IGNITED SMALL GAS LEAK OF UNKOWN ORIGIN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403419 | 229164.68 | 501858.16 | 11200 | 4707.8431 | 392219 | 497150.3169 | 0 | 0 | NO | YES | NO | YES | 30 | PRECAUTIONARY | 3 | 0 | 848936 | 2007-09-14 | 289 | 324 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | INSIDE METER STATION | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1953 | [6 empty] | VARIOUS SIZES AND MFRS. IN STATION | 1953 | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | DURING A THUNDERSTORM IN THE VICINITY OF CULLODEN, GA ON SEPTEMBER 14, 2007, LIGHTNING IS BELIEVED TO HAVE HIT SNG'S FORT VALLEY METER STATION. THIS IS BASED UPON INFORMATION OBTAINED FROM PEOPLE IN THE AREA. THE SPECIFIC SOURCE OF IGNITION IS UNKOWN BUT THE LIGHTNING IS BELIEVED TO HAVE IGNITED A SMALL GAS LEAK, A REGULATOR VENT DESIGNED TO RELEASE GAS AS PART OF NORMAL OPERATION, OR TO HAVE HIT AND BURNED THROUGH INSTRUMENTATION TUBING. THE STATION PIPING WAS HEAVILY DAMAGED DUE TO THE FIRE AND WILL REQUIRE REBUILDING. THE FIRE WAS DESCRIBED AS REACHING AS MUCH AS 60 FEET IN HEIGHT BUT WAS CONTAINED WITHIN A 150 FEET RADIUS. SNG'S CUSTOMER IS ON A TEMPORARY FEED UNTIL THE METER STATION REBUILD IS COMPLETED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070120 | 2007-10-09 14:44 | SUPPLEMENTAL FINAL | 2564 |  | COLORADO INTERSTATE PIPELINE COMPANY | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1205 | 2007-09-16 | 2007 | CARR | WELD | CO | 80612 | SECTION 85, M.P. 0.00 | IN COMPRESSOR STA. YARD | 40.952621 | -104.796602 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | INSTALLATION SPECIFICATIONS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2209300 | 1259501.8382 | 2792480.6197 | 9300 | 3909.1912 | 2200000 | 2788571.4286 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 10 | 849020 | 2007-09-16 | 1000 | 1000 | YES | NO | NO | NO | NO | YES | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2005 | 6.63 |  | API 5L |  |  | RELIEF VALVE | ANDERSON GREENWOOD | 2005 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | SEE EXPLANATION UNDER PART G. |  | THE INVESTIGATION INTO THIS OCCURRENCE INDICATED THAT DURING THE VENTING OF GAS FROM A 6" RELIEF VALVE ON THE SUCTION SIDE OF THE COMPRESSOR YARD PIPING AN UNCONTROLLED GAS RELEASE OCCURRED AT A BREACH IN THE FLANGED CONNECTION DIRECTLY UNDER THE RELIEF VALVE. THE BREACH MOST LIKELY OCCURRED AS A RESULT OF IMPROPER TORQUING OF THE NUTS AND BOLTS ON THE FLANGE DURING CONSTRUCTION. INDICATIONS SUGGEST THE ESCAPING GAS WAS IGNITED BY AN EXTERNAL UTILITY HEATER. THE STATION SUSTAINED SEVERE PROPERTY DAMAGE, BUT THERE WERE NO PERSONAL INJURIES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070121 | 2007-10-11 14:34 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1010 | 2007-09-21 | 2007 | DOWNSVILLE | UNION | LA | 71234 |  | 773+79 | +32.6589 | -92.3693 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | DAMAGED VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10104 | 4891.0294 | 4247.1471 | 10104 | 4247.1471 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 7 | 849495 | 2007-09-21 | 920 | 1200 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | VALVE | 1996 | [5 empty] | 1" BALL VALVE | STOCKHAM | 1996 | OTHER | VALVE JUST UNDER SURFACE OF GROUND PLUG EXPOSED |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON LINE F-EAST WHILE A CONTRACTOR WAS MOWING THE RIGHT-OF-WAY THE CONTRACTOR HIT AN EXPOSED PLUG OF A 1" BALL VALVE THAT WAS JUST UNDER THE SURFACE OF THE GROUND. THE PLUGGED VALVE WAS INSTALLED FOR A TAP THAT WAS NEVER PLACED IN SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070122 | 2007-10-11 17:37 | SUPPLEMENTAL FINAL | 31531 | 30630 | ONEOK WESTEX TRANSMISSION | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103 | 1330 | 2006-12-05 | 2006 | ANTHONY | EL PASO | TX |  | BLK A-87 SEC 161 | NORTENO 5 | N32 00.069' | W106 36.263' | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74171 | 34599.8512 | 33614.369 | 69671 | 27755.1138 | 4500 | 5859.2551 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 |  |  | 35 | 60 | NO | YES | NO | NO | NO | NO | STEVE BUSTOS | 8067473037 | SBUSTOS@ONEOK.COM | TRANSMISSION | OTHER | WELD-CONSTRUCTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 4 | 188 | X-42 | 1664 | UNKNOWN | ANSI 150 | UNKNOWN |  | UNDER PAVEMENT |  | 84 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | PIN HOLE IN WELD | OTHER | CONSTRUCTION | YES | 1977 | NO | [57 empty] | GAS LEAK WAS DETERMINED DURING ANNUAL LEAK SURVEY ON SEPTEMBER 14, 2006. GAS LEAK DETECTED WAS 1.4% IN CASING PIPE AND NOT MIGRATING. LEAK WAS MONITORED WEEKLY UNTIL REPAIRS WERE MADE ON DECEMBER 5, 2006. 1APR10 - ADDED OWNER IDENTIFICATION NUMBER, FINALIZED REPORT. PATTI FORD, ONEOK PARTNERS, SR PIPELINE SAFETY ENGINEER, (918) 588-7131 PATTI.FORD@ONEOK.COM
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070123 | 2007-10-22 18:53 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE COMPANY OF AMERICA | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 145 | 2007-10-15 | 2007 | ROCK FALLS | WHITESIDE | IL | 61071 | 48 | 1810+90.7 | 41.68053 | -89.65220 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1382700 | 676465.8066 | 651271.0135 | 1300000 | 546446.0784 | 77700 | 98487.2727 | 5000 | 6337.6623 | NO | NO | NO | YES | 11 | PRECAUTIONARY | 2 | 30 | 851-594 | 2007-10-15 | 772 | 800 | NO | YES | NO | NO | NO | NO | KRISTIN VAN DER LAAN | 3039147753 | KRISTIN_VANDERLAAN@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 24 | 0.25 | 5LX60 | 60000 | EFW | N/A | A.O. SMITH | 1964 | UNDER GROUND |  | 60 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | LOCALIZED PITTING ASSOCIATED WITH SCC | STRESS CORROSION CRACKING |  | YES | 1964 | NO | [57 empty] | ON THE MORNING OF OCTOBER 15, 2007 A FAILURE OCCURRED ON THE #2 ILLINIOS LATERAL, MILE 48, WHITESIDE COUNTY, ILLINOIS. THE FAILURE OCCURRED IN A RURAL FARM AREA. THERE WERE NO INJURIES, NO FIRE, AND MINIMAL PROPERTY DAMAGE ASSOCIATED WITH THIS INCIDENT. THERE WERE NO CUSTOMER INTERUPTIONS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070124 | 2007-10-25 19:35 | SUPPLEMENTAL FINAL | 19892 |  | UCAR PIPELINE INCORPORATED | P.O. BOX 186 | PORT LAVACA | CALHOUN | TX | 77979 | 312 | 2007-10-18 | 2007 | PORT ARTHUR | JEFFERSON | TX | 77640 | VALVE 30 |  | 29.9244177 | 93.9716619 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357658 | 190580.9726 | 321471.3305 | 155658 | 65429.7721 | 200000 | 253506.4935 | 2000 | 2535.0649 | NO | YES | NO | NO | 0 |  | 96 |  | 851922 | 2007-10-18 | 1440 | 1585 | NO | YES | NO | NO | NO | NO | RICHARD L. SCOTT | 3615533005 | SCOTTRL1@DOW.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 6 | 0.25 | 5LX-42 | 42000 | ERW |  | REPUBLIC | 1977 | OPEN DITCH |  | 0 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | IMPROPER APPLICATION | YES | 1967 | NO
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070125 | 2007-10-19 | ORIGINAL FINAL | 15931 |  | PUBLIC SERVICE COMPANY OF COLORADO | P.O. BOX 840 | DENVER | DENVER | CO | 80201 | 1330 | 2007-09-28 | 2007 | LOVELAND | LARIMER | CO | 80537 | 1400' W. OF TAFT AVE | 14 + 14 | 40. 22. 695' | 105. 06. 103' | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74060 | 39737.4889 | 69254.1326 | 29060 | 12215.1716 | 45000 | 57038.961 | 0 | 0 | NO | NO | NO | YES | 198 | PRECAUTIONARY | 0 | 35 | 850250 | 2007-09-29 | 475 | 960 | NO | YES | NO | NO | NO | NO | PATRICK KREAGER, MANAGER GAS FIELD OPERATIONS | 9702257865 | PAT.KREAGER@EXELENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 6 | 0.19 | API 5L GRADE B | 35000 | SEAMLESS |  |  |  | UNDER PAVEMENT |  | 63 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | YES | 9 | 6 | 2007 | ONE-CALL SYSTEM | NO | [40 empty] | INCIDENT SUMMARY 9/28/07: THE EXISTING 6" MW STEEL GAS TRANSMISSION MAIN LOCATED AT SW 14TH STREET AND TYLER AVENUE IN LOVELAND, COLORAD WAS DAMAGED AND PUNCTURED BY A BORING CONTRACTOR INSTALLING ELECTRIC DUCTS ACROSS SW 14TH STREET. A LOCATE REQUEST WAS MADE BY THE CONTRACTOR ON 9/4/07 TO THE UTILITY NOTIFICATION CENTER OF COLORADO. FIELD LOCATES WERE TO BE COMPLETED BY END OF DAY ON 9/06/07. ALL OTHER KNOWN UTILITIES THAT WERE TO BE CROSSED BY THE BORE WERE PHYSICALLY MARKED IN THE FIELD, BUT THE GAS LINE WAS NOT MARKED. ALL KNOWN UTILITIES HAS BEEN POTHOLED BY THE CONTRACTOR PRIOR TO BORING TO DETERMINE ACTUAL DEPTHS. THE CONTRACTOR HAD COMPLETED THE BORE FROM THE NORTH SIDE OF THE STREET TO THE SOUTH SIDE WITHOUT INCIDENT. THE WERE IN THE PROCESS OF PULLING BACK AN 18" REAMER WITH THREE 6" PVC CONDUITS WHEN THE TOP OF THE GAS MAIN WAS DAMAGED AND PUNCTURED. THE DAMAGED OCCURED AT APPROXIMATELY 13:30 ON 9/28/07 AND THE BLOWING GAS WAS SHUT OFF BY 04:35 ON 9/29/07.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20070127 | 2007-10-31 09:23 | SUPPLEMENTAL FINAL | 19570 |  | TRANSCONTINENTAL GAS PIPE LINE COMPANY | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1755 | 2007-10-17 | 2007 | GIBSON | TERREBONNE | LA | 70356 | 101.92 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 36647.6159 | 78153.6637 | 5000 | 2101.7157 | 60000 | 76051.9481 | 0 | 0 | NO | NO | NO | NO | 0 |  | 18 | 50 | 851098 | 2007-10-17 | 830 | 1169 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 30 | 0.41 | API 5LX | 60000 | DSAW | GATE | KAISER STEEL | 1965 | UNDER WATER |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1965 | NO | [57 empty] | A LEAK (BUBBLES AND SHEEN) ON SELA LINE B WAS REPORTED ON 10/17/07 AT THE HANSON CANAL CROSSING. THE LINE WAS ISOLATED AND CONTAINMENT BOOMS DEPLOYED. BLOWDOWN OF THE LINE SEGMENT WAS COMPLETED, THE LEAKS STOPPED, AND CLEAN UP WAS COMPLETED. THE PIPELINE HAS BEEN DEACTIVATED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070129 | 2007-11-06 18:42 | SUPPLEMENTAL FINAL | 2748 |  | CONSUMERS ENERGY | 1945 W PARNALL ROAD | JACKSON | JACKSON | MI | 49201 | 1517 | 2007-10-08 | 2007 | ALLEGAN | ALLEGAN | MI | 49314 |  |  | 42.7256 | 85.8209 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 12 | 703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | YES | 10 | THREAT TO THE PUBLIC | 0 | 25 | 851071 | 2007-10-08 | 1467 | 1674 | NO | NO | NO | NO | YES | NO | JOAQUIN J AFFONSO JR | 5177881835 | JJAFFONSO@CMSENERGY.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 12 | 0.38 | API5LX-52 | 52000 | ERW |  | US STEEL COMPANY | 1960 | UNDER GROUND |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | SEAM | OTHER | SEE PART G | YES | 1962 | NO | [57 empty] | THE PIPELINE FAILURE OCCURRED ON A 12- INCH STORAGE FIELD LINE OPERATING IN A CLASS 1 AREA AND WAS IN A NORMAL OPERATING POSITION AT THE TIME OF THE FAILURE. THE PIPELINE WAS A SECTION OF THE MAIN LINE BETWEEN THE COMPRESSOR STATION AND THE STORAGE FIELD. THE LINE WAS BEING USED AS A STORAGE FIELD INJECTION LINE OPERATING AT 1,467 PSIG WHEN THE INCIDENT OCCURRED. THE LINE RUPTURED, IGNITED AND WAS SHUT IN BY STORAGE FIELD PERSONNEL BY CLOSING SYSTEM VALVES. THE SYSTEM WAS SHUT IN AND THE FIRE WAS EXTINGUISHED IN 27 MINUTES FROM THE TIME OF RUPTURE. POOR SEAM QUALITY AND CORROSION WERE IDENTIFIED AS THE CAUSE OF THE FAILURE. SEAM DEFECTS, SEAM POSITION, EXPANSION AND CONTRACTION ASSICIATED WITH NORMAL OPERATING PRESSURES, AND CREVICE CORROSION WERE CONTRIBUTING FACTORS TO THE FAILURE. THE TELEPHONIC REPORT WAS SUBMITTED ON OCTOBER 8, 2007 TO MR. SNOWDEN AND THE REPORT NUMBER WAS 851071. THIS REPORT IS BEING SUBMITTED TO CORRECT A DATE ERROR IN PART A, ITEM 7, TELEPHONIC REPORT DATE FROM 2002 TO 2007.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070130 | 2007-11-07 19:41 | SUPPLEMENTAL FINAL | 207 |  | ALASKA PIPELINE COMPANY | 401 E. INTERNATIONAL AIRPORT ROAD | ANCHORAGE | ANCHORAGE | AK | 99518 | 918 | 2007-11-04 | 2007 | ANCHORAGE | ANCHORAGE | AK | 99515 |  |  | 61.06.31N | 149.48.15W | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | BROKE 1/4 NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50500 | 28764.7616 | 63586.7949 | 500 | 210.1716 | 50000 | 63376.6234 | 0 | 0 | YES | NO | NO | NO | 0 |  |  | 38 | 853429 | 2007-11-02 | 500 | 685 | NO | YES | NO | NO | NO | NO | DAVE BREDIN | 9072643745 | DAVE.BREDIN@ENSTARNATURALGAS.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1983 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | AT 0918 ON NOVEMBER 2, 2007 ENSTAR/ALASKA PIPELINE COMPANY WAS NOTIFIED BY ANCHORAGE FIRE DEPARTMENT THAT A PICK-UP TRUCK HAD SLID OFF THE ROAD INTO A DISTRICT PRESSURE REGULATOR STATION AT THE CORNER OF ELMORE ROAD AND HUFFMAN ROAD. THE ROADS WERE SNOW COVERED AND WET. NATURAL GAS WAS REPORTED TO BE BLOWING FROM THE STATION. EMPLOYEES WERE DISPATCHED TO THE LOCATION AND FOUND THE STATION PIPING BENT AND GAS BLOWING FROM A 1/4" NIPPLE THAT HAD BROKEN. THE STATION WAS SHUT OFF AT THE UNDEGROUND INLET VALVE AND OUTLET VALVE AT 0954 TO STOP THE BLOWING GAS. THE STATION WAS EXCAVATED AND ALL PIPING WAS INSPECTED AND REPLACED WHERE DAMAGED. THE STATION WAS PUT BACK IN SERVICE ON NOVEMBER 5, 2007. NO CUSTOMERS WERE WITHOUT GAS AS THIS SYSTEM IS BACKFED BY MULTIPLE REGULATOR STATIONS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070132 | 2007-11-14 11:51 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1600 | 2007-10-14 | 2007 |  |  | LA |  | 527A-300 |  | 2902.397 | -8936.458 | OFFSHORE |  | WEST DELTA | 61 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472000 | 257592.4465 | 483904.7651 | 135000 | 56746.3235 | 337000 | 427158.4416 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 851582 | 2007-10-14 | 800 | 1264 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 30 | 0.5 | API 5L | 60000 | DSAW |  | US STEEL |  | UNDER WATER |  | 120 | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | THE UNITED STATES COAST GUARD (USCG) REPORTED A SHEEN IN THE VICINITY OF TENNESSEE GAS PIPELINE (TGP) COMPANY'S 30-INCH 527A-300 PIPELINE. TGP CONFIRMED THE PRESENCE OF BUBBLES AS WELL, PLOTTED COORDINATES, AND DETERMINED THAT A GAS LEAK HAD OCCURRED ON THE 527A-300 PIPELINE. DIVERS DETERMINED THE PRESENCE OF A PINHOLE ON THE PIPE AT THE 6 O'CLOCK POSITION. A CLAMP WAS INSTALLED TO REPAIR THE LEAK. REPAIRING WITH A CLAMP PRECLUDED THE REMOVAL OF PIPE FOR ANALYSIS SO THE EXACT CAUSE OF THE LEAK COULD NOT BE ASCERTAINED. THIS PIPELINE WAS INITIALLY RESTORED TO SERVICE BUT, WITH THE REROUTING OF GAS, THE LINE IS NOW PLANNED FOR ABANDONMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070133 | 2007-11-15 08:51 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 851 | 2007-11-03 | 2007 | PERRYTON | OCHILTREE | TX | 79070 | TX-047 | SEC 929, BLK43,H&TC RR SU | N36.37938 | W-100.82660 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | PERRYTON/BARLOW DEHYDRATOR FIRE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152907 | 87226.4932 | 193814.587 | 0 | 0 | 152907 | 193814.587 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 853502 | 2007-11-03 | 216 | 1000 | NO | YES | NO | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | GLYCOL DEHYDRATOR UNIT | STEEL |  | NO | NO | NO | OTHER | GLYCOL DEYDRATOR UNIT | 1961 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | INVESTIGATION INDICATES THAT IT APPEARS THAT THE GLYCOL RECICULATING PUMPS STOPPED OPERATING. THE LOSS OF THE GLYCOL CIRCULATION ALLOWED THE MIXTURE OF HYDROCARBON CONDENSATE AND GLYCOL TO DRAIN BACK TO THE OVERFLOW TANK AND SPILL ONTO THE VFD FROM THE TANK VENT STACK CAUSING A FIRE. |  | ON NOVEMBER 3, 2007 @ APPROXIMATELY 8:51 A.M. THE TEXAS OCHILTREE COUNTY SHERIFF'S DEPARTMENT RECEIVED A 911 CALL REPORTING A FIRE AT NORTHERN'S PERRYTON-BARLOW FIELD COMPRESSOR STATION. NORTHEN WAS IMMEDIATELY NOTIFIED AN PERSONNEL WERE DISPATCHED. UPON ARRIVAL IT WAS CONFIRMED THAT THE GLYCOL DEHYDRATOR UNIT, LOCATED AT THE PERRYTON-BARLOW COMPRESSOR STATION WAS ON FIRE. AFTER ASSESSING THE SITUATION, AND TAKING INTO CONSIDERATION THE PROXIMITY OF THE FIRE TO THE EMERGENCY BLOW-DOWN PIPING, IT WAS DETERMINED THAT THE EMERGENCY SHUTDOWN SYSTEM FOR THE STATION COULD SAFELY BE ACTIVATED. THE LOCAL FIRE DEPARTMENT EXITINGUISHED THE FIRE. INVESTIGATION INTO THE INCIDENT FOUND THAT THE FIRE HAD OCCURRED ON THE DEHYDRATOR SKID WITH MOST OF THE DAMAGE CENTERED AT THE VARIABLE FREQUENCY DRIVE (VFD) FOR THE GLYCOL PUMPS, WHICH IS BELIEVED TO BE THE ORIGIN OF THE FIRE. IT APPEARS THE FIRE WAS FUELED BY HYDROCARBON CONDENSATE AND GLYCOL SPILLING OUT THE OVERFLOW VENT STACK, LOCATED ON THE DEHYDRATOR SKID, ONTO THE VFD CONTROLS FOR THE VFD. THE POSITIONING OF THE VFD AS IT RELATED TO THE OVERFLOW VENT STACK WAS A CONTRIBUTING FACTOR. ADDITIONAL INVESTIGATION INDICATES THAT AS SOME POINT THE GLYCOL RECIRCULATING PUMPS MUST HAVE STOPPED WORKING WHICH ALLOWED THE MIXTURE OF HYDROCARBON CONDENSTATE AND GLYCOL TO DRAIN BACK TO THE OVERFLOW TANK RESULTING IN A SPILL FROM THE OVERFLOW PIPING ONTO THE VFD CONTROLS. NORTHERN IS CURRENTLY WORKING WITH EQUIPMENT VENDORS TO ACQUIRE COST AND AVILABILITY OF REPLACING THE DEHYDRATOR UNIT. A CURRENT ESTIMATE OF REPLACEMENT IS ESTIMATED AT APPROXIMATELY $140,000. SUPPLEMENTAL REPORT FILED TO INDICATE/CLARIFY PART A, ITEM G CLASS LOCATION DESCRIPTION IS: ONSHORE, CLASS 1. SUPPLEMENTAL/FINAL REPORT - A FINAL COST OF $152,907 HAS BEEN DETERMINED TO REPLACE THE DAMAGED DEHY UNIT AND THE ASSOCIATED ELECTRICAL AND CONTROL PANELS. THIS ITEM IS CONSIDERED CLOSED WITH NO FURTHER ACTIONS PLANNED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070134 | 2007-11-15 11:33 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1350 | 2007-11-07 | 2007 | VOLGA | BROOKINGS | SD | 57071 | BETWEEN MP 23.71 AND 24.7 | NW1/4SEC14,T110N,R51W | 44.33060 | 96.92040 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48015 | 25730.2968 | 44580.1341 | 19217 | 8077.7341 | 28798 | 36502.4 | 0 | 0 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 1 |  | 853899 | 2007-11-07 | 691 | 800 | NO | YES | NO | NO | NO | NO | BYRON H. WOOD | 4023987397 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 6.63 | 0.25 | 5L | 35000 |  |  | KAISER |  | UNDER GROUND |  | 41 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 11 | 6 | 2007 | ONE-CALL SYSTEM | YES |  | YES | [38 empty] | ON NOVEMBER 7, 2007 AT APPROXIMATELY 13:50 A NORTHERN NATURAL GAS EMPLOYEE REPORTED TO NORTHERN'S OMAHA OPERATIONS COMMUNICATIONS CENTER THAT HE HAD RECEIVED A CALL FROM THE CITY OF VOLGA, SD CONCERNING A LINE HIT ON THE NORTH SIDE OF THE CITY BY BOWES CONSTRUCTION. GAS WAS BLOWING FROM THE DAMAGED PIPELINE. IT WAS DETERMINED THAT IT WAS THE 6 INCH BROOKINGS BRANCHLINE, SDB91901. PERSONNEL WERE DISPATCHED TO THE SITE. THE LOCAL FIRE DEPARTMENT EVACUATED APPROXIMATELY 20 PEOPLE WITHIN 1,000 FEET OF THE LINE HIT. THE LINE WAS ISOLATED AND BLOWN DOWN. AN APPROXIMATE 3 TO 4 INCH PUNCTURE AND A DENT WAS FOUND. A 10 FOOT SECTION OF PIPE HAD TO BE REPLACED. THERE WAS BLOWING GAS BUT NO FIRE AND NO INJURIES. THERE WAS NO LOSS OF SERVICE TO ANY TOWNS. THE EXCAVATION CONTRACTOR HAD MADE A 1 CALL TO THE SOUTH DAKOTA ONE CALL CENTER ON 11/6/07. IT STATED THAT WORK WAS SCHEDULED TO COMMENCE ON 11/08/07 AT APPROXIMATELY 10:37 A.M.. NORTHERN PERSONNEL WERE SCHEDULED TO LOCATE THE LINE THE MORNING OF 11/8/07. THE CONTRACTOR DID NOT WAIT THE REQUIRED 48 HOURS AND INSTEAD COMMENCED CONSTRUCTION ACTIVITIES ON 11/7/07, ONE DAY PRIOR TO THE DAY AND TIME REQUESTED FOR LOCATION OF THE LINE.THERE WERE PERMANENT PIPELINE MARKER SIGNS IN THE AREA OF THE PIPELINE. THE EXCAVTOR WAS PREPARING A ROAD BED AT THE TIME OF THE INCIDENT. HE REMOVED APPROXIMATELY 30 INCHES OF COVER FROM OVER THE PIPELINE THAT ORIGINALLY HAD APPROXIMATELY 42 INCHES OF COVER. HE WAS IN THE PROCESS OF UTILIZING A "RIPPER" TO MIX THE WET SOIL THAT WAS IN THE AREA OF THE PIPELINE TO PROVIDE DRAINAGE FOR THE ROAD THEY WERE INSTALLING WHEN THE RIPPER TEETH STUCK AND PUNCTURED THE PIPELINE. NORTHERN FOLLOWED UP WITH MEETINGS WITH THE CONTRACTOR ON EXCAVATION SAFETY AND WILL BE FOLLOWING UP WITH NOTIFICATION OF A VIOLATION OF THE SOUTH DAKOTA STATE ONE CALL. A SUPPLEMENTAL/FINAL REPORT WILL BE FILED WHEN FINAL COST OF GAS LOSS AND DAMAGE IS DETERMINED. IT IS EXPECTED THAT THE COST WILL EXCEED THE $50K REPORTING THRESHOLD. SUPPLEMENTAL/FINAL REPORT - A TOTAL COST OF REPAIR FOR THIS LINE DAMAGE HAS BEEN CALCULATED AT $45,135.00. ALL THOUGHT THE FINAL COST IS LESS THAN THE $50,000 REPORTING THRESHOLD THIS INCIDENT WAS/IS STILL REPORTABLE AS THE LOCAL FIRE DEPARTMENT CONDUCTED PRECAUTIONARY EVACUATION OF APPROXIMATELY 20 PEOPLE WITH APPROXIMATELY 1,000 FEET OF THE LINE HIT SITE. SUPPLEMENTAL/FINAL REPORT - THIS REPORT IS BEINGING UPDATED TO REFLECT THE FINAL SUMMARY OF THIS INCIDENTS COSTS WHICH HAS BEEN CALCULATED AS $48,015.00.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070135 | 2007-11-16 11:06 | ORIGINAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 1639 | 2007-10-17 | 2007 | BASTROP | MOREHOUSE | LA | 71220 | MP 55+3899 |  | 32.960 | 91.854 | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | OTHER | ESD SYSTEM ACTIVATED AND ONE VALVE DID NOT CLOSE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155650 | 75345.2819 | 65426.4093 | 155650 | 65426.4093 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 851906 | 2007-10-17 | 495 | 840 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | OTHER | VALVE MLS-7-85 |  |  | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ESD VALVE DID NOT CLOSE COMPLETELY WHEN ESD ACTIVATED |  | THE PURCHASED POWER TO THE STATION WAS LOST DURING A THUNDER STORM AND THE STAND-BY POWER DID NOT WORK. THE INSTRUMENT AIR COULD NOT BE MAINTAINED BECAUSE OF THE LOSS OF POWER AND SUBSEQUENTLY CAUSED ACTIVATION OF THE ESD SYSTEM. THE SUCTION VALVE ONLY PARTIALLY CLOSED ALLOWING ADDITIONAL GAS TO ESCAPE. THE VALVE ACTUATED PROPERLY THE DAY BEFORE DURING THE ESD SYSTEM TEST. AND WHEN IT WAS CHECKED THE DAY AFTER IT ALSO WORKED PROPERLY. IT IS BELIEVED THAT THE CAUSE OF THE VALVE NOT FULLY CLOSING CAN BE ATTRIBUTED TO THE LEVEL OF RELIABILITY OF THE CONTROLS. NEW CONTROLS HAVE BEEN PURCHASED AND WILL REPLACE THE EXISTING CONTROLS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070136 | 2007-11-21 10:30 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1735 | 2007-10-25 | 2007 |  |  |  |  | 821E-1100 | 583+63 | 29.512451 | -93.999980 | OFFSHORE |  | HIGH ISLAND | 21 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 77272.0588 | 152038.8655 | 30000 | 12610.2941 | 110000 | 139428.5714 | 0 | 0 | NO | NO | NO | NO | 0 |  | 35 | 0 | 852716 | 2007-10-25 | 1050 | 1440 | YES | NO | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12.75 | 0.5 | API 5L | 52000 |  |  |  |  | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | BLEEDER ON SIDE OF BY-PASS VALVE | [8 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | BUBBLES WERE REPORTED IN THE VICINITY OF TENNESSEE GAS PIPELINE (TGP) COMPANY'S 12"821E-1100 PIPELINE. UPON INVESTIGATION, DIVERS DISCOVERD LEAK TO BE COMING FROM A BLEEDER ON THE SIDE OF A 2" BY-PASS VALVE AT A TIE-IN LOCATION. THE BLEEDER WAS REMOVED AND A PLUG WAS INSTALLED IN ITS PLACE TO STOP THE LEAK. PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070137 | 2007-11-26 15:21 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 602 | 2007-11-13 | 2007 | VERGENNES | JACKSON | IL | 62994 | 936 | 49445+99 | 37.907642 | -89.388614 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223564 | 113553.6124 | 146277.368 | 161826 | 68022.4485 | 61738 | 78254.9195 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 854393 | 2007-11-13 | 680 | 858 | YES | NO | NO | NO | NO | NO | SUZANNE DAVIS | 7133699707 | SUZANNE_DAVIS@KINDERMORGAN.COM | TRANSMISSION | OTHER | 2 INCH BRANCH PIPE | STEEL |  | NO | NO | NO | OTHER | 2 INCH BRANCH PIPE | 1969 | 2 | 0.22 | GRD B | 6425 | SMLS | NA | US STEEL | 1969 | UNDER GROUND |  | 102 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | HOT TAP |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 8 | 20 | 1969 | WATER |  | 24 | 1140 | [12 empty] | A LEAK WAS REPORTED TO GAS CONTROL BY A LANDOWNER NEAR THE VERGENNES, ILLINOIS AMEREN CIPS METER SITE SIDE TAP VALVE ON GULF COAST #3. THE SIDE TAP WAS EXCAVATED AND THE LEAK WAS IDENTIFIED AS A CIRCUMFERENTIAL CRACK AT THE FILLET WELD OF THE 2" BRANCH PIPE AND 2" ON 36" SADDLE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20070138 | 2007-11-28 13:43 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 840 | 2007-10-29 | 2007 | SLAUGHTERS | WEBSTER | KY | 42456 | MP 470.6778 |  | 37D 30M | 87D 30M | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | SEE PART G. | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 288000 | 164290.9091 | 365049.3506 | 0 | 0 | 288000 | 365049.3506 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 0 | 852967 | 2007-10-29 | 738 | 840 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 9858981006 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | OTHER | PIG TRAP DOOR | STEEL |  | NO | NO | NO | OTHER | PIG TRAP | 1959 | 30 | 0.5 | X-52 | [5 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | PIG TRAP VALVE WAS LEAKING CAUSING BUILDUP OF PRESSURE BEHIND PIG. INVESTIGATION COMPLETE. |  | INCIDENT OCCURRED DURING LAUNCH OF PIG AFTER BLOWING DOWN PIPING AND OPENING PIG TRAP DOOR TO CHECK POSITION OF PIG. PIG DISLODGED AND BROKE OFF DOOR WHILE EXITING LAUNCHER PINNING EMPLOYEE BETWEEN DOOR AND BACKHOE LOCATED APPROXIMATELY 4 FEET BEHIND LAUNCHER. INVESTIGATION COMPLETE
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070139 | 2007-12-04 10:53 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 214 | 2007-11-07 | 2007 | [6 empty] | 29.16.18.00 | 92.21.22.80 | OFFSHORE |  | VERMILLION | 76 | LA | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77200 | 43952.705 | 97006.3172 | 1000 | 420.3431 | 76200 | 96585.974 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 853898 | 2007-11-07 | 128 |  | NO | YES | NO | NO | NO | NO | MARK NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 36 | [7 empty] | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | OTHER | NOT KNOWN | NO |  | NO | [57 empty] | OFFSHORE LEAK. LINE HAS BEEN DEGASSED IN PREPARATION OF ABANDONING THE COLUMBIA GULF'S LINE 200. LEAK COORDINATES: X= 1,673,821.20 Y= 221,465.08 LAT.: 29 DEG 16' 18.00 N LONG.: 92 DEG 21' 22.80 W LINE IS SCHEDULED FOR ABANDONMENT IN 2012.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070140 | 2007-12-05 | SUPPLEMENTAL FINAL | 32099 |  | ENERGY TRANSFER COMPANY | 711 LOUISIANA ST., STE. 900 | HOUSTON | HARRIS | TX | 77002 | 100 | 2007-10-27 | 2007 | 1798 (NEAR CR 3148D) | MINDEN RUSK | TX | 75681 | BETWEEN MLV 15 & 16 | 7827+81 | N 31.98251 | W 94.73444 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153461 | 74285.6556 | 64506.2782 | 153461 | 64506.2782 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  |  | 2007-10-26 | 900 | 973 | NO | YES | NO | NO | NO | NO | DANNY NICHOLS, DIRECTOR OF REGULATORY COMPLIANCE | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | BRANCH | STEEL |  | NO | NO | NO | PIPELINE |  | 2000 | 30 | 312 | API 5L | 65000 | SAW | ANSI 600 BALL AVENUE | KF VALVES | 2000 | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | OTHER | WELDED | [6 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 11 | 29 | 2000 | INERT GAS |  | 1 | 650 | [12 empty] | ETC WAS NOTIFIED OF A GAS LEAK, ON A LATERAL TAP, OFF THE TEXOMA 30" DURING THE EVENING OF 10/26/07. THE LEAK WAS ON A FILLET WELD THAT HAD BEEN PREVIOUSLY HOT-TAPPED ONTO THE 30". COORDINATION WAS MADE WITH DELIVERY MARKETS AND WELL PROCEDURES, TO ALLOW FOR THE LINE TO BE SHUT-IN. MAINLINE VALVES WERE CLOSED ON EACH SIDE OF THE LEAK SITE AND GAS PRESSURE WAS VENTED THROUGH THE BLOW DOWN VALVES. GAS PRESSURE WAS OFF BY 6:45 AM ON 10/27/07 AND REPAIRS BEGAN. APPROXIMATELY 41 FOOT OF PIPE WAS REPLACED WITH PRETESTED PIPE. PURGING AND PACKING WAS COMPLETED BY 9:20 PM ON 10/27/07 ALLOWING THE LINE TO BE PLACED BACK INTO SERVICE. FINAL UPDATE 01/04/2010: PREVIOUS OPERATING PROCEDURES WERE REVISED BY CURRENT OPERATOR. CONSTRUCTION PRACTICES NOW REQUIRE SUPPORTING BRANCH CONNECTIONS TO ENSURE PROPER INSTALLATION, FITTING AND REINFORCEMENT. MAG PARTICAL INSPECTIONS ARE REQUIRED INADDITION TO PRESSURE TESTS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070141 | 2007-12-08 | ORIGINAL FINAL | 32005 |  | CROSSTEX LIG, LLC | 2501 CEDAR SPRINGS SUITE 100 | DALLAS | DALLAS | TX | 75201 | 858 | 2007-10-30 | 2007 | LOGANSPORT | DESOTO | LA | 71049 | UNKNOWN | UNKNOWN | 31.97211N | 93.96427W | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | OTHER | 2-INCH BELOW GROUND TAP BROKEN OFF | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 31202.2282 | 68019.9071 | 2000 | 840.6863 | 8000 | 10140.2597 | 45000 | 57038.961 | NO | NO | NO | YES | 6 | PRECAUTIONARY |  | 45 | 853067 | 2007-10-30 | 457 | 500 | NO | NO | YES | NO | NO | NO | WILLIAM S. BYRD MANAGER NORTHERN AREA | 3186195662 | WILLIAM.BYRD@CROSSTEXENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 2 | 0.15 | ASTM 106 | 35000 | SEAMLESS | PLUG | ROCKWELL |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | ON OCTOBER 30, 2007, AT 0927 HOURS, CROSSTEX LIG, L.L.C. (CROSSTEX), A SUBSIDIARY OF CROSSTEX ENERGY SERVICES, L.P. REPORTED A NATURAL GAS AND CONDENSATE RELEASE FROM THEIR 6-INCH UNDERGROUND TRANSMISSION PIPELINE IN DE SOTO PARISH, LOUISIANA. THE RELEASE WAS CAUSED BY A BACKHOE STRIKING AND DAMAGING THE PIPELINE DURING EXCAVATION. CROSSTEX REPORTED THE UNAUTHORIZED RELEASE TO THE LOUISIANA EMERGENCY HAZARDOUS MATERIALS HOTLINE (INCIDENT NO. 07-06604), AND THE NATIONAL RESPONSE CENTER (NRC) WAS ALSO NOTIFIED OF THE EVENT (INCIDENT NO. 853067). AFTER THE INITIAL EMERGENCY RESPONSE, IT WAS DETERMINED DURING THE INVESTIGATION THAT THE CAUSE OF THE RELEASE AND SUBSEQUENT CONDENSATE SPILL WAS FROM AN UNIDENTIFIED TAP VALVE THAT WAS INADVERTENTLY BROKEN OFF BY A CONTRACTOR UTILIZING EXCAVATION EQUIPMENT DURING CONSTRUCTION ACTIVITIES, CREATING AN APPROXIMATE 2-INCH HOLE IN THE PIPELINE. CROSSTEX PERSONNEL WERE PREVIOUSLY UNAWARE OF THE PRESENCE OF SUCH TAP VALVE AS IT WAS NOT INDICATED ON FACILITY DRAWINGS. CROSSTEX PERSONNEL ON THE SCENE OF THE INCIDENT QUICKLY ISOLATED THE AFFECTED PIPELINE SEGMENT, AND CAREFULLY EXCAVATED AROUND THE DAMAGED TAP VALVE GAINING ACCESS TO THE DAMAGED PORTION OF THE PIPELINE. REPAIRS TO THE PIPELINE AND PURGING ACTIVITIES WERE FINALIZED BY 1645 HOURS AND GAS SERVICE TO THE TOWN OF LOGANSPORT WAS RESTORED BY 1750 HOURS THE DAY OF THE INCIDENT. THERE WAS ONE INJURY ASSOCIATED WITH INCIDENT WHICH OCCURRED WHEN THE CONTRACT BACKHOE OPERATOR EXITED THE EXCAVATOR AND TWISTED HIS KNEE. HE WAS TAKEN TO A LOCAL HOSPITAL FOR A DOCTOR'S EXAMINATION AND WAS RELEASED THE SAME DAY. HOWEVER IT IS ANTICIPATED THAT ADDITIONAL TREATMENT WILL BE REQUIRED DUE THE NATURE OF THE INJURY. 200 MCF (THOUSAND CUBIC FEET)OR APPROXIMATELY 9,341 POUNDS OF SWEET NATURAL GAS AND LESS THAN TWO (2) BARRELS OF CONDENSATE WERE RELEASED. A CLEANUP CREW TRAINED IN EMERGENCY RESPONSE WAS SUMMONED BY CROSSTEX TO REMOVE SOILS IMPACTED BY CONDENSATE. THE EXCAVATED MATERIALS WERE PROPERLY STORED IN THE COVERED ROLL-OFF BINS PENDING TRANSPORTATION TO AN OFF-SITE LOCATION FOR PROPER DISPOSAL. SUBSEQUENT TO THE CLEANUP ACTIVITIES, A NUMBER OF CONFIRMATORY SOIL SAMPLES ARE SCHEDULED FOR COLLECTION BY 11/09/07. UPON RECEIPT OF THE ANALYTICAL DATA DEOMONSTRATING NO PRESENCE OF CONDENSATE IN THE AFFECTED AREA, CLEAN FILL WILL BE PLACED OVER THE EXCAVATED AREA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070142 | 2007-12-18 14:59 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1430 | 2007-11-26 | 2007 |  |  | LA |  |  | 39+94 | 28* 19'12.9 | 91*36 | OFFSHORE |  | EUGENE ISLAND | 306 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821000 | 466615.4635 | 1023700.3692 | 20000 | 8406.8627 | 801000 | 1015293.5065 | 0 | 0 | NO | NO | NO | NO | 0 |  | 8 |  | 855521 | 2007-11-26 | 650 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 16 | 0.38 | API 5L | 52000 |  |  | UNKNOWN | 1977 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1977 | NO | [57 empty] | AT APPROXIMATELY 2:30 P.M. ON 11/26/2007, WHILE PATROLLING OFFSHORE, A SMALL BUBBLE CIRCLE WITH NO SHEEN WAS SIGHTED NEAR EUGENE ISLAND BLOCK 306, IN THE NEAR VICINITY OF ANR'S 16-INCH LINE 607, AND IN CLOSE PROXIMITY TO A PREVIOUS LEAK. UPON FURTHER MONITORING, IT WAS OBSERVED THAT THE PRESSURE IN THE LINE CONTINUED TO DROP. THE CAUSE OF THE LEAK WAS ATTRIBUTED TO INTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070143 | 2007-12-19 14:14 | ORIGINAL | 31613 |  | ENBRIDGE PIPELINES (EAST TEXAS) L.P. | 1100 LOUISIANA STE 3300 | HOUSTON | HARRIS | TX | 77002 | 1430 | 2007-12-10 | 2007 | LIVINGSTON | POLK | TX | 77351 | 64 |  | N 30 44.264 | W 95 00.618 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105657 | 52726.1013 | 59915.7596 | 87357 | 36719.9154 | 18300 | 23195.8442 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 30 | 856829 | 2007-12-10 | 860 | 1080 | YES | NO | NO | NO | NO | NO | GREGG JOHNSON | 7133536369 | GREGG.JOHNSON@ENBRIDGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 20 | 0.25 | X-60 |  | ERW |  |  |  | UNDER GROUND |  | 58 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | TAPE DISBONDED | YES | 1978 | NO | [57 empty] | MOWING CREW NOTICED A LEAK AND NOTIFIED OPERATIONS AT ABOUT 11:30 AM ON DECEMBER 12, 2007. OPERATIONS LOCATED THE POSSIBLE LEAK SITE AND CONFIRMED IT WAS OUR LINE, THE LINE WAS ISOLATED AND BLOWN DOWN BY 8:00 PM DECEMBER 10, 2007. ON DECEMBER 11, 2007 EXCAVATION REVEALED EXTERNAL CORROSSION PITS DUE TO DISBONDMENT OF TAPE. A SEGMENT OF PIPE WAS REPLACED AND THE LINE PLACED BACK INTO SERVICE BY 8:00 PM DECEMBER 11, 2007.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070144 | 2007-12-20 14:22 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 2030 | 2007-11-27 | 2007 | CEDARTOWN | POLK | GA | 30125 | 27.852 |  | 33.970742N | -85.243027W | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55566 | 27329.6869 | 27592.7334 | 50566 | 21255.0711 | 5000 | 6337.6623 | 0 | 0 | NO | NO | NO | YES | 30 | PRECAUTIONARY | 3 | 0 | 855637 | 2007-11-27 | 1090 | 1190 | NO | NO | NO | NO | YES | NO | KEN PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | BLOWOFF RISER | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 4.5 | 0.34 | API 5L | 35000 | SEAMLESS |  |  | 1965 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | BLOWOFF PIPE WAS ACCIDENTALLY STRUCK BY A 7 MM BULLET FROM A HUNTING RIFLE. |  | A LOCAL HUNTER WAS SHOOTING AT A COYOTE IN POLK COUNTY, GA, NEAR SOUTHERN NATURAL GAS COMPANY'S CEDARTOWN GATE SETTING ON ITS 14" CHATTANOOGA BRANCH PIPELINE. THE HUNTER ACCIDENTALLY HIT THE 4" BLOWOFF RISER PIPE UPSTREAM OF THE ISOLATION VALVE AT THE GATE SETTING. THE BULLET PUNCTURED THE PIPE RESULTING IN A HOLE ABOOUT ONE-HALF INCH IN DIAMETER (THIS REPORT SHOWS A 1" HOLE BUT THAT FIELD ON THE FORM WOULD NOT TAKE A DECIMAL NUMBER NOR A FRACTION). GAS ESCAPED UNTIL THE LINE SEGMENT WAS ISOLATED. AFTER ISOLATION, THE PIPE WAS BLOWN DOWN AND A WELDOLET WAS INSTALLED AT THE POINT OF THE BULLET HOLE WITH A THREADED PLUG INSERTED INTO THE HOLE. ABOUT TEN HOMES WERE EVACUATED SHORTLY AFTER THE INCIDENT BEGAN AS A PRECAUTIONARY MEASURE BY LOCAL OFFICIALS. THE NEARBY ROAD WAS CLOSED AS WAS A NEARBY RAILROAD OPERATED BY CSX.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20070145 | 2007-12-11 | ORIGINAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1045 | 2007-11-07 | 2007 | TYLER | SMITH | TX | 75703 | 700' WEST OF COPELAND RD. |  | 32.279816 | -95.290858 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 43303.9439 | 78528.4855 | 27000 | 11349.2647 | 53000 | 67179.2208 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 |  | 2007-11-07 | 675 | 1000 | YES | NO | NO | NO | NO | NO | MARCUS CHAPMAN DIRECTOR OF OPERATIONS | 2144267029 | MARCUS.CHAPMAN@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 20 | 0.5 | X52 | 47 | ERW |  |  |  | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | NO |  |  |  |  | YES | FLAGS | YES | ACCURATE | YES
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20070146 | 2007-12-27 11:32 | SUPPLEMENTAL | 2714 |  | DOMINION TRANSMISSION INC | PO BOX 2450,445 W MAIN ST | CLARKSBURG | HARRISON | WV | 26302 | 1806 | 2007-12-01 | 2007 | HARRISON VALLEY | POTTER | PA | 16927 | GATE 144 |  | 41.58.39.53 N | 77.41.11.37 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782000 | 388044.1176 | 421899.1597 | 672000 | 282470.5882 | 100000 | 126753.2468 | 10000 | 12675.3247 | NO | NO | NO | YES | 1 | THREAT TO THE PUBLIC | 3 | 30 | 856060 | 2007-12-01 | 911 | 1200 | YES | NO | NO | NO | NO | NO | SHAWN A. MILLER | 3046273404 | SHAWN.A.MILLER@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | OTHER | POT DRIP | 1994 | 24 | 0.47 | API 5L | 65000 |  |  |  |  | UNDER GROUND |  | 80 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | SEE BELOW | YES | 1994 | NO | [57 empty] | AT 6:06 PM ON DECEMBER 1, 2007, A POT DRIP LOCATED ON PIPELINE TL-453 RUPTURED, IN POTTER COUNTY, PA. THE PIPELINE WAS ISOLATED (BY DOMINION PERSONNEL) AND EVACUATED OF NATURAL GAS BY 9:30 PM. THE CAUSE OF THE INCIDENT WAS INITIALLY IDENTIFIED AS INTERNAL CORROSION. THE PIPE HAS BEEN SENT TO CC TECHNOLOGIES FOR ANALYSIS IN ORDER TO CONFIRM THE FAILURE MECHANISM. THE PIPELINE REMAINED OUT OF SERVICE WHILE ASSESSMENT WORK WAS PERFORMED. THE PIPELINE WAS PLACED BACK IN SERVICE ON DECEMBER 12, 2007. UPDATE - CC TECHNOLOGIES HAS DETERMINED THAT THE PRIMARY CASUE OF THE INTERNAL CORROSION WAS A HIGH CHLORIDE LEVEL, AND UNDER-SEPOSIT CORROSION. THE SECONDARY CAUSE WAS ACID-PRODUCING BACTERIA (APB)
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080001 | 2007-12-31 | ORIGINAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056-5306 | 1507 | 2007-11-21 | 2007 | HAVEN | RENO | KS | 67543 | MP 3.1 VS 0 | 159+77 | 37.910450 | -97.752683 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573700 | 298442.7919 | 444476.2971 | 333700 | 140268.5049 | 165000 | 209142.8571 | 75000 | 95064.9351 | NO | YES | NO | NO | 0 |  | 0 | 45 | 855247 | 2007-11-21 | 897 | 900 | NO | NO | NO | NO | YES | NO | BRIAN JIMENEZ ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 30 | 0.31 | API-5LX | 60000 | EFW |  | AO SMITH | 1962 | UNDER GROUND |  | 32 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1962 | NO | [57 empty] | CREVICE CORROSION OF THE LONGITUDINAL SEAM CAUSED THE PIPE TO RUPTURE. THE FAILURE ARRESTED IN THE TWO ADJACENT PIPE JOINTS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080002 | 2008-01-07 | SUPPLEMENTAL FINAL | 792 |  | ATLANTA GAS LIGHT CO | 10 PEACHTREE PL NE | ATLANTA | FULTON | GA | 30309 | 1624 | 2007-12-03 | 2007 | CANTON | CHEROKEE | GA | 30107 |  |  | 34.290881 | -84.434005 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92000 | 47557.8209 | 68323.1952 | 57000 | 23959.5588 | 35000 | 44363.6364 | 0 | 0 | NO | NO | NO | YES | 100 | PRECAUTIONARY | 3 | 56 | 856210 | 2007-12-03 | 480 | 960 | NO | YES | NO | NO | NO | NO | SCOTT CRIDER, STAFF ENGINEER | 4045844697 | SCRIDER@AGLRESOURCES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1987 | 16 | 0.31 | API 5L | 60000 |  |  | MAVERICK |  | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | YES | [36 empty] | AFTER THE INCIDENT SITE WAS EXCAVATED IT WAS DISCOVERED THAT THE PIPELINE HAD BEEN PREVIOUSLY DAMAGED BUT THE DAMAGE WAS NEVER REPORTED. THE TOP OF THE PIPE HAD BEEN SCRAPED / GOUGED OVER AN APPROXIMATELY 9-FOOT SECTION. A PORTION OF THIS DAMAGED AREA OPENED IN A 14-INCH LONG SPLIT.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20080003 | 2008-01-07 13:36 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 1255 | 2007-12-14 | 2007 | DELHI | MADISON | LA |  | 2 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 36 | 89 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3045450 | 1719974.7382 | 3690387.652 | 200450 | 84257.7819 | 2100000 | 2661818.1818 | 745000 | 944311.6883 | NO | NO | YES | NO | 0 |  |  |  | 857240 | 2007-12-14 | 930 | 935 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 30 | 0.38 |  | 52000 | DSAW |  | CONSOLIDATED WESTERN | 1954 | OTHER | CASING |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | ATMOSPHERIC | YES | 1954 | NO | [57 empty] | FAILURE WAS CAUSED BY A COATING FAILURE INSIDE A CASING, WHICH ALLOWED CORROSION TO OCCUR UNDER THE DISBONDED COATING. INNVESTIGATION REPORT SUBMITTED TO PHMSA
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080004 | 2008-01-08 14:50 | ORIGINAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 855 | 2007-12-18 | 2007 | WOODSBORO | REFUGIO | TX | 78393 | 78.09 | 4123+29 | 28 10 24.1 | -97 26 14.5 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165443 | 84413.8732 | 111988.7095 | 115341 | 48482.7978 | 50102 | 63505.9117 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 5 | 0857-524 | 2007-12-18 | 590 | 900 | NO | YES | NO | NO | NO | NO | KRISTIN VAN DER LAAN | 3039147753 | KRISTIN_VANDERLAAN@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 30 | 0.31 | 5LX60 | 60000 | DSAW |  | KAISER STEEL | 1965 | UNDER GROUND |  | 60 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1965 | NO | [57 empty] | WHILE SANDBLASTING THE PIPELINE IN PREPARATION FOR APPLICATION OF NEW COATING AN EMPLOYEE FELT GAS BLOWING ON HIS ARM. HE IMMEDIATELY SHUT OFF THE SANDBLASTER, NOTIFIED THE SUPERVISOR AND EXITED THE TRENCH. ALL WORK STOPPED AND EMPLOYEES WERE MOVED TO A SAFE AREA. THE VALVE SECTION WAS ISOLATED AND BLOWN DOWN.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080005 | 2008-01-09 13:59 | SUPPLEMENTAL FINAL | 18156 |  | SEADRIFT PIPELINE CORP | 7802 SH 185 NORTH | SEADRIFT | CALHOUN | TX | 77983 | 1400 | 2008-01-03 | 2008 | BAY CITY | MATAGORDA | TX | 77414 |  | 0+00 | 28.996389 | -96.148056 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211058 | 98860.8186 | 133173.6937 | 148500 | 55485.2941 | 57558 | 71479.0898 | 5000 | 6209.3097 | NO | NO | NO | NO | 0 |  |  | 25 | 858722 | 2008-01-03 | 1100 | 1794 | NO | YES | NO | NO | NO | NO | JENNIFER ASHCRAFT - REGULATORY COMPLIANCE SPECIALIST | 9792380361 | JOASHCRAFT@DOW.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2001 | 4 | 0.25 | X-65 | 65000 | SMLS |  | LONE STAR | 2000 | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [5 empty] | MATERIAL DEFECT |  | NO | YES | 1 | 27 | 2001 | WATER |  | 11 | 2700 | [12 empty] | THE LEAK WAS THE RESULT OF A CRACKED WELD ON A 14 INCH BY 4 INCH TEE COMING FROM THE 14 INCH LAVACA PIPELINE TO 4 INCH PIPING GOING TO MARKHAM STATION. UPDATED BY PHMSA ON 12/3/2015 PER OPERATOR'S MARK UP (PART A, QUESTION 3.F - LATITUDE/LONGITUDE; AND PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080006 | 2008-01-17 15:19 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 630 | 2007-12-21 | 2007 | FULTONDALE | JEFFERSON | AL | 35068 | 194.3 |  | N 33 DEG 35.0515 | W -86 DEG 50.7606 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 11 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572660 | 294483.9238 | 410151.567 | 372660 | 156645.0735 | 200000 | 253506.4935 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 857822 | 2007-12-21 | 604 | 650 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 24 | 0.25 |  | 52000 | DSAW |  | REPUBLIC | 1953 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1973 | NO | [57 empty] | SOUTHERN NATURAL GAS COMPANY GAS CONTROL PERSONNEL NOTICED AN ABNORMAL PRESSURE DROP VIA SCADA ON SNG'S NORTH MAIN PIPELINE SYSTEM BETWEEN PROVIDENCE COMPRESSOR STATION AND TARRANT COMPRESSOR STATION IMMEDIATELY BEFORE DAWN DECEMBER 21, 2007. FIELD PERSONNEL WERE CALLED OUT TO INVESTIGATE. THEY FOUND A RUPTURE AND GAS RELEASING AT ABOUT MILEPOST 194.3 ON SNG'S 24" 2ND NORTH MAIN PIPELINE. THE GEOGRAPHIC LOCATION WAS IN A HOLLOW ABOUT 5 MILES WEST OF THE CITY OF FULTONDALE, AL AND ABOUT ONE HALF MILE EAST OF COALBURG ROAD, VERY REMOTE. PERSONNEL ON THE SCENE REPORTED A 37' X 58' HOLE AROUND THE PIPELINE DITCH WITH ABOUT 20' OF PIPE MISSING. THIS PIPE WAS RECOVERED FOR LABORATORY ANALYSIS. THE AXIAL PIPE LENGTH AFFETED WAS ABOUT 19' IN LENGTH. SUBSEQUENT INVESTIGATION HAS REVEALED EXTERNAL CORROSION PITTING TO BE THE PROBABLE CAUSE OF THE FAILURE. THERE WAS NO PUBLIC OR CUSTOMER IMPACT RELATIVE TO SAFETY OR NATURAL GAS DELIVERY.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20080007 | 2008-01-24 | SUPPLEMENTAL FINAL | 857 |  | MARKWEST PINNACLE LP | 3417 73RD STREET SUITE 1 | LUBBOCK | LUBBOCK COUNTY | TX | 79423 | 630 | 2008-01-10 | 2008 | WOLFFORTH | LUBBOCK | TX | 79423 | 16.276 M.P./ FARM TAP |  | 27.054 | 00.529 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 17923 | 8676.6033 | 13208.397 | 10423 | 3894.4325 | 7500 | 9313.9646 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 |  | 2008-01-10 | 721 | 920 | NO | YES | NO | NO | NO | NO | BRUCE GILLICK, DIRECTOR SAFETY, RISK & SECURITY | 3039259228 | BGILLICK@MARKWEST.COM | TRANSMISSION | OTHER | NIPPLE & VALVE CONNECTION | STEEL |  | NO | NO | NO | OTHER | FARMTAP | 1984 | [8 empty] | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | CAR GOING NORTH ON FM 179 CAME OUT OF A CURVE & DRIVER GOING TOO FAST OR DOZED OFF AND HIT GUARD RAIL AROUND FARM TAP. ATMOSENERGY REGULATORS ATTACHED TO FARM TAP BY A 2" WELD X 1" THREAD REDUCER. GUARD RAIL HIT REGULATOR PIPING CAUSING THE 1" THREADED CONNECTION TO BREAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080008 | 2008-01-28 15:34 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1728 | 2007-12-28 | 2007 | MOUNTAINBURG | CRAWFORD | AR | 72959 | LINE OM-1 | 1948+13 | 35.70816 | -94.02222 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 1 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472450 | 242951.8995 | 338377.3547 | 307450 | 129234.4975 | 165000 | 209142.8571 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 858362 | 2007-12-28 | 850 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 20 | 0.25 | X-60 | 60000 | DSAW |  | KAISER | 1967 | UNDER GROUND |  | 36 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | METALLURGICAL REPORT SHOWED THE FAILURE INITIATED AT A BUCKLE THAT AFFECTED THE LONG SEAM OF THE PIPE. IT IS NOT KNOW FOR SURE WHAT CAUSED THE BUCKLE, BUT ONE POSSIBLE SCENARIO WHICH COULD EXPLAIN THE INCIDENT IS THE BUCKLE DEVELOPED IN RESPONSE TO GROUND MOVEMENT OR SUBSIDENCE. THIS SITUATION APPEARED TO HAVE EXISTED FOR A NUMBER OF YEARS SLOWLY WORSENING UNTIL IT FAILED. THERE WAS NO EVIDENCE THIS WAS A SHORT TERM EVENT SUCH AS AN EARTHQUAKE AND THE EVIDENCE AT THE SURFACE SEEMED TO SUPPORT THAT AS WELL. ONE IMPORTANT THING FROM THE REPORT IS THAT THIS DOES NOT APPEAR TO BE A SYSTEMIC EPISODE. THE PIPE ANALYSIS AND TESTING INDICATES WE HAVE A SOUND PIPE, THAT IS, THERE ARE NO INHERENT SEAM ISSUES AND THERE IS ADEQUATE TOUGHNESS TO ARREST AND CONTROL FRACTURES. COPY OF REPORT SENT TO OPS.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20080009 | 2008-01-24 | ORIGINAL | 30792 |  | LAMAR OIL & GAS | 4305 BUS HWY 35S | ROCKPORT | ARANSAS | TX | 78382 | 1500 | 2007-10-30 | 2007 | PORTLAND | NUECES | TX | 78374 |  |  | 27 50 44 | 97 26 57 | OFFSHORE |  | NUECES BAY | 746 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2900 | 1619.7638 | 3336.9684 | 400 | 168.1373 | 2500 | 3168.8312 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 |  |  | 25 | 2000 | YES | NO | NO | NO | NO | NO | NEIL SULLIVAN PRODUCTION FOREMAN | 3617273309 | NEIL.SULLIVAN@WOODGROUP.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 3 | 0.25 | [6 empty] | UNDER WATER |  |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | DEFECT IN COATING | YES | 1990 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080010 | 2008-01-31 | SUPPLEMENTAL FINAL | 31531 | 30630 | ONEOK WESTEX TRANSMISSION, INC. | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103 | 1100 | 2007-12-12 | 2007 | CANUTILLO | EL PASO | TX |  | BLOCK: 239 TRACT: 8 | 39+60 | N31* 54.86 | W106* 35.54 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250068 | 142646.553 | 316911.7002 | 68 | 28.5833 | 250000 | 316883.1169 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 857062 | 2007-12-12 | 224 | 250 | NO | YES | NO | NO | NO | NO | TIM SMITH, MANAGER PERMIAN DISTRICT | 4326831235 | TSSMITH@ONEOK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 4 | 0.19 | GRADE A | 24000 | ERW | NA | UNKNOWN |  | UNDER PAVEMENT |  | 60 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1972 | NO | [57 empty] | GAS LEAK WAS DISCOVERED DURING ANNUAL LEAK SURVEY CONDUCTED ON THE 12TH OF DECEMBER 2007. GAS WAS DETECTED AT BOTH CASING VENT PIPES. LEAK WAS MONITORED DAILY UNTIL THIS SECTION OF THE PIPE WAS TAKEN OUT OF SERVICE ON THE 19TH OF DECEMBER 2007. 1APR10 - NO CHANGES, JUST FINALIZED THE REPORT. PATTI FORD, ONEOK PARTNERS, SR PIPELINE SAFETY ENGINEER, (918) 588-7131
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080011 | 2008-02-04 18:09 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1750 | 2008-01-04 | 2008 | OKAY | HOWARD | AR | 71859 | LINE AM-46 | 1512+38 | 33.76955 | -93.95274 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141912 | 72202.2386 | 128222.3472 | 55300 | 20662.2004 | 86612 | 107560.1468 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 40 | 858822 | 2008-01-04 | 485 | 500 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 10 | 0.25 | GRADE B | 35000 | UNKNOWN |  | UNKNOWN | 1961 | UNDER WATER |  | 68 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | DAMAGE TO COATING | YES | 1961 | YES | 4 | 6 | [55 empty] | ON JANUARY 4, 2008 FIELD PERSONNEL WERE NOTIFIED OF A POTENTIAL LEAK ON CEGT LINE A-46 WEST OF OKAY AR, JUST OFFSHORE IN MILLWOOD LAKE. INDICATIONS OF TWO LEAKS WERE FOUND AND THE AREA WAS MONITORED WHILE OVER THE COURSE OF FIVE DAYS THE CORP OF ENGINEER LOWERED THE LAKE LEVEL AND A CONTRACTOR BUILT A COFFER DAM TO ALLOW FOR PIPE INSPECTION AND REPAIR. THE PIPE WAS LOCATED IN ABOUT 24 INCHES OF WATER AND 44 INCHES OF STILT. THE LINE PRESSURE WAS LOWERED IN INCREMENTS TO KEEP SEVERAL COMMERCIAL BUSINESSES ONLINE ALONG WITH THE COMMUNITY OF ASHDOWN, AR. THE PIPE INSPECTION SHOWED COATING DAMAGE TO THE TOP OF THE PIPE AND CORROSION PITTING AT THE 12 O¿CLOCK POSITION. IT WAS ESTIMATED THAT THE DAMAGE TO THE COATING MAY HAVE TAKEN PLACE IN SUMMER 2003 WHEN THE CORP OF ENGINEER HAD A BARAGE IN THE AREA DOING WORK. BOTH LEAKS WERE REPAIRED WITH BOLT-ON CLAMPS AND THE LINE RETURN TO NORMAL SERVICE ON JANUARY 8, 2008.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080012 | 2008-02-06 10:36 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 930 | 2008-01-10 | 2008 |  |  |  |  | LINE 524X-200 |  | 28 DEG 12 MIN 4 SEC. | 91 DEG 41 MIN 27.0 S | OFFSHORE |  | EUGENE ISLAND | 338C |  | YES | NO | INTERSTATE | OTHER | LEAK AT PREVIOUSLY INSTALLED LEAK CLAMP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447349 | 248516.876 | 545371.8549 | 11718 | 4378.2941 | 435631 | 540993.5608 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 859298 | 2008-01-10 | 850 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | REPAIR CLAMP | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 | 0.5 | API 5LX | 52000 | SEAMLESS |  | US STEEL | 1976 | UNDER WATER |  | 36 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | REPAIR CLAMP PREVIOUSLY INSTALLED IN APPROXIMATELY 1997 WAS FOUND LEAKING DUE TO MECHANICAL WEAR. |  | PRODUCER PERSONNEL OBSERVED BUBBLES DURING CREW CHANGE FLIGHT IN EUGENE ISLAND BLOCK 338C AND REPORTED TO US COAST GUARD. TENNESSEE GAS PIPELINE COMPANY WAS NOTIFIED AND INVESTIGATED, DETERMINING LEAK TO BE FROM ITS 524X-200 PIPELINE. DIVER DETERMINED PREVIOUSLY INSTALLED REPAIR CLAMP TO BE LEAKING. CLAMP WAS REMOVED, RE-MACHINED, AND REINSTALLED BY JANUARY 26, 2008. DELAY WAS DUE TO INCLEMENT WEATHER.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080013 | 2008-02-14 09:12 | SUPPLEMENTAL FINAL | 31451 |  | KINDER MORGAN TEXAS PIPELINE CO | 500 DALLAS ST | HOUSTON | HARRIS | TX | 77002 | 1209 | 2008-02-12 | 2008 | RICARDO | KLEBERG | TX | 78363 |  | 554+22 | 27.392083 | 97.903528 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 11 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 847302 | 453274.9961 | 915311.5112 | 157702 | 58923.5142 | 389600 | 483829.4136 | 300000 | 372558.5834 | NO | NO | YES | YES | 231 | PRECAUTIONARY | 2 | 25 | 862186 | 2008-02-12 | 952 | 1024 | NO | YES | NO | NO | NO | NO | SUZIE DAVIS | 7133699707 | SUZANNE_DAVIS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1964 | 16 | 0.22 | API 5LX52 | 52000 | ERW |  | LONE STAR STEEL | 1964 | UNDER GROUND |  | 40 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1964 | NO | [57 empty] | ON FEBRUARY 12, 2008 KINDER MORGAN RECEIVED TELEPHONE NOTIFICATION OF A FIRE APPROXIMATELY 7 MILES SOUTH OF KINGSVILLE AND 2 MILES SOUTHWEST OF RICARDO IN KLEBERG COUNTY, TEXAS NEAR THE KMTP 16" SARITA LATERAL. LOCAL KINDER MORGAN EMPLOYEES RESPONDED TO THE CALL CONFIRMING THAT THE FIRE WAS KINDER MORGAN'S SECURED THE SITE AND ISOLATED THE LINE SEGMENT FROM GAS FLOW. LOCAL FIRE AND LAW ENFORCEMENT EMERGENCY RESPONDERS SECURED APPROXIMATELY A ONE MILE RADIUS AND EVACUATED ALL RESIDENCES WITHIN THAT AREA AS WELL AS RESTRICTED ACCESS TO THE SITE FROM LOCAL ROADS. RESIDENTS WERE ALLOWED TO RETURN TO THEIR PROPERTY THE FOLLOWING DAY ON FEBRUARY 13, 2008
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080014 | 2008-02-18 14:24 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1525 | 2008-01-26 | 2008 |  |  |  |  | 509A-500 | 8+92 | 28.432059 | -92.637603 | OFFSHORE |  | EAST CAMERON | 272 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482700 | 258759.1659 | 525039.9981 | 85700 | 32020.8061 | 397000 | 493019.192 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 860708 | 2008-01-26 | 800 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 16 | 0.38 | API 5L | 52000 | UNKNOWN |  | US STEEL | 1973 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1973 | NO | [57 empty] | A LEAK WAS REPORTED BY A PRODUCER THE ESTIMATED COORDINATES OF WHICH PLOTTED TO BE NEAR TENNESSEE GAS PIPELINE COMPANY'S 16" 509A-500 PIPELINE. BAD WEATHER WITH HIGH SEAS PREVENTED IMMEDIATE INVESTIGATION ALTHOUGH PRODUCTION INTO THE SUSPECT PIPELINE WAS SHUT IN. A REPORT WAS MADE TO THE USCG FOR A NOTICE TO MARINERS; THUS, THE LEAK WAS REALLY NEVER CONSIDERED TO BE UNSAFE. AS SOON AS WEATHER ALLOWED MOBILIZATION AND REPAIR TO BE PERFORMED SAFELY, DIVERS WERE DISPATCHED AND INSTALLED A REPAIR CLAMP OVER THE PINHOLE SOURCE OF THE LEAK. THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080015 | 2008-02-19 11:06 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1800 | 2008-01-18 | 2008 | ARAPAHO | CUSTER | OK | 73620 |  | CUSTER COMPR. ST. | 35.705555 | -99..017125 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE MALFUNTION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86800 | 37348.5839 | 32431.8083 | 86800 | 32431.8083 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 860313 | 2008-01-22 | 100 | 275 | YES | NO | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1976 | [5 empty] | RELIEF VALVE 1.5 | GROVE | 1976 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | RELIEF VALVE SPRING BROKE | [10 empty] | UPON REPORTING TO THEIR WORK LOCATION ON MONDAY 1/21/08, FIELD PERSONNEL FOUND A RELIEF VALVE RELEASING NATURAL GAS ON STATION PIPING. IT WAS DETERMINED THAT A SPRING BROKE ON RELIEF VALVE AND THE RELIEF VALVE WAS REPLACED. MEASUREMENT SPECIALIST WERE CALLED IN AND IT WAS DETERMINED THAT THE RELEASE BEGAN ON FRIDAY 1/18/08 AT 1800 HRS. AND BLEW UNTIL MONDAY 1/21/08 AT 0800 HRS. WHEN FIGURING THE AMOUNT OF GAS LOST ON TUESDAY 1/22/08 IT WAS DETERMINED THAT OVER $50000 OF GAS WAS RELEASED AND A TELEPHONIC NRC REPORT WAS MADE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080016 | 2008-02-22 09:11 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1755 | 2008-01-23 | 2008 |  |  |  |  | 523M-2300 |  | 28.318298 | -91.411646 | OFFSHORE |  | EUGENE ISLAND | 302 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1186000 | 581710.1055 | 925073.8417 | 630914 | 235733.6623 | 555086 | 689340.1794 | 0 | 0 | NO | NO | NO | NO | 0 |  | 16 | 0 | 860457 | 2008-01-23 | 765 | 1250 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 30 | 0.75 | API 5L | 60000 | DSAW |  | ARMCO STEEL | 1973 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1973 | NO | [57 empty] | A DIVE BOAT IN THE VICINITY OF TENNESSEE GAS PIPELINE COMPANY'S 523M-2300 PIPELINE REPORTED BUBBLES IN THE WATER AT EUGENE ISLAND BLOCK 302. INVESTIGATION DETERMINED THE LEAK TO BE IN A WELD JOINT OF THE PIPELINE UNDERWATER. ROUGH SEAS AND INCLEMENT WEATHER CONTRIBUTED TO THE TIME REPORTED "UNTIL AREA WAS MADE SAFE" ALTHOUGH THE AREA WAS PROBABLY NOT UNSAFE FROM THE LEAK DUE TO THE WEATHER AND A NOTICE TO MARINERS FROM THE USCG. INCLEMENT WEATHER ALSO DELAYED THE COMPANY'S ABILITY TO REPAIR THE PIPELINE BUT THIS WAS ULTIMATELY ACCOMPLISHED ON FEBRUARY 2, 2008, WITH THE LINE BEING PLACED BACK INTO SERVICE. REPAIR WAS EFFECTED BY CLAMP INSTALLATION. TEN PRODUCERS WERE TAKEN OFF LINE BEGINNING ON JANUARY 24, 2008, AND REMAINED SO UNTIL THE PIPELINE WAS REPAIRED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080017 | 2008-02-22 12:17 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 748 | 2008-01-26 | 2008 | HEFLIN | CLEBURNE | AL | 36264 | 401.21 | NORTH MAIN LOOP | N 33.62735 | W -85.43336 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187500 | 98491.7351 | 190306.1582 | 49000 | 18308.2789 | 117500 | 145918.7785 | 21000 | 26079.1008 | NO | NO | NO | YES | 2 | PRECAUTIONARY | 2 | 15 | 860675 | 2008-01-26 | 449 | 500 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 24 | 0.25 |  | 52000 | SAW |  | REPUBLIC STEEL | 1948 | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | WRINKLE BEND | [11 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 12 | 20 | 1950 | NATURAL GAS |  | 30 | 700 | [12 empty] | NEARBY LANDOWNER REPORTED A NATURAL GAS RELEASE ON SOUTHERN NATURAL GAS COMPANY'S 24" NORTH MAIN LOOP PIPELINE JANUARY 26, 2008. POST INCIDENT INVESTIGATION REVEALED THAT THE FAILURE WAS DUE TO A WRINKLE BEND INSTALLED DURING THE ORIGINAL PIPELINE CONSTRUCTION USED IN A PIPELINE SAG BEND WITH THE PIPE'S LONGITUDINAL SEAM AT THE 12 O'CLOCK POSITION AND IN THE INSIDE PORTION OF THE WRINKLE BEND. THE PIPELINE WAS REPAIRED BY REPLACEMENT WITH A NEW PIPELINE SEGMENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080018 | 2008-02-26 | ORIGINAL FINAL | 31571 |  | CONSUMERS ENERGY | 2074 242 STREET | MARSHALLTOWN | MARSHALL | IA | 50158 | 15 | 2008-01-31 | 2008 | MINGO | JASPER | IA | 50158 |  |  | 41.75870 | -93.28566 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 3590.7648 | 6522.4746 | 2500 | 934.0959 | 4500 | 5588.3788 | 0 | 0 | NO | NO | NO | NO | 0 |  | 12 | 45 | 861109 | 2008-02-01 | 475 | 100 | YES | NO | NO | NO | NO | YES | JAMES KIDD ENERGY SERVICES MANAGER | 6417521593 | JKIDD@CONSUMERSENERGY.COOP | TRANSMISSION LINE OF DISTRIBUTION SYSTEM |  |  |  |  | NO | NO | NO | REGULATOR/METERING | [13 empty] | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | FEBRUARY 7, 2008 OFFICE OF PIPELINE SAFETYINFORMATION RESOURCE MANAGER1200 NEW HERSEY AVENUES.E. EAST BUILDING2ND FLOOR (PHP-10) ROOM E22-321WASHINGTON D.C. 20590RE: INCIDENT REPORT #861109, CONSUMERS ENERGY ATTACHMENT TO RSPA FORM F7100.0 AND F7100.2 INCIDENT REPORTSTHIS NARRATIVE PROVIDE AS PER INSTRUCTION FOR PART G OF THE ABOVE REFERENCE FORMS.OVER PRESSURES OF MINGO/HARVESTER GAS TRANSMISSION AND DISTRBUTION SYSTEMSON JANUARY 31, 2008 AT 1215AM AN OVER PRESSURE ALARM, FROM THE ELECTRONIC METERING, WAS RECEIVED BY NORTHERN NATURAL GAS AND CALLED TO CONSUMER ENERGY FROM OUR MINGO TBS, LOCATED AT 12359 NORTH 59TH AVENUE WEST MINGO, IOWA 50168. CONSUMERS ENERGY PERSONNEL RESPONDED AND FOUND THAT TWO EZR REGULATORS IN A WORKER MONITOR CONFIGURATION HAD FAILED IN THE OPEN POSITION AND THE PRESSURE TO BE 475PSI.AT 1:15AM. THIS TBS FEEDS 6 INCH PE PIPE 3408 SDR 11 PIPE WITH AN MAOP OF 100PSI.CONSUMER'S PERSONNEL SHUT DOWN THE REGULATOR STATION AND BEGAN TO VENT THE GAS. AFTER VENTING WAS STARTED A SECOND CREW WAS CALLED TO CHECK OUR REGULATOR STATION AT THE HARVESTER DEVELOPMENT, LOCATED NEAR THE CORNER OF W100TH STREET NORTH AND HIGHWAY 330. THE PRESSURE AT THIS STATION HAD PEGGED THE PRESSURE GAGE AT 16PSI. CREW 2 BEGAN VENTING GAS FROM THE DISTRIBUTION SYSTEM AT 2AM. THIS SYSTEM CONSISTS OF 4 INCH, 2 INCH, AND 1 INCH PE PIPE3408 SDR 11 WITH AN MAOP OF 60PSI. DURING VENTING HOUSE REGULATORS WERE CHECKED TO SEE IF ANY WERE VENTING AND AL REGULATORS APPEARED NORMAL.CREW 3 WAS DISPATCHED AT 6:30AM AND BEGAN VENTING GAS AT A FARM TAP CENTRALLY LOCATED ALONG THE TRANSMISSION LINE.CRE 4 ARRIVED AT 8AM AND BEGAN VENTING GAS AT THE DISTRIBUTION TBS AT HARVESTER. GAGES THAT HAD BEEN PEGGED WERE CHANGED.WITH THE PRESSURE IN THE TRANSMISSION SYSTEM AT 300PSI CONSUMERS CHECKED ALL FARM TAP METERS DOWN STREAM SIDES AND FOUND PRESSURES TO THE HOUSES TO BE NORMAL. SPOT CHECKS WERE TAKEN ON THE DOWN STREAM SIDE OF METERS ON OUR DISTRIBUTION SYSTEM AND ALL CHECKS WERE NORMAL FOR PRESSURE GOING INTO HOUSES.WHEN PRESSURE REACHED 75PSI AT THE TBS AT HARVESTER THE STATION WAS LOCKED IN AND LIKE PACK WAS USED TO FEED THE CONSUMERS.3PM PRESSURE WAS DOWN TO 100PSI AT THIS TIME A SHUT IN TEST WAS PERFORMED ON THE TRANSMISSION SYSTEM FOR ONE HOUR WITH NO LOSS OF PRESSURE DURING THAT HOUR. GAS WAS TURNED BACK ON AND SHUT IN TEST WERE PERFORMED ON THE HOUSES.4PM PRESSURE WAS RESTORED TO HARVESTER TBS AND REGULATORS CHECKED. GASKETS WERE DAMAGED ON ONE SIDE OF THE DUAL FEED WORKER MONITOR SYSTEMS FISHER 299H REGULATORS. THIS SIDE WAS LOCKED OUT AND THE SYSTEM WAS OPERATED OFF OF THE ALTERNATE SIDE.5PM MINGO TBS CREWS RESTORED HIGH PRESSURE FEED TO MINGO STATION LEAVING MALFUNCTIONING REGULATORS LOCKED OUT. CREWS CHECKED FUNCTION OF FISHER EZR REGULATORS ON OPPOSITE SIDE OF DUAL RUN AND IT WAS DECIDED THAT REGULATORS ON THE OPPOSITE SIDE WOULD ALSO BE LOCKED OUT AND THAT A FISHER 627 THAT FEEDS THE VORTEX HEATER WOULD FEED SYSTEM FOR THE NIGHT.FEBRUARY 1, 2008 AN INFRARED LEAK SURVEY WAS PERFORMED BY IOWA ASSOCIATION OF MUNICIPAL UTILITIES. THESE SURVEYS ARE PLANNED TO BE CONDUCTED MONTHLY FOR A MINIMUM OF THE NEXT 90 TO 120 DAYS.REGULATORS AT HARVESTER TBS WERE REPAIRED. EZR REGULATORS AT MINGO WERE ALSO TAKEN APART FOR REPAIR. THERE WAS A LARGE AMOUNT OF FOREIGN MATTER IN THE REGULATORS. DIAPHRAGMS APPEARED INTACT BUT WERE REPLACED.CONTACT WAS MAD WITH EAGLE PIPE, MANUFACTURES OF 3408 SDR 11 PIPE. MINIMUM BURST FOR THIS PIPE IS 504 PSI. EAGLE INFORMED CONSUMERS THAT THE PIPE REGAINS ITS STRENGTH WHEN EXCESSIVE PRESSURE IS RELIEVED FROM THE PIPE AND PIPE IS OPERATED AT NORMAL PRESSURES. EAGLE DECLINED TO PUT THIS IN WRITING.FEBRUARY 2, 2008 CONSUMERS PERFORMED A SHUT IN TEST ON OUR DISTRIBUTION SYSTEM FOR ONE HOUR. STARTING AND ENDING PRESSURES WAS 19.2PSI.AT THIS TIME CONSUMER PLANS TO ADD RELIEF TO OUR MINGO STATION AND CHANGE REGULATORS AND CONTINUE INFRARED LEAK SURVEYS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080019 | 2008-02-27 10:55 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 2217 | 2008-02-27 | 2008 | HARTSVILLE | MACON | TN | 37074 | HARTSVILLE COMPRESSOR STA |  | 36.461 | -86.180 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78500000 | 43873767.363 | 97486162.6551 | 0 | 0 | 78500000 | 97486162.6551 | 0 | 0 | NO | YES | NO | NO | 0 |  | 3 | 0 | 861616 | 2008-02-06 | 670 | 1008 | NO | NO | YES | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | COMPRESSOR STATION | OTHER | STEEL AND BUILDINGS | NO | NO | NO | COMPRESSOR |  | 1954 | [8 empty] | OTHER | COMPRESSOR STATION |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | HARTSVILLE COMPRESSOR STATION TOOK DIRECT HITS FROM ONE OR MORE F2 TORNADOS. DAMAGE TO THE STATION WAS EXTENSIVE. THERE WAS A FIRE CAUSED BY THE RELEASE OF GAS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080020 | 2008-02-28 15:59 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 415 | 2008-02-18 | 2008 | MOUNTAIN TOP | LUZERNE | PA | 18707 | 11.823 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK AND GAS IGNITION | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 167670.4485 | 372558.5834 | 0 | 0 | 300000 | 372558.5834 | 0 | 0 | NO | YES | NO | YES | 10 |  | 5 | 15 | 862651 | 2008-02-18 | 1080 | 1200 | NO | YES | NO | NO | NO | NO | MARIA CAMILA QUEZADA | 7132152749 | CAMILA.QUEZADA@WILLIAMS.COM | TRANSMISSION | OTHER | . | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2000 | 8 | [7 empty] | INSIDE/UNDER BUILDING |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | THE INCIDENT OCCURRED AT THE WRIGHT METER STATION A DUAL OWNERSHIP FACILITY. RECENT PIPING MODIFICATIONS WERE MADE BY THE CUSTOMER ON THE CUSTOMERS SIDE OF THE FACILITY. IT IS BELIEVED THAT THE INITIAL CAUSE OF THE LEAK AND IGNITION WAS A FLANGE GASKET ON THE CUSTOMERS PIPING.THE FIRE SPREAD TO THE WILLIAMS SIDE OF THE BUILDING COMPLETLY DESTROYING THE ENTIRE FACILITY. UGI WOULD BE CONSIDERED THE OUTSIDE FORCE
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080021 | 2008-02-29 12:33 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 2218 | 2008-01-30 | 2008 | ARMOREL | MISSISSIPPI | AR | 72710 | MP 1 | LINE J-78 83+06 | 35.930775506 | -89.777649635 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10325 | 4484.4752 | 4139.9886 | 10000 | 3736.3834 | 325 | 403.6051 | 0 | 0 | NO | NO | NO | YES | 0 | PRECAUTIONARY | 1 | 30 | 861098 | 2008-01-30 | 315 | 720 | YES | NO | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2007 | 4 | 0.24 | API5L | 42000 | ERW | RELIEF VALVE | ANDERSON GREENWOOD | 2000 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | THIS EVENT WAS CAUSED BY AN ICE- UP IN THE REGULATOR WHICH RESULTED IN A RELIEF VALVE RELEASE. NO INCIDENT REPORTING CRITERIA FOUND IN §191.3 - DEFINITIONS, PARAGRAPHS 1 AND 2 WAS MET. WE ARE REPORTING THIS INCIDENT UNDER PARAGRAPH 3 AS A SIGNIFICANT EVENT ¿IN THE JUDGMENT OF THE OPERATOR¿ SINCE THE LOCAL FIRE DEPARTMENT BLOCKED A PORTION OF A COUNTY HIGHWAY AND EVACUATED 23 PEOPLE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080022 | 2008-03-03 17:20 | SUPPLEMENTAL FINAL | 19580 |  | TRANS - COLORADO PIPELINE CO | 370 VAN GORDON STREET | LAKEWOOD | JEFFERSON | CO | 80228 | 915 | 2008-02-29 | 2008 | MEEKER | RIO BLANCO | CO |  | MP 296 / MLV #1 | 283 + 09 | N395355.0355 | -1081731.9340 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FLANGE GASKET FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91500 | 40206.9338 | 39831.3619 | 85000 | 31759.2593 | 6500 | 8072.1026 | 0 | 0 | NO | NO | NO | YES | 1 | THREAT TO THE PUBLIC | 4 | 15 | 863720 | 2008-02-29 | 1100 | 1287 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | HOT TAP MACHINEGASKET | 2008 | 24 | [7 empty] | OPEN DITCH |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FLANGE GASKET FAILURE |  | FLANGE GASKET ON A REDUCING SPOOL (24" X 20") CONNECTED TO A HOT-TAP MACHINE FAILED WHILE IN SERVICE AND UNDER PRESSURE. IMPROPER TORQUE APPLIED AT FACTORY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080023 | 2008-03-04 | SUPPLEMENTAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1453 | 2008-01-08 | 2008 | KEENE | JOHNSON | TX | 76059 |  | 173+76 | 32.422368 | 97.385932 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243983 | 109118.1555 | 119083.4751 | 211823 | 79145.195 | 32160 | 39938.2801 | 0 | 0 | NO | NO | NO | NO | 0 |  | 9 | 8 |  | 2008-01-08 | 577 | 800 | NO | YES | NO | NO | NO | NO | MICHAEL E. ARCHER - COMPLIANCE ANALYST | 2142062879 | MICHAEL.ARCHER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 10.75 | 0.22 | X42 | 42000 |  |  |  |  | UNDER GROUND |  | 52 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | YES | 1 | 4 | 2008 | ONE-CALL SYSTEM | NO | [40 empty] | AN EXCAVATOR STRUCK A TRANSMISSION LIKE, CAUSING A LEAK. UPDATED BY PHMSA ON 12/17/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080024 | 2008-03-05 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056-5306 | 1115 | 2008-02-01 | 2008 | CHIPLEY | WASHINGTON | FL | 32428 | MP 7.46 / 13-01CC | 394+18 | 30.73429 | -85.6088 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124100 | 69346.8137 | 154028.245 | 100 | 37.3638 | 116000 | 144055.9856 | 8000 | 9934.8956 | NO | NO | NO | NO | 0 |  | 2 | 30 | 861415 | 2008-02-01 | 815 | 975 | NO | NO | NO | NO | YES | NO | BRIAN JIMENEZ ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 3.5 | 0.13 | GRADE B | 35000 | ERW |  | NATIONAL TUBE | 1959 | UNDER GROUND |  | 40 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | LF ERW |  | MATERIAL DEFECT |  | NO | YES | 7 | 1 | 1963 | WATER |  | 8 | 1160 | [12 empty] | A 1/2 INCH LONG SEAM LEAK WAS FOUND AT THE 3:00 POSITION AT STATION 394+18 ON THE CHIPLEY LATERAL. THE PIPE IS 3.5 INCH ERW .125 WALL GRADE B NATIONAL TUBE PIPE, INSTALLED IN 1959. A 3RD PARTY REPORTED SMALL BUBBLES IN A WATER FILLED DITCH DIRECTLY OVER THE PIPELINE. AFTER EXCAVATION AND VISUAL INSPECTION, A 1/2 INCH MANUFACTURING DEFECT WAS REVEALED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080025 | 2008-03-07 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 45 | 2008-02-06 | 2008 |  | SHELBY | TN |  | MLS 25C MP 248.2398 |  | 35.05 | -089.88333 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | SEE PART G. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102500 | 44168.3396 | 38732.0421 | 102000 | 38111.1111 | 500 | 620.931 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 41 | 861623 | 2008-02-06 | 722 | 810 | YES | NO | NO | NO | NO | NO | JEFFREY B. MCMAINE - MANAGER, CODES AND STANDARDS | 2706886361 | JEFF.MCMAINE@BWPMLP.COM | TRANSMISSION | OTHER | 1 | STEEL |  | NO | NO | NO | OTHER | MAIN LINE VALVE CONTROL LINE |  | 1 | [7 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | SETTLING OF GROUND FROM FLOODING | [51 empty] | A BURIED 1" VALVE WAS BROKEN OFF AT THE NIPPLE FROM GROUND SETTLING
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080026 | 2008-03-07 12:42 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 |  | 2008-02-17 | 2008 | [6 empty] | 28.15.45 | 96.19.48 | OFFSHORE |  | MI | 564 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335000 | 185302.7268 | 403000.3975 | 15000 | 5604.5752 | 320000 | 397395.8223 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 86211 | 2008-02-17 | 960 | 1440 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7133812494 | JMCDONALD@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 12 | 0.38 | 5LX 42 | 42 |  |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1983 | NO | [57 empty] | LEAK WAS INITIALLY CALLED IN TO NRC BY ANOTHER OPERATOR AND PRODUCERS IN AREA SHUT HAD ALREADY SHUT IN THEIR PRODUCTION. ON FEBRUARY 17, CONFIRMATION WAS RECEIVED BY ENTERPRISE THAT THIS WAS OUR PIPELINE. A VESSEL WAS ONSITE AND DIVERS WERE ABLE TO SECURE A PIPELINE CLAMP TO REPAIR LEAK. THIS IS ENTERPRISE PRODUCTS OPERATING LLC PIPELINE X1-300. NO SHEEN WAS EVER DETECTED ON WATER. LINE WAS REPRESSURIZED ON FEBRUARY 18TH AND NO ADDITIONAL LEAKS WERE NOTED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080027 | 2008-03-17 14:51 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 818 | 2008-02-21 | 2008 | NEW HEBRON | SIMPSON | MS | 39140 | 76.994 | GWINVILLE PICKENS LINE | N 31 46.332 | W 89 52.794 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52003 | 28545.0653 | 61073.7916 | 4039 | 1509.1253 | 47964 | 59564.6663 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 862953 | 2008-02-21 | 874 | 1000 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | PIPE COMPRISING AN OBSOLETE TAP | STEEL |  | NO | NO | NO | PIPELINE |  | 1947 | 16 | 0.28 |  | 42000 | LOW RESISTANCE WELD |  | REPUBLIC STEEL | 1947 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1971 | NO | [57 empty] | LANDOWNER CONTACTED SNG PERSONNEL TO REPORT A HISSING SOUND IN THE VICINITY OF PIPELINE FACILITIES IN A VALVE BOX AT AN INACTIVE, OBSOLETE 4" SIDE TAP ON SNG'S GWINVILLE-PICKENS MAIN LINE AT MP 76.994. EXTERNAL CORROSION WAS FOUND THE 4" TAP LINE THAT WAS PRESSURIZED BUT NO LONGER IN SERVICE. HOWEVER, LEAK AFFECTED THE 16" GWINVILLE-PICKENS MAIN LINE, REQUIRING A SECTION OF THAT PIPELINE TO BE ISOLATED AND DEPRESSURIZED TO FACILITATE REPAIRS. THE REPAIR CONSISTED OF REMOVING THE 4" TAP AND APPROXIMATLEY 7 LINEAR FEET OF THE 16" MAIN LINE. THE CORROSION CONTRIBUTING TO THE LEAK WAS LIMITED TO THE TAP AND THERE WAS NO EVIDENCE OF CORROSION ON THE 16" GWINVILLE-PICKENS PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080028 | 2008-03-17 15:11 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1945 | 2008-03-03 | 2008 | FRANKLIN | HEARD | GA |  | 1000.265 |  | W85 01.527' | N33 19.536' | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185790 | 79942.3203 | 69418.268 | 185790 | 69418.268 | 0 | 0 | 0 | 0 | NO | NO | NO | YES | 250 | PRECAUTIONARY | 1 | 46 | 863963 | 2008-03-03 | 730 | 800 | NO | NO | NO | NO | YES | NO | JOHNNY LOPEZ | 7132152995 | JOHNNY.LOPEZ@WILLIAMS.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 30 | 0.33 | API 5L | 52000 | DSA |  | CONSOLIDATED WESTERN | 1949 | UNDER GROUND |  | 72 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE CAUSE OF THE LEAK AT THE GIRTH WELD WAS INCREASED BENDING LOADS CAUSED BY SOIL SETTLEMENT INCONJUNCTION WITH EXCESSIVE STRESSES AT GIRTH WELD DUE TO WELD IMPERFECTIONS. |  | THE LEAK FAILURE WAS CAUSED BY A COMBINATION OF FACTORS. THE ANALYSIS PROVIDED TO WILLIAMS BY A HIRED ENGINEERING FIRM CONCLUDE THAT WELD IMPERFECTIONS AT THE GIRTH WELD AND SOIL CONDITIONS DUE TO A PREVIOUS EXCAVATION CAUSED THE RUPTURE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080030 | 2008-03-17 | SUPPLEMENTAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1424 | 2008-01-10 | 2008 | MANCHESTER | WASHTENAW | MI | 48158 | VS 0 | 1+75 | 42 DEG 12' 24 N | 83 DEG 58' 15 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | SHEAR | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221700 | 114043.4401 | 208728.043 | 76700 | 28658.061 | 145000 | 180069.982 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 51 | 859340 | 2008-01-10 | 380 | 936 | NO | NO | NO | NO | YES | NO | BRIAN JIMENEZ, ENGINEER | 7139897414 | BRIAN.JIMENEZ@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 2.38 | 0.22 | UNKNOWN |  | SEAMLESS | N/A | UNKNOWN |  | UNDER GROUND |  | 56 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | OPERATING COMPANY WAS EXCAVATING IN AREA OF A DRIP, WHEN MECHANICAL DAMAGE OCCURRED ON A 2 IN. EQUALIZING LINE CONNECTED PERPENDICULAR TO 20 IN. CARRIER LINE. THE 2 IN. LINE WAS SHEARED NEAR A WELDOLET WELDED TO THE SIDE OF THE CARRIER LINE. THE REPAIR CONSISTED OF REPLACING OVER 20 FT. OF 20 FT. PIPE (0.500 IN. WALL THICKNESS, X-60, ERW) FOR THE NEW DRIP, ABOUT 30 FT. OF 20 IN. PIPE (0.375 IN. WALL THICKNESS, X-65, ERW) REPLACING THE EXISTING 20 IN. PIPE, AND 98 FT. AND 2 IN. PIPE (0.218 WALL THICKNESS, X-42, SEAMLESS) FOR REPLACING THE ENTIRE EXISTING 2 IN. EQUALIZING LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080031 | 2008-03-18 13:20 | SUPPLEMENTAL FINAL | 15259 |  | UGI PENN NATURAL GAS | 1 UGI CENTER | WILKES-BARRE | LUZERNE | PA | 18711 | 414 | 2008-02-18 | 2008 | MOUNTAIN TOP | LUZERNE | PA | 18707 |  |  | 41.1134 | -75.87406 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510000 | 283753.5798 | 624667.3558 | 10000 | 3736.3834 | 200000 | 248372.3889 | 300000 | 372558.5834 | NO | YES | NO | NO | 10 | PRECAUTIONARY | 1 | 3 | 862646 | 2008-02-18 | 1100 | 1200 | NO | YES | NO | NO | NO | NO | ANTHONY M. DECESARIS | 5708298870 | ADECESARIS@UGIPNG.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2001 | [8 empty] | INSIDE/UNDER BUILDING |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | GASKET | [7 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | THE EVENT OCCURRED AT A CITY GATE STATION THAT INCLUDES FACILITIES OWNED AND OPERATED BY TRANSCO AND FACILITIES OWNED AND OPERATED BY UGI PENN NATURAL GAS. THE SOURCE OF GAS WAS A FAILURE OF THE GASKET INSTALLED AT THE FLANGE FACES. THE IGNITION SOURCE REMAINS UNDETERMINED. THE PUBLIC/PRIVATE PROPERTY DAMAGE, AMOUNT OF $300,000 NOTED IN SECTION 5C, WAS TRANSCO'S ESTIMATED DAMAGE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080032 | 2008-03-20 17:08 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1041 | 2008-02-21 | 2008 | REED CITY | OSCEOLA | MI | 49677 |  |  | 43.9255295 | -85.5444336 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539300 | 298200.1195 | 648030.5567 | 25000 | 9340.9586 | 514300 | 638689.5981 | 0 | 0 | NO | NO | YES | NO | 0 |  | 9 | 15 | 863021 | 2008-02-21 | 400 | 800 | NO | YES | NO | NO | NO | NO | ROBERT CADORIN | 2482057669 | ROBERT_CADORIN@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1965 | 8 | 0.24 | API 5L | 52000 | SEAMLESS |  | UNKNOWN |  | UNDER GROUND |  | 96 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | ELECTROCHEMICAL | YES | 1965 | NO | [57 empty] | THIS EVENT OCCURRED AT ANR PIPELINE COMPANY¿S REED CITY COMPRESSOR STATION, WHICH IS ASSOCIATED WITH THE REED CITY AND LOREED GAS STORAGE FIELDS. INVESTIGATIONS INDICATED THAT A LEAK IN AN UNDERBEND SEGMENT OF STATION PIPE KNOWN AS THE 8¿ LOW PRESSURE RECYCLE LINE RESULTED IN NATURAL GAS SATURATING THE IMMEDIATE AREA OF THE LEAK AND THEN MIGRATING INTO THE MOTOR CONTROL CENTER (MCC) ROOM AT THE STATION VIA AN UNDERGROUND ELECTRICAL CONDUIT. ONCE INSIDE THE ENCLOSED MCC PANELS, IGNITION OCCURRED RESULTING IN SOME OF THE PANEL DOORS BECOMING DETACHED FROM THE PANELS, AS WELL AS A SMALL FIRE OCCURRING WHERE THE CONDUIT ENTERED THE BUILDING. THE FIRE, WHICH RESULTED IN SOME DAMAGE TO THE STATION ELECTRICAL SYSTEM, WAS IMMEDIATELY CONTAINED AND EXTINGUISHED BY STATION PERSONNEL. AIR MOVERS WERE ATTACHED TO THE CONDUIT AT LOCATIONS REMOVED FROM THE BUILDING TO PREVENT ADDITIONAL GAS FROM ENTERING THE BUILDING. ONCE GROUND GAS LEVELS WERE LOWERED TO A SAFE LEVEL, THE PIPELINE WAS EXCAVATED TO LOCATE THE SOURCE OF THE LEAK. UPON DETERMINING THE LEAK LOCATION, A 50-FOOT SEGMENT WAS REMOVED AND REPLACED. THE REPLACEMENT SEGMENT AND THE REMAINING SEGMENTS OF THE EXISTING 8¿ LOW PRESSURE RECYCLE LINE WERE PRESSURE TESTED FOR 8 HOURS. FURTHER INVESTIGATION INDICATED TWO THROUGH-WALL PITS AT THE 6:00 O¿CLOCK POSITION IN THE UNDERBEND REGION. IT WAS DETERMINED THAT THE PITS WERE THE RESULT OF INTERNAL CORROSION CAUSED BY ELECTROCHEMICAL ACTIVITY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080034 | 2008-03-27 10:22 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 715 | 2008-03-14 | 2008 | GOESSEL | MARION | KS | 67053 | 8 | 100/433+25 | 38.1944 | -97.3179 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FITTING BROKEN BY CAR ACCIDENT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217889 | 94319.9019 | 85231.869 | 213489 | 79767.6765 | 3900 | 4843.2616 | 500 | 620.931 | NO | NO | NO | YES | 2 | THREAT TO THE PUBLIC | 4 | 0 | 865025 | 2008-03-14 | 777 | 900 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR, MANAGER PIPELINE COMPLIANCE AND INTEGRITY | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 2 | 0.22 |  | 24000 |  |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | PAUL GRABER (NON-EMPLOYEE) AT 853 CHISHOLM TRAIL NEAR NEWTON, KS REPORTED THAT A CAR HAS HIT A DEER THEN HIT SSCGP¿S LINE AND GAS IS LEAKING AT 7:15 A.M. SSCGP PERSONNEL ARRIVED ON SCENE AT 7:32 A.M AND GAS CONTROL WAS INFORMED ABOUT THIS LEAK AT 7:51 A.M. IT WAS DETERMINED THAT TO ISOLATE THIS 1¿ IT WAS GOING TO BE NECESSARY TO ISOLATE THE QE LINE BETWEEN HESSTON STATION AND MARION MAIN LINE GATE. GATE 34 WAS CLOSED AT 8:03 A.M. AND MARION GATE WAS CLOSED AT 9:40 A.M. SSCGP PERSONNEL CONTACTED HARVEY COUNTY 911, CITY OF HESSTON AND MARION COUNTY SHERIFF¿S DEPARTMENT TO INFORMED THEM ABOUT THE BLOW-DOWN. IN THE MEANTIME DOMESTIC CUSTOMERS, KANSAS GAS SERVICE, NATIONAL RESPONSE CENTER AND KANSAS DEPARTMENT OF HEALTH AND ENVIRONMENT WERE INFORMED OF THIS SITUATION. ONE CALL WAS CONTACTED AND STARTED EXCAVATION TO REPAIR THE TAP VALVE. AFTER PERFORMING THE NECESSARY REPAIRS, THE LINE WAS BACK INTO SERVICE AT 5:00 PM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080035 | 2008-03-28 15:12 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1130 | 2008-02-28 | 2008 | NAYLOR | FAULKNER | AR | 72047 | JM-30, MP 13 | 750+43 | 35.13768 | -92.18990 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67532 | 36938.9712 | 78432.9458 | 6257 | 2337.8551 | 61275 | 76095.0907 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 863629 | 2008-02-08 | 950 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 10 | 0.19 | X-46 | 46000 | ERW |  | UNKNOWN | 1969 | UNDER GROUND |  | 36 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | RUPTURE DUE TO THE COMBINATION OF TWO THINGS. ONE, LAYER OF CONTAMINATION AT THE CENTER OF THE WALL THICKNESS, CAUSED BY THE SELL MANUFACTURING PROCESS. SECOND, HIGH STRESSES (DUCTILE OVERLOAD) RESULTED FROM HYDROGEN BLISTERS FORMING IN THE CONTAMINATION LAYER. THE SOURCE OF THE HYDROGEN IS SUSPECTED TO BE FROM THE CATHODIC PROTECTION SYSTEM. |  | 2/27/08-5:30PM, FOUND LEAK IN PASTURE IN CLASS 1 LOCATION AT STATION 750+43, OF UNKNOWN CAUSE ON JM-30 BY LOCATING ODORIZED GAS SMELL. THERE WAS NO SOUND OF GAS ESCAPING OR HOLE IN THE GROUND OR VISIBLE INDICATIONS OF A SEVERE LEAK. MONITORED LEAK THROUGH OUT THE NIGHT BY MANNING SITE WITH EMPLOYEES TO PROVIDE PUBLIC SAFETY. 2/28/08 ¿ 7:30AM, DISPATCHED PERSONNEL TO BLOCKGATES AT EACH END OF SECTION AND BEGIN LOWERING PRESSURE FROM 950 #¿S TO EQUALIZE WITH SOUTHERN SECTION OF JM-30 AT 500 #¿S BEFORE DIGGING. ISOLATED SECTION AND BEGAN FEEDING SOUTHERN END OF JM-30 WITH ALTERNATE PIPELINE BT-14. ONCE PRESSURE WAS AT 500 #¿S WE BEGAN DIGGING UP LOCATION OF LEAK TO DETERMINE CAUSE AND EXTENT OF LEAK. WHEN PIPE WAS EXPOSED WE FOUND A LONGITUDAL CRACK OF APPROX. 1 INCH. AT THAT TIME WE LOWERED SAID SECTION DOWN TO 320#¿S BY BLOWING GAS TO THE ATMOSPHERE. FROM THAT TIME FORWARD WE BEGAN PROCESS OF REPLACING SECTION OF PIPE WITH CRACK. WE CONTINUED TO MONITOR THE LEAK SITE ON A 24HR SHIFT, WE MANNED THE BLOCK VALVES AT EACH END ON 24 HR SHIFT AND MANUALLY FED THAT SECTION TO KEEP AT 320 #¿S AND MAINTAIN CUSTOMERS. 2/29/08 7:30AM, WE PROCCURED FITTINGS AND BEGAN INSTALLING STOPPLE FITTINGS ON EACH SIDE OF SECTION OF PIPE LEAKING. CONTINUED MONITORING EFFORTS ON 24 HR SHIFT AT BLOCKGATES AND LEAK SITE. 3/01/08-7:30AM, BEGAN UTILIZING STOPPLE EQUIPMENT TO ISOLATE LEAKING SECTION OF PIPE FOR REPLACEMENT SAME DAY. LATE EVENING HOURS APPROX 20:00 HRS WE WILL PUT PIPELINE BACK IN SERVICE, WILL UPDATE THIS REPORT WITH ACTUAL TIME OF INSERVICE ON SUPPLEMENTAL REPORT. WE ARE SENDING 6 FT OF LEAKING SECTION WITH CRACK TO: KEIFNER AND ASSOCIATES, INC. MATERIALS TEST FACILITY, 6384 PROPRIETORS RD., WORTHINGTON, OHIO, 43085. PHONE # 614-888-8275, THEY WILL HELP US IDENTIFY THE TRUE CAUSE OF THIS LEAK. THE METALLURGICAL REPORT FROM KIEFNER & ASSOCIATES CONCLUDED THAT THE CAUSE FOR THIS LEAK WAS DUE TO A COMBINATION OF TWO THINGS. ONE, THE PIPE EXHIBITED A PROMINENT LAYER OF CONTAMINATION AT THE CENTER OF THE WALL THICKNESS, CAUSED BY THE SELL MANUFACTURING PROCESS. SECOND, HIGH STRESSES (DUCTILE OVERLOAD) OCCURRED IN THE SEPARATED LIGAMENTS OF THE PIPE WHERE HYDROGEN BLISTERS FORMED. THE SOURCE OF THE HYDROGEN IS SUSPECTED TO BE FROM THE CATHODIC PROTECTION SYSTEM. A COPY OF THE REPORT WAS SENT TO OPS.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080036 | 2006-11-21 | ORIGINAL | 32205 |  | DAVIS PETROLEUM PIPELINE, LLC. | 1360 POST OAK BOULEVARD, SUITE 2400 | HOUSTON | HARRIS | TX | 77056 | 1651 | 2006-10-24 | 2006 | LAPORTE | HARRIS | TX | 77571 | .76 | 40+00 | 29.36.56 | 95.00.19 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230120 | 134833.2624 | 299520.8455 | 120 | 47.8049 | 230000 | 299473.0406 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 27 | 815919 | 2006-10-24 | 190 | 1067 | YES | NO | NO | NO | NO | NO | KATERINA HUBACKOVA, ASSOCIATE | 7136267766 | KHUBACKOVA@DAVCOS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 12 | 375 | UNKNOWN | 1411 | UNKNOWN | ANSI 600 GATE VALVE | UNKNOWN |  | UNDER GROUND |  | 108 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | SULFATE REDUCING BACTERIA | MICROBIOLOGICAL |  | YES | 1952 | NO | [57 empty] | WE WERE PRESSURING UP THE PIPELINE, BRINGING ON AN ADDITIONAL WELL WHEN WE EXPERIENCED A PIN-HOLE LEAK ON OUR 12" O.D. PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080037 | 2008-04-04 16:48 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 405 | 2008-03-08 | 2008 | STERLINGTON | OUACHITA | LA | 71280 | MP 0.00 E15 1 |  | 32.680691 | -92.021677 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297500 | 128073.5684 | 111591.5192 | 297000 | 110970.5882 | 500 | 620.931 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 35 | 864398 | 2008-03-08 | 500 | 624 | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 7134798099 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | OTHER | VALVE OPERATED |  |  | NO | NO | NO | COMPRESSOR |  |  | 4 |  |  |  |  | NORDSTROM PLUG |  |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ESD VALVE OPENED PREMATURELY
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080038 | 2008-04-10 09:02 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 840 | 2008-03-20 | 2008 | GALVESTON |  | TX |  | 35.23 |  | 29.17.46 | 94.15.35 | OFFSHORE |  | NHI | 139 | TX | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574335 | 317866.7646 | 692116.5587 | 24335 | 9092.4891 | 550000 | 683024.0696 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 865540 | 2008-03-20 | 875 | 1440 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 24 | 0.44 | API-5LX | 60 | SEAMLESS |  | BETHLEHEM STEEL | 1977 | UNDER WATER |  | 48 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1977 | NO | [57 empty] | LEAK WAS LOCATED ON THE NHI24" PIPELINE SYSTEM THAT RUNS FROM HI 154 TO STATION 44, LEAK WAS IN THE GIRTH WELD IN THE 5 O'CLOCK POSITION. REPAIR CLAMP WAS INSTALLED ON LEAK AND LINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080039 | 2008-04-11 09:45 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 1400 | 2008-03-14 | 2008 |  | SUMTER | AL |  | 104.854 | SOUTH MAIN PIPELINE | N32.35076 | W -088.25626 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138000 | 70311.638 | 125361.0975 | 53000 | 19802.8322 | 85000 | 105558.2653 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 865074 | 2008-03-14 | 856 | 1200 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 18 | 0.31 | API 5L | 52000 | FLASH WELD |  | A.O. SMITH | 1951 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | NO | [19 empty] | A THIRD PARTY NOTICED HOLE IN GROUND AND HISSING SOUND IN THE VICINITY OF SOUTHERN NATURAL GAS (SNG) COMPANY'S 18" SOUTH MAIN PIPELINE. HE REPORTED THIS TO SNG AND COMPANY PERSONNEL WERE DISPATCHED TO THE SITE. UPON ISOLATION AND BLOWDOWN OF THE VALVE SECTION, THE LINE WAS EXCAVATED AND A CRACK IN THE CIRCUMFERENTIAL WELD OR WELD AREA WAS FOUND TO BE THE SOURCE OF THE LEAKING GAS. METALLURGICAL ANALYSIS REVEALED POORLY COMPLETED WELDING DURING THE ORIGINAL CONSTRUCTION THAT FAILED DUE TO TENSILE STRESSES ALONG THE PIPE IN A LONGITUDINAL DIRECTION. FURTHER INVESTIGATION SHOWED THAT THE BACKFILL SURROUNDING THE PIPELINE HAD BEEN DISTURBED FOR CONSTRUCTION ON A PARALLEL PIPELINE. THE FAILED PIPELINE MAY NOT HAVE BEEN ADEQUATELY SUPPORTED BEFORE ITS COVER WAS RESTORED, RESULTING IN THE EXTRA TENSILE STRESSES. ABOUT 80 FEET OF PIPE WAS REMOVED AND REPLACED WITH NEW PIPE. THE PIPELINE SEGMENT IS BACK IN SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080041 | 2007-01-11 | SUPPLEMENTAL FINAL | 15931 |  | PUBLIC SERVICE CO OF COLORADO | 1225 SEVENTEENTH ST | DENVER | DENVER | CO | 80202 | 1013 | 2007-01-11 | 2007 | HIGHLAND RANCH | DOUGLAS | CO | 80126 | VALVE 52827 |  | 39.55 | 104.97 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708000 | 403190.7308 | 890635.4724 | 8000 | 3362.7451 | 700000 | 887272.7273 | 0 | 0 | YES | NO | NO | YES | 176 | PRECAUTIONARY |  | 43 | 823536 | 2007-01-12 | 466 | 650 | NO | YES | NO | NO | NO | NO | MARK A. NOLAN | 3035713931 | MARK.NOLAN@XCELENERGY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 24 | 0.25 | API 5L X42 ERW | 52000 | WELD | COOPER-CAMERON 4 | STUPP CORP BATON ROUGE LA | 1970 | UNDER GROUND |  | 144 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | SUBSIDENCE RESULTED IN ABNORMAL DOWNWARD STRESS ON A 4" LATERAL OFF OF A 24" HIGH PRESSURE PIPELINE. THIS RESULTED IN A 3.25 CRACK JUST ABOVE THE WELD SADDLE JOINT FOR THE 4" VALVE 62827 ON THE 24" PIPE AND UNINTENTIONAL RELEASE OF GAS. UPDATED BY PHMSA ON 12/22/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080042 | 2008-04-17 14:18 | SUPPLEMENTAL FINAL | 21252 |  | VIKING GAS TRANSMISSION CO | 3140 NEIL ARMSTRONG BLVD., SUITE 208 | EAGAN | DAKOTA | MN | 55121 | 830 | 2008-04-10 | 2008 | GRAND FORKS | GRAND FORKS | ND | 55208 | MP 14.97 | 790+50 | 47.94763 | -97.06154 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK IN 45 DEG FITTING APPROX 3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302000 | 168531.015 | 373305.8601 | 2000 | 747.2767 | 300000 | 372558.5834 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 867596 | 2008-04-10 | 780 | 877 | NO | NO | YES | NO | NO | NO | MARK A. MICKELBERG | 6519940332 | MARK.MICKELBERG@ONEOK.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2003 | 6 | 0.28 | ASTM A234 | 35000 | SMLS | NA | CHICAGO TUBE & IRON | 2003 | UNDER GROUND |  | 42 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE 6" 45 DEGREE FITTING WAS SENT TO A TESTING LAB FOR FAILURE ANALYSIS. DURING CONSTRUCTION OF THE GRAND FORKS LEVEE BY THE ARMY CORPS OF ENGINEERS, HEAVY EQUIPMENT MAY HAVE CROSSED THE PIPELINE IN THIS LOCATION, WHICH MAY HAVE INITIATED THE CRACKING OF THE FITTING AND RESULTANT FAILURE. THE RESULTS OF THE ANALYSIS CONCLUDED: 1) EXCESSIVE EXTERNAL STRAIN CAUSED TRANSVERSE CRACKS IN THE EPOXY COATING AND AND WERE PROBABLY RELATED TO ABOVE GROUND FORCES DIRECTLY OVER THE PIPELINE ELBOW. 2) THE CRACKS IN THE EPOXY COATING RESULTED IN SEPARATION OF THE COATING FROM THE PIPE. 3) THERE WERE NUMEROUS CRACK LIKE FEATURES (CLF) ON THE INSIDE SURFACE OF THE ELBOW. TWO FATIGUE CRACKS INITATED AT THESE CLF'S AND CONTINUED TO CRACK THROUGH THE ENTIRE WALL THICKNESS UNTIL LEAKAGE OCCURRED. THE PRIMARY CAUSE OF THE FAILED FITTING AND GAS LEAKAGE WAS EXTERNAL STRESSES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080043 | 2008-04-17 15:15 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 630 | 2008-04-04 | 2008 | ASHLAND | CLARK | KS | 67831 | 59.6 |  | N37.26060 | W99.72115 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69783 | 32579.5269 | 43307.843 | 49933 | 18656.8834 | 19850 | 24650.9596 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 867053 | 2008-04-04 | 335 | 500 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1931 | 24 | 0.31 | 5L | 36000 |  |  | A. O. SMITH |  | UNDER GROUND |  | 46 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1965 | NO | [57 empty] | ON APRIL 4, 2008 AT APPROXIMATELY 0630 A PERSON FROM THE GENERAL PUBLIC REPORTED WHAT HE THOUGHT WAS A MINOR GAS LEAK. NORTHERN PERSONNEL RESPONDED AND DETERMINED THAT IT WOULD REQUIRE THAT A SEGMENT OF THE LINE BE ISOLATED AND BLOWDOWN TO SAFELY EXCAVATE AND REPAIR THE LEAK. APPROPRIATE BLOCK VALVES WERE CLOSED TO ISOLATE THE PIPELINE SEGMENT AND THE LINE WAS BLOWN DOWN TO ZERO PRESSURE. A SLIGHTLY SMALLER THAN 1/4 INCH PIN HOLE LEAK WAS FOUND. REPAIRS WERE MADE BY INSTALLING A .375 WALL THICKNESS DRESSER STYLE 220 SLEEVE. THERE WAS NO FIRE, NO INJURIES AND NO EVACATION OF PERSONNEL. THE COST OF REPAIR INCLUDING GAS LOSS IS ESTIMATED TO EXCEED THE $50,000 REPORTING THRESHOLD. THE EVENT WAS REPORTED TO THE NRC VIA TELEPHONE WITH ASSIGNED REPORT NUMBER 867053 ON 4/4/08. A FINAL REPORT WILL BE SUBMITTED ONCE ALL COST OF REPAIRS IS DETERMINED. SUPPLEMENTAL/FINAL REPORT: ESTIMATED COST SUBMITTED ON THE INITIAL REPORT HAVE BEEN UPDATED WITH FINAL TOTAL COST. NO OTHER ACTIONS ARE REQUIRED OR PLANNED. THIS IS CONSIDERED AS CLOSED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080044 | 2008-04-18 14:18 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1430 | 2008-03-31 | 2008 | GLENN | GLENN | CA |  | LINE 169C MP1.98 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43800 | 24184.0635 | 52396.6389 | 2300 | 859.3682 | 41500 | 51537.2707 | 0 | 0 | NO | NO | NO | YES | 2 | COMPANY POLICY | 1 | 0 | 866595 | 2008-03-31 | 215 | 275 | NO | NO | YES | NO | NO | NO | RICHARD ARITA | 9259744313 | RTA2@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 12 | 0.22 | API-5L | 35000 | ERW |  |  | 1955 | OTHER | IRRIGATION DITCH |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | CLEANING & DEEPENING DITCH | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | A CONTRACTOR WAS CLEANING AND DEEPENING AN IRRIGATION DITCH WITH A "V-PLOW" AND STRUCK A 12-INCH GAS LINE. CONTRACTOR DID NOT CALL FOR UNDERGROUND SERVICE ALERT (ONE-CALL) PRIOR TO EXCAVATING. THERE WERE TWO GAS LINE MARKERS POSTED ON BOTH SIDE OF THE IRRIGATION DITCH. HAD CONTRACTOR CALLED UNDERGROUND SERVICE ALERT, COMPANY PERSONNEL WOULD HAVE LOCATED PIPE AND STANDBY DURING EXCAVATION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080045 | 2008-04-30 15:29 | ORIGINAL | 8010 |  | IBERVILLE PARISH NATURAL GAS SYSTEM | 59805 BAYOU ROAD | PLAQUEMINE | IBERVILLE | LA | 70764 | 440 | 2006-12-05 | 2006 | PLAQUEMINE | IBERVILLE | LA | 70764 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | REGULATOR FROZE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 | [7 empty] | NO | NO | NO | NO | NO | NO | BRIAN BERTHELOT | 2256875152 | BBERTHELOT@IBERVILLEPARISH.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | OTHER | REGULATOR |  |  | NO | NO | NO | REGULATOR/METERING | [8 empty] | FISHER 627 |  | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | REGULATOR FROZE CAUSING RELIEF VALVE TO VENT
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080047 | 2008-05-07 11:43 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1230 | 2008-04-09 | 2008 | [6 empty] | 28 05 06.202 | 87 59 09.021 | OFFSHORE |  | MISSISSIPPI CANYON | 920 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17000000 | 9501325.4162 | 21111653.0591 | 0 | 0 | 17000000 | 21111653.0591 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 867418 | 2008-04-09 | 3300 | 3640 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPROD.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2007 | 20 | 1.21 | API 5L | 65000 | DSAW |  |  |  | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | FLEX JOINT SEAL RING | [8 empty] | MATERIAL DEFECT |  | NO | YES | 4 | 20 | 2007 | WATER |  | 8 | 4550 | [12 empty] | GAS BUBBLES WERE DETECTED AT THE SURFACE OF MC 920. AFTER INVESTIGATION, IT WAS DETERMINED THAT THE FLEX JOINT SEAL RING WAS LEAKING. PIPELINE WAS SECURED AND REPAIR PROCEDURES HAVE BEEN IMPLEMENTED AND WORK IS ONGOING. THE OFFSHORE REPLACEMENT OPERATION OF THE 20¿ FLEX-JOINT O-RING WAS PERFORMED IN THREE (3) PHASES: PHASE I, DETAILED INSPECTION AND INITIAL BOLT TIGHTENING APRIL 9, TO APRIL 23, 2008 PHASE II, FLEX-JOINT O-RING REPLACEMENT APRIL 24, TO JUNE 16, 2008 PHASE III, FINAL BOLT TIGHTENING, UT VERIFICATION, TESTING JULY 28, TO AUGUST 8, 2008 ENTERPRISE CONFIRMS THE 20 INCH FLEX-JOINT O-RING REMEDIATION WAS SUCCESSFULLY COMPLETED IN ACCORDANCE WITH THE WORK PLAN, AND ON AUGUST 9, 2008 NORMAL PRODUCTION WAS RESUMED IN THE GAS EXPORT PIPELINE. FOR THE POST INSPECTION PERIOD, AUGUST 8, TO SEPT 8, 2008, ¿REMOTE CAMERAS¿ WERE USED TO MONITOR THE FLEX-JOINT. ENTERPRISE AND OIL STATES HAVE WORKED CLOSELY TO ANALYZE AND EVALUATE BOTH HISTORIC AND PROJECT DATA ON THE FLEX-JOINT AND INCIDENT TO BEST DETERMINE THE DIRECT CAUSE OF THE LEAK. THERE WAS NO IDENTIFIED SINGLE ITEM OR CLEAR DIRECT CAUSE FOR THE LEAK. HOWEVER, THE EVALUATION AND ANALYSIS POINTS TO A SERIES OF EVENTS THAT TOGETHER MOST LIKELY CONTRIBUTED TO THE CAUSE OF THE LEAK. THE FACTORS IDENTIFIED INCLUDED POSSIBLE INCORRECT ATTACH FLANGE BOLT TORQUE VALUE READINGS DURING THE FINAL MANUFACTURING SHOP ASSEMBLY, WHICH COULD ALLOW EXCESS ATTACH FLANGE DEFLECTION, AND SLIGHT BOLT RELAXATION DURING HYDROTESTING. THE O-RING DESIGN, DIMENSION, AND DISSIMILAR MATERIALS WERE ALSO A FACTOR. AFTER OFFSHORE INSTALLATION OF THE FLEX-JOINT AND DURING PIPELINE OPERATIONS, FRETTING BEGAN TO TAKE PLACE WITHIN THE O-RING SEAL SYSTEM. THIS DEVELOPMENT THEN LED TO THE PROGRESSION OF MINOR CORROSION, AND INDUCTION OF SEA WATER, WHICH AFTER A PERIOD OF TIME PROGRESSED UNTIL THE LEAK STARTED. DURING THE OFFSHORE REPAIR PHASES, CORRECTIVE ACTIONS WERE IMPLEMENTED TO ADDRESS EACH OF THE POTENTIAL CAUSES, WHICH INCLUDED A NEWLY DESIGNED LARGER O-RING WHICH IS NOW THE SAME MATERIAL AS THE ATTACH FLANGE, AND ACCURATE BOLT TORQUING MEASURED AND VERIFIED BY UT STUD ELONGATION PROCESS. THIS UT PROCESS ELIMINATES ANY UNKNOWN FRICTION FACTORS WHICH AFFECT BOLT TORQUE VALUES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080048 | 2008-05-07 | SUPPLEMENTAL FINAL | 792 |  | ATLANTA GAS LIGHT CO | 10 PEACHTREE PL NE | ATLANTA | FULTON | GA | 30309 | 1934 | 2008-03-31 | 2008 | ATLANTA | FULTON | GA | 30354 |  |  | 33.6609116 | -84.3494263 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 35685.5058 | 76379.9084 | 5000 | 1868.1917 | 60000 | 74511.7167 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 866585 | 2008-03-31 | 250 | 300 | NO | NO | NO | NO | YES | NO | RALPH MCCOLLUM, STAFF ENGINEER | 4045843733 | MCCOLLU@AGLRESOURCES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 24 | 0.31 |  | 42000 | SPIRAL WELDED PIPE |  | UNKNOWN |  | UNDER GROUND |  | 48 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | THIS INCIDENT BEGAN AS A GRADE 2 LEAK DISCOVERED AT A VALVE BOX OVER A 6-INCH VALVE CONNECTING TO A 24-INCH MAIN DURING THE ANNUAL LEAKAGE SURVEY WHICH DID NOT REQUIRE IMMEDIATE ATTENTION AT THE TIME OF DISCOVEREY. HOWEVER, IT WAS DISCOVERED SEVEN DAYS LATER DURING REPAIR THAT THE LEAK WAS ACTUALLY LOCATED ON THE 24-INCH STEEL MAIN ABOVE THE 6-INCH WELDED CONNECTION. FOR THIS REASON, REPAIRS TO THE 24-INCH STEEL MAIN EXCEEDED THE $50,000 REQUIREMENT FOR REPORTING. AN INVESTIGATION DETERMINED THAT THE SUPPORT UNDERNEATH THE 6-INCH CONNECTION SUBSIDED DUE TO INCREASED WATER LEVELS IN A LOW AREA. AS A RESULT, THE 24" LINE FAILED IN THE BASE METAL DUE TO DUCTILE OVERLOAD ADJACENT TO THE WELDED JOINT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080049 | 2008-05-08 11:32 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 2235 | 2008-04-12 | 2008 | PORT SULPHUR | PLAQUEMINES | LA | 70083 | 11.5 | LAKE WASHINGTON LOOP | 29.30.2 | -89.40.8 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7450000 | 4105937.9165 | 8861170.8675 | 450000 | 168137.2549 | 7000000 | 8693033.6126 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 867803 | 2008-04-12 | 750 | 1100 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12.75 | 0.5 |  | 35000 | SEAMLESS |  | NATIONAL TUBE | 1958 | UNDER WATER |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A VESSEL NAVIGATING THE MISSISSIPPI RIVER LOST POWER AND DROPPED ANCHOR. THE ANCHOR STRUCK ONE OF SOUTHERN NATURAL GAS COMPANY'S 12" RIVER CROSSING LINES FOR ITS LAKE WASHINGTON LOOP PIPELINE. THE ANCHOR PUNTURED THE PIPE RESULTING IN A NATURAL GAS RELEASE THAT CAUSED THE US COAST GUARD TO CLOSE THE RIVER TO THROUGH TRAFFIC UNTIL THE PIPELINE COULD BE SECURED. THE 12" RIVER CROSSING LINE WAS ISOLATED AND REMAINS OUT OF SERVICE. RIVER TRAFFIC WAS RESTORED ABOUT THREE HOURS FOLLOWING THE INITIAL DAMAGE. UPDATE AUGUST 4, 2009: THIS 12" RIVER CROSSING LINE IS PLANNED FOR IN PLACE ABANDONMENT WITH WORK SCHEDULED TO BEGIN IN SEPTEMBER 2009.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080050 | 2008-05-13 10:05 | SUPPLEMENTAL FINAL | 13299 |  | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF RD, PO BOX 1464 | WALL | MONMOUTH | NJ | 07719 | 2340 | 2008-05-06 | 2008 | OLD BRIDGE | MIDDLESEX | NJ | 08857 |  |  |  |  | ONSHORE | 4 |  |  |  | NO | NO | INTRASTATE | OTHER | CONSTRUCTION DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151485 | 77657.4265 | 140818.2938 | 54485 | 20357.6852 | 97000 | 120460.6086 | 0 | 0 | YES | NO | NO | NO | 0 |  | 1 | 45 | 870013 | 2008-05-06 | 276 | 525 | YES | NO | NO | NO | NO | NO | MOBEEN KHAN | 7329198035 | MUKHAN@NJNG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 10.75 | 0.28 |  | 25000 | SEAMLESS |  |  |  | UNDER GROUND |  | 102 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | CONTRACTORS WORKING FOR NEW JERSEY NATURAL GAS COMPANY INSTALLING A 20INCH TRANSMISSION TO REPLACE THE EXISTING 10INCH LINE. DRILLING ACROSS AND ABOVE THE 10INCH LINE AT 45DEGREE ANGLE DAMAGED THE 10INCH LINE WHICH WAS APPROXIMATELY 8.5 FEET DEEP AT LOCATION OF CROSSING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080051 | 2008-05-19 16:14 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1730 | 2008-05-18 | 2008 | CLATONIA | GAGE | NE | 68328 | 0.2 | SEC 21, TWP 6N, RGE 5E | 40.4782654 | -96.8740492 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283192 | 124784.1059 | 125599.0741 | 260401 | 97295.7985 | 22791 | 28303.2756 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 871342 | 2008-05-18 | 479 | 500 | NO | NO | NO | NO | YES | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 2.38 | 0.15 |  | 24000 |  |  |  |  | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | NO | [19 empty] | ON MAY 18, 2008, AT APPROXIMATELY 5:30 P.M., NORTHERN'S OPERATIONS COMMUNICATION CENTER (OCC), RECEIVED A CALL FROM DANA ELIKER, A TECHNICIAN WITH AQUILA, REPORTING THAT THERE WAS A LEAK ON NORTHERN'S TWO-INCH CLATONIA, NE BRANCH LINE (NEB42201)IN A CORNFIELD APPROXIMATELY 1/4 MILE NORTHWEST OF THE TOWN OF CLATONIA, NE. THE LEAK SITE IS LOCATED IN SECTION 21, TOWNSHIP 6N, RANGE 5E, GAGE COUNTY, NE. NORTHERN PERSONNEL UTILIZED A BOTTLE TRUCK AT THE CLATONIA TOWN BORDER STATION TO PROVIDE GAS SERVICE TO THE TOWN WHILE THE BRANCH LINE WAS SHUT OFF FROM THE TAKE OFF TO THE TBS TO SAFELY ASSESS AND REPAIR THE LINE. THIS LINE'S CONSTRUCTION INCLUDES DRESSER COUPLING, ELECTRIC WELDS AND SCREWED COUPLINGS. UPON ASSESSMENT, IT WAS FOUND THAT THE THREADS ON THE PIPE GOING INTO A TWO-INCH SCREWED COUPLING HAD FAILED RESULTING IN LEAKING GAS. LINE PRESSURE WAS REDUCED TO ZERO AND REPAIRS WERE MADE BY CUTTING OUT THE FAILED COUPLING ALONG WITH SMALL PIECES OF THE LINE, ON EACH SIDE OF THE COUPLING, AND INSTALLING APPROXIMATELY 10 FEET OF NEW, TESTED TWO-INCH, .218 WALL THICKNESS PIPE. PRESSURE WAS RESTORED TO 100 PSIG AND THE COMPLETE 1.26 MILES OF LINE WAS INSTRUMENT LEAK DETECTED. THE PRESSURE WAS THEN INCREASED TO NORMAL OPERATING PRESSURE AND THE FULL LENGTH OF THE LINE WAS AGAIN INSTRUMENT LEAK DETECTED. UPON SUCCESSFUL LOADING OF THE LINE TO NORMAL PRESSURE AND NO LEAKS DISCOVERED NORMAL GAS SERVICE WAS RESTORED TO THE TOWN BORDER STATION OF CLATONIA. THE SMALL PIECES OF PIPE AND THE FAILED COUPLING ARE BEING SENT TO A LABORATORY FOR FAILURE ANALYSIS TO ASSIST WITH DETERMINING THE ROOT CAUSE OF THE FAILURE. THERE WAS NO FIRE, NO INJURIES AND NO LOSS OF SERVICE AS THERE ARE NO FARM TAP CUSTOMERS ON THE LINE AND THE CLATONIA TOWN BORDER STATION SERVICE WAS MAINTAINED WITH A BOTTLE TRUCK. THIS REPORT IS BEING FILED AS IT IS EXPECTED THAT REPAIRS, INCLUDING GAS LOSS, WILL EXCEED THE $50,000 REPORTING THRESHOLD. SUPPLEMENTAL/FINAL REPORT - TOTAL FINAL COST OF REPAIRS, INCLUDING GAS LOSS, ETC IS $283,192. BASED UPON A OUTSIDE SERVICES FAILURE ANALYSIS LABORATORY REPORT, THE ROOT CAUSE OF THIS FAILURE IS BELEIVED TO BE FRACTURING OF THE PIPE BY CLEAVAGE (A FORM OF BRITTLE CRACKING) ORIGINATING IN THE THREAD ROOT IMMEDIATELY ADJACENT TO THE CONNECTION COUPLING. THIS EVENT IS CONSIDERED CLOSED WITH NO FURTHER ACTIONS PENDING OR PLANNED. NORTHERN IS SCHEDULUED ADDITION PRECUATIONARY EQUIPMENT LEAK TESTING OF OTHER SMALL DIAMTER PIPELINES OF THIS SAME VINATAGE AND CONSTRUCTION TO ENABLE EARLY DETECTION OF LEAK SHOULD A SIMILAR CONDITION OCCUR ON ANY OF THESE FACILITIES. ADDED INCIDENT COORDINATES PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080052 | 2008-05-28 12:10 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 2200 | 2008-05-24 | 2008 | CUNNINGHAM | PRATT | KS | 67035 |  | SEC 3, T28S, R11W | 37.6415303 | -98.5191754 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | DAMAGE SUSTAINED FROM TORNADO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 95013.2542 | 211116.5306 | 0 | 0 | 0 | 0 | 170000 | 211116.5306 | NO | NO | NO | NO | 0 |  | 1 |  | 871941 | 2008-05-24 |  |  | NO | NO | NO | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | BUILDING DAMAGE | STEEL |  | NO | NO | NO | OTHER | RE-COMPRESSOR BUILDING | [9 empty] | ABOVE GROUND |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | ON MAY 24, 2008 AT APPROXIMATELY 09:46 FACIITIES IN THE CUNNINGHAM STORAGE FIELD WERE STRUCK BY TORNADIC ACTIVITY. THE RE-COMPRESSOR BUILDING @ WELL # 345 WAS HEAVILY DAMAGED BY WIND. THIS SITE IS LOCATED WEST OF THE LIQUIDS PLANT-SOUTH OF HIGHWAY 54, PRATT COUNTY, KANSAS. IN ADDITION MINOR DAMAGE WAS INCURRED AT OB-WELL 26-41 WHICH RESULTED IN A MINOR LEAKAGE OF GAS DUE TO LUBRICATOR TUBING BEING DAMAGED. PERSONNEL WERE ABLE TO SHUT IN THE PIPING AND STOP THE LEAK UPON DISCOVERY. THIS EVENT WAS REPORTED TO THE NRC TICKET # 871941. THE WAS NO DAMAGE TO THE CUNNINGHAM COMPRESSOR STATION, HOWEVER ELECTRICAL POWER LINES, THAT PROVIDE ELECTRICAL SERVICE TO THE PLANT APPEAR TO HAVE APPROXIMATELY 4 MILES OF POLES AND LINE DAMAGED. THE FACILITY IS UTILIZING PORTABLE ELECTRICAL GENERATORS TO SUPPLY THEIR ELECTRICAL NEEDS. THERE WERE NO INJURIES, FIRE OR BLOWING GAS ASSOCIATED WITH THIS EVENT, HOWEVER IT WAS REPORTED AS IT WAS DEEMED AS SIGNFICANT AND IT IS LIKELY THAT REPAIR COST WILL EXCEED THE $50,000 REPORTING THRESHOLD. SUPPLEMENTAL/FINAL REPORTS WILL BE SUBMITTED AS ALL DAMAGE IS IDENTIFIED AND A FINAL COST OF REPAIRS IS CALCULATED. FINAL REPORT: TOTAL ESTIMAED REPAIR DAMAGE IS CALCULATED AT $170,000. ROOT CAUSE WAS HIGH WINDS/TORNADO. DAMAGE WAS INCURRED TO A NUMBER OF BUILDINGS AND EQUIPMENT. THERE WAS NO GAS LOSS, NO FIRE AND NO INJURIES. NO FURTHER ACTIONS ARE PENDING OR PLANNED. THIS INCIDENT WAS REPORTED AS IT WAS DEEMED AS SIGNIFICANT AND COST OF REPAIRS WERE EXPECTED TO EXCEED THE $50,000 REPORTING THRESHOLD LIMIT. THIS EVENT IS CONSIDERED CLOSED. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080053 | 2008-05-28 13:30 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 539 | 2008-05-25 | 2008 | GAYLORD | SIBLEY | MN | 55334 | 25.28 | SEC 36, T113N, R29W | 44.5576844 | -94.2665670 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85203 | 46224.8331 | 96391.8737 | 10848 | 4053.2288 | 74355 | 92338.6449 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 872025 | 2008-05-25 | 800 | 950 | YES | NO | NO | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 3.5 | 0.16 | 5LX | 42000 |  |  | LONE STAR |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | DRAIN TILE | NO |  |  |  |  | NO | [40 empty] | ON MAY 25, AT APPROXIMATELY 0630 A.M., NORTHERN'S OCC RECEIVED A CALL FROM THE SIBLEY COUNTY SHERIFF REPORTING THAT A PASSER-BY HAD REPORTED GAS BLOWING IN A FIELD NEAR GAYLORD, MN. OPERATIONS PERSONNEL RESPONDED TO THE SITE AND CONFIRMED A LEAK ON THE MNB69801, 3-INCH WINTHROP, MN BRANCH LINE. LINE PRESSURE AT THE TIME WAS APPROXIMATELY 800 PSIG. PRESSURE WAS LOWERED TO 350 PSIG. BOTTLE TRUCKS AND STOPPLE PERSONNEL WERE DISPATCHED TO THE SITE. STOPPLE FITTINGS WERE WELDING ON BY APPROXIMATELY 10 P.M. ON MAY 26 THE BOTTLE TRUCKS WERE CONNECTED TO SUPPLY GAS TO THE TOWN OF WINTHROP, MN TBS # 1. THE STOPPLE WAS SET IN PLACE AND APPROXIMATELY 4 MILES OF 3-INCH BRANCH LINE WERE BLOWN DOWN TO ZERO PRESSURE. THE LEAK SITE WAS EXCAVATED TO EXPOSE THE PIPELINE. THE LINE WAS FOUND TO BE DENTED AND LEAKING, APPARENTLY AS A RESULT OF BEING HIT BY A TILING MACHINE. A 30 FOOT SEGMENT OF PIPE WAS REPLACED WITH NEW, TESTED PIPE. DUE TO THE COATING APPEARING TO BE DISBONDED AND CRACKED A MAGNETIC PARTICLE INSPECTION WAS CONDUCTED ON AREAS OF THE PIPE. A FOUR FOOT PIECE OF THE PIPE WAS REMOVED AND TRANSPORTED TO A LABORATORY FOR ANALYSIS. THE REPAIRED, DAMAGED AREA WAS RE-COATED AND BACK FILLED. THE LINE WAS PURGED AND PRESSURE WAS RESTORED TO THE LINE TO BE MAINTAINED, NOT TO EXCEED 699 PSIG, PENDING RETURN OF LAB ANALYSIS AND FINALIZATION OF INVESTIGATION OF THE INCIDENT. AN INTERNAL POST INCIDENT INVESTIGATION IS BEING CONDUCTED. AN NRC REPORT WAS FILED AND THIS 7100 REPORT IS BEING FILED AS THIS IS CONSIDERED AS A SIGNIFICANT EVENT AND IT IS LIKELY THAT COST OF REPAIRS WILL EXCEED THE $50K REPORTING THRESHOLD. ADDITIONAL SUPPLEMENTAL/FINAL REPORTS WILL BE FILED REGARDING LAB ANALYSIS AND FINAL CALCULATION OF TOTAL COST OF REPAIR. SUPPLEMENTAL/FINAL REPORT: AN INVESTIGATION INDICATES THAT THE ROOT CAUSE OF THIS EVENT WAS THAT THE LANDOWNER INTALLED DRAINAGE TILE, WITHOUT MAKING A ONE CALL REQUEST, SOMETIME DURING 2006, AND IN THE PROCESS THE PIPLINE WAS STRUCK. THE COATING AND PIPE WAS DAMAGED WHICH RESULTED IN THE GAS LEAK. AN APPROXIMATE 30 FEET OF NEW, TESTED, COATED PIPE WAS INSTALLED TO COMPLETE THE REPAIRS. LABORATORY ANALYSIS WAS COMPLETED AND NO OTHER FACTORS WERE FOUND TO HAVE CONTRIBUTED TO THE LEAK BEYOND THE DAMAGED SUSTAINED DURING THE DRAINAGE TILE INSTALLATION IN 2006. THIS INCIDENT IS CONSIDERED CLOSED WITH NO FURTHER ACTIONS PLANNED OR PENDING. CIRCUMSTANCES/PARTICULARS OF THE INCIDENT AND COST HAVE BEEN TURNED OVER TO NORTHERN'S LEGAL DEPARTMENT FOR APPROPRIATE FOLLOW-UP ACTIONS. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080054 | 2007-04-24 | ORIGINAL | 32327 |  | MAVERICK-DIMMIT PIPELINE LTD | 777 E. SONTERRA BLVD., SUITE 350 | SAN ANTONIO | BEXAR | TX | 78258 | 1130 | 2006-03-06 | 2006 | CARRIZO SPRINGS | DIMMIT | TX | 78834 |  | No. 7, A-393 | N28 34.874 | W100 01.759 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46700 | 27365.8366 | 60806.0478 | 0 | 0 | 0 | 0 | 46700 | 60806.0478 | NO | YES | NO | NO | 0 |  | 1 | 0 |  |  | 850 | 1128 | YES | NO | NO | NO | NO | NO | STEVE CRUSE, PIPELINE MANAGER | 2104965300 | SCRUSE@TX.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 12 | 0.19 | [6 empty] | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PIPELINE |  | NO |  |  |  |  | YES | [40 empty] | THE PIPELINE WAS HIT BY A BACKHOE OPERATOR WHO WAS WORKING UNDER THE SUPERVISION OF THE LANDOWNER. THEY HAD FAILED TO PROPERLY NOTIFY THE PROPER AUTHORITIES THAT THEY WOULD BE DOING EXCAVATION WORK IN THE AREA OF THE PIPELINE. THE PIPELINE WAS CLEARLY MARKED BY SIGNS AND DAMAGES TO THE PIPELINE WERE SOLELY FROM THE NEGLIGENCE OF THE BACKHOE OPERATOR.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080055 | 2008-05-29 11:44 | SUPPLEMENTAL FINAL | 18516 | 18516 | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 1400 | 2008-05-01 | 2008 |  |  | LA |  | MAIN PASS 107 LINE | M.P. 0.096 | 29 32 30 N | 88 43 38 W | OFFSHORE |  | MAIN PASS | 107 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528000 | 293427.9519 | 644416.2 | 13000 | 4857.2985 | 515000 | 639558.9015 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 869612 | 2008-05-01 | 800 | 1200 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 16 | 0.5 | API 5L | 52000 |  | FULL OPENING BALL | GROVE | 1972 | UNDER WATER |  |  | MATERIAL AND/OR WELD FAILURES | JOINT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [34 empty] | O-RING | [7 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | A SURVEY VESSEL IN THE VICINITY OF A SUBSEA TIE-IN ASSEMBLY ON SOUTHERN NATURAL GAS (SNG) COMPANY'S MAIN PASS 107 PIPELINE, OFFSHORE LOUISIANA, REPORTED SEEING EVIDENCE OF A POSSIBLE GAS LEAK. DUE TO NUMEROUS PIPELINES AT THE LOCATION AND NO PRESSURE DROP SEEN ON THE SNG SYSTEM, A SUBSTANTIAL EFFORT WAS MADE TO CONFIRM THE OWNERSHIP OF THE LEAK. INVESTIGATION BY PERSONNEL FROM A DIVE VESSEL SNG DISPATCHED TO THE LOCATION REVEALED THAT GAS WAS ESCAPING FROM A BOLTED FLANGE CONNECTION IN THE SUBSEA ASSEMBLY. THE CAUSE WAS A DAMAGED O-RING SEAL THAT APPEARED TO HAVE BEEN GOUGED UPON INSTALLATION. A NEW O-RING AND NEW BOLTS WERE INSTALLED TO REPAIR THIS CONNECTION. THE PIPELINE WAS PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080056 | 2008-06-04 18:26 | SUPPLEMENTAL FINAL | 11820 |  | BRIDGELINE HOLDINGS, LP | 4800 FOURNACE PLACE | BELLAIRE | HARRIS | TX | 77401-2324 | 1055 | 2008-04-29 | 2008 | PORT ALLEN | WEST BATON ROUGE | LA | 70767 | MILE POST 5.2 | 265+17 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | UNKNOWN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2516000 | 1404138.2693 | 3110633.0751 | 16000 | 5978.2135 | 2500000 | 3104654.8616 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 | 869397 | 2008-04-29 | 530 | 811 | NO | YES | NO | NO | NO | NO | HENRY L. LEGER - DOT PIPELINE SAFETY SPECIALIST | 3376548915 | HENRYLEGER@CHEVRON.COM | TRANSMISSION | OTHER | UNKNOWN | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 16 | 0.5 | API 5LX-52 | 520000 | ERW | N/A |  | 1954 | UNDER WATER |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | THE CAUSE OF THE INCIDENT AND THE FACTOR/S CONTRIBUTING TO IT IS/ARE UNKNOWN. THE INCIDENT, WHICH IS BELIEVED TO HAVE BEEN A LINE RUPTURE, OCCURRED APPROXIMATELY MID-RIVER ON THE 16-INCH MISSISSIPPI RIVER RIVER CROSSING WHICH IS LOCATED APPROIMATELY 500-FEET NORTH OF THE U.S HWY 190 MISSISSIPPI RIVER BRIDGE, JUST EAST OF THE TOWN OF PORT ALLEN, LA. AT THE TIME OF THE INCIDENT, THE MISSISSIPPI RIVER STAGE AND FLOW WERE AT A RECORD HIGH AND IT IS SUSPECTED THAT THESE CONDITIONS MAY HAVE CONTRIBUTED TO THE INCIDENT. THE LINE IS PRESENTLY OUT OF SERVICE WITH NO PRESSURE. DUE TO THE DANGERS INVOLVED IN RECOVERING THE IMPACTED PIPE FOR INVESTIGATION, BRIDGELINE HOLDINGS, L.P. HAS OPTED TO FORGO THE INVESTIGATION AND NOT REPAIR BUT ABANDON THE RIVER CROSSING IN PLACE. PLEASE NOTE THAT THE OPERATOR DAMAGE STATED IN THIS REPORT IS AN ESTIMATED COST OF INSTALLING A NEW DRILLED CROSSING. AT THIS POINT IN TIME, THERE ARE NO PLANS TO REPLACE THE CROSSING WITH A NEW DRILLED CROSSING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080057 | 2008-06-05 10:21 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 2055 | 2008-05-16 | 2008 | JOLIET | WILL | IL | 60436 | MILE 2 | 126+25 | 41.4914 | 88.1103 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94000 | 48163.7193 | 87215.4204 | 34000 | 12703.7037 | 60000 | 74511.7167 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 5 | 871186 | 2008-05-16 | 390 | 437 | NO | YES | NO | NO | NO | NO | SUZIE DAVIS | 7133699707 | SUZANNE_DAVIS@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 24 | 0.25 | 5LX52 | 52000 | ERW-HF |  | STUPP | 1970 | UNDER GROUND |  | 60 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | DURING A ROUTINE CASING VENT SURVEY AN EMPLOYEE SMELLED GAS AND INITIATED AN INVESTIGATION OF THE ROW IN THE AREA. HE FOUND AN AREA OF DEAD VEGETATION AND A LEAK WAS CONFIRMED. WHILE EXCAVATING TO DETERMINE CAUSE OF LEAK IT WAS DISCOVERED THAT ANOTHER OPERATOR, COMMONWEALTH EDISON COMPANY, HAD INSTALLED AT SOME TIME IN THE PAST A GROUNDING SYSTEM TIED TO THEIR FENCING AROUND AN ELECTRICAL SUBSTATION. THE GROUND WIRE WAS LAID DIRECTLY ABOVE THE PIPELINE DAMAMGING THE COATING. AT SOME POINT AN ELECTRICAL DISCHARGE FROM THE GROUNDING ROD TO THE DAMAMGED PIPE RESULTED IN A PINHOLE LEAK APPROXIMATELY THE SIZE OF 1/32" RESULTING IN REPLACEMENT OF AN 8' PIECE OF PIPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080058 | 2008-06-05 12:46 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1457 | 2008-05-23 | 2008 | BEAVER BAY | LAKE | MN | 55601 | APPROX 59.5 |  | 47.27101 | -91.34526 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530000 | 294185.6237 | 644468.8978 | 15800 | 5903.4858 | 514200 | 638565.4119 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 871912 | 2008-05-23 | 405 | 425 | NO | NO | NO | YES | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 16 | 0.22 | 5LX | 52000 | ERW |  | REPUBLIC |  | UNDER GROUND |  | 38 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | ON MAY 23, AT APPROXIATELY 14:57 THE CARLTON LOCATION WAS NOTIFIED BY ANGEL SERVICE ITT CORP, THAT THEY HAD COMPLETED THEIR AERIAL LEAK SURVEYING. UPON REVIEW OF THE INFORMATION IT APPEARED THAT THERE WAS A DETECTION OF A SINGLE METHANE INDICATION IN LAKE COUNTY, MN ON THE 16-INCH RESERVE (MNB69801) BRANCH LINE ON THE PIPELINE RIGHT OF WAY APPROXIMATELY 1.1 MILES WEST OF LAX LAKE ROAD @ APPROXIMATE MILEPOST 59.5. NORTHERN PERSONNEL PROCEEDED TO REDUCE THE PRESSURE FROM 405 TO 300 PSIG AND SENT PERSONNEL TO THE SITE TO UTILIZE PORTABLE LEAK DETECTION EQUIPMENT TO VERIFY IF THERE WAS A LEAK. A LEAK WAS DETECTED @ THE APPROXIMATE LOCATION INDICATED. A STRONG HYDRO CARBON SMELL WAS DETECTED, A READING OF 5% LEL WAS INDICATED AND A PATCH OF DEAD VEGETATION APPROXIMATELY 15 FT IN DIAMETER WAS NOTED. ACTIONS WERE TAKEN TO ACQUIRE THE SERVICES OF A CONTRACTOR AND ARRANGE FOR NORTHERN'S STOPPLE CREW TO PROCEED TO THE SITE. AN 8-INCH STOPPLE AND BYPASS WAS INSTALLED AROUND THE LEAK AREA, THEN THE SECTION OF LINE WAS BLOWN DOWN AND EXCAVATED. A ROCK WAS FOUND TO HAVE IMPINGED ON THE PIPELINE AT THE 6 O'CLOCK POSITION. THE IMPINGMENT RESULTED IN A DENT MEASURING APPROXIMATELY 11 INCHES LONGITUDINALLY, SEVEN INCHES CIRCUFERENTIALLY AND 0.903 INCHES DEEP. THERE WAS A CRACK LOCATED AT THE BOTTOM OF THE DENT MEASURING APPROXIMATELY 1-INCH LONG. IT WAS DETERMINED THAT THE LEAK COULD BE REPAIRED BY INSTALLATION OF A 2-FOOT BY 16-INCH TYPE B PRESSURIZED CONTAINING SLEEVE. INSTALLATION OF THE SLEEVE WAS COMPLETED ON JUNE 3. ALL WELDS WERE INSPECTED USING MAGNETIC PARTICLE AND ULTRASONIC THICKNESS METHODS. THE PIPELINE BETWEEN THE STOPPLE FITTINGS WAS PURGED, PRESSURE TESTED AND RETURNED TO NORMAL 405 PSIG SERVICE. THERE WAS NO FIRE, NO INJURIES AND NO LOSS OF SERVICE TO ANY CUSTOMERS. THE ROOT CAUSE OF THE LEAK WAS A ROCK IMPINING ON THE LINE AND GROUND SUBSIDENCE. A FINAL REPORT WILL BE COMPLETED UPON DETERMINATION OF THE TOTAL COST OF REPAIRS. SUPPLEMENTAL REPORT: IN THE NARRATIVE IT WAS INDICATED THAT THE LINE NUMBER WAS MNB69801, WHICH IS INCORRECT AND SHOULD INSTEAD BE MNB72701. SUPPLEMENTAL/FINAL REPORT: TOTAL COST OF REPAIRS ESTIMATES, INCLUDING GAS LOSS HAVE BEEN UPDATED. THE ROOT CAUSE OF THE LEAK WAS DETERMINED TO BE THAT GROUND SUBSIDENCE RESULTING IN A ROCK IMPINGING ON THE LINE, WHICH RESULTED IN DAMAGE TO COATING AND A DENT IN THE LINE AND AN APPROXIMATE ONE INCH CRACK IN THE BOTTOM OF THE DENT WHICH ALLOWED GAS LEAKAGE TO THE ATMOSPHERE. THIS EVENT IS CONSIDERED CLOSED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080059 | 2008-06-06 11:26 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1607 | 2008-05-13 | 2008 | BURAS | PLAQUEMINES | LA | 70041 | MP 57.14 | 1469+44 | 29.36705 | 89.42637 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72671 | 37700.0257 | 70563.8521 | 22671 | 8470.7549 | 50000 | 62093.0972 | 0 | 0 | NO | NO | NO | NO | 0 |  | 116 | 48 | 870791 | 2008-05-13 | 648 | 982 | NO | NO | NO | NO | YES | NO | JACK L. ADAMS | 7134798099 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 16 | 0.31 |  | 46000 | ELECTRIC FLASH WELD |  | A. O. SMITH | 1950 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | WASHOUT | [52 empty] | PIPE IS LOCATED IN A PIPELINE CANAL THAT FEEDS INTO THE MISSIPPI RIVER. A 4" CRACK IN A JOINT WELD RESULTED FROM PIPELINE BEING EXPOSED AND SUSPENDED PIPE SWINGING FROM VERY STRONG WATER CURRENT IN THE MISSISSIPPI RIVER. PIPELINE PRESSURE REDUCED TO 5 PSIG AND A CLAMP WAS INSTALLED AT THE WELD JOINT TO STOP GAS ESCAPING UNTIL PIPELINE REPAIR IS COMPLETED. THE DECISION HAS BEEN MADE TO ABANDON THIS PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080060 | 2008-06-09 19:29 | ORIGINAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1039 | 2008-05-11 | 2008 | GREENVILLE | WAYNE | MO | 29605 |  | LINE A208 1+44 | 37.138621 | -90403837 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FIRE DUE TO LIGHTNING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197000 | 103801.2993 | 202103.8467 | 49000 | 18308.2789 | 148000 | 183795.5678 | 0 | 0 | NO | YES | NO | NO | 0 |  | 3 | 36 | 870559 | 2008-05-11 | 400 | 500 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY,COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING | [13 empty] | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | ON 5/11/08 AT APPROXIMATELY 1040 SYSTEM CONTROL CALLED FIELD PERSONNEL TO INVESTIGATE A HIGH PRESSURE ALARM AT THE PIEDMONT DELIVERY M&R STATION OFF OF LINE A208. UPON ARRIVAL FOUND THE M&R BUILDING ON FIRE. CLOSED TAP VALVES FEEDING THE DELIVERY. AT 1425 FIRE WAS OUT AND REPAIR WORK BEGAN. LINE PUT BACK IN SERVICE ON 5/12/08. SEVERE STORMS HAD PASSED THROUGH THE AREA AND WE BELIEVE A DIRECT HIT FROM A LIGHTNING STRIKE CAUSED THE FIRE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080061 | 2008-06-11 14:00 | SUPPLEMENTAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1750 | 2008-05-18 | 2008 | MARSHALL | HARRISON | TX | 75671 | WEST LINE 136.5 | 7207+76 | 32.631 | -94.2802 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 49201.9994 | 79038.5672 | 52000 | 19429.1939 | 40000 | 49674.4778 | 8000 | 9934.8956 | NO | NO | NO | NO | 0 |  | 1 | 23 | 871412 | 2008-05-19 | 742 | 900 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 16 | 0.25 |  | 52000 | ERW |  | A O SMITH | 1951 | UNDER GROUND |  | 30 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | LANDOWNER HAD A PERSON ON A DOZER CONSTRUCTING A WATER BREAK. NEITHER THE DOZER OPERATOR NOR LANDOWNER PLACED AN ONECALL. OUR PIPELINE WAS IN A PARALLEL RIGHT OF WAY WITH ANOTHER COMPANY AND THE LANDOWNER CALLED THE OTHER PIPELINE LINES EMERGENCY NUMBER. AFTER THEY SENT PERSONNEL TO THE SITE AND VERIFIED THAT IT WASN'T THEIR PIPELINE. THEIR SYSTEM CONTROL GROUP NOTIFIED OUR SYSTEM CONTROL GROUP. WE SENT PERSONNEL TO THE SITE WHO VERIFIED THAT OUR MRT-WEST LINE HAD BEEN HIT. FIELD PERSONNEL ISOLATED LEAK. BLOWDOWN THE LEAK AT A VALVE LOCATED 17 MILES UPSTREAM WHICH WAS IN CADDO PARISH, LA. LINE WAS REPAIRED AND PUT BACK INTO SERVICE WITH NO LOSS OF CUSTOMERS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080062 | 2008-06-17 14:45 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 600 | 2008-06-12 | 2008 | OWASA | HARDIN | IA | 50126 | .46 | SEC20,T88N,R19W | 42.4231883 | -93.2145788 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23947 | 13127.5493 | 28007.6301 | 1994 | 745.0349 | 21953 | 27262.5953 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 |  | 873878 | 2008-06-12 | 784 | 960 | NO | NO | YES | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 2.38 | 0.15 | 5LX | 35000 |  |  |  |  | UNDER GROUND |  | 47 | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | ON JUNE 12, 2008, NORTHERN WAS NOTIFIED OF WHAT APPEARED TO BE A LAZY FLAME TYPE FIRE COMING FROM THE GROUND NEAR THE OWASA, IOWA BRANCH LINE. PERSONNEL RESPONDED AND CONFIRMED THAT THE FIRE WAS COMING FROM THE GROUND ON WHAT WAS THE OWASA, IOWA 2-INCH BRANCH LINE (IAB47201) IN SECTION 20, TOWNSHIP 88N, RANGE 19W, HARDIN COUNTY, IOWA. THE OWASA BRANCH LINE IS APPROXIMATELY 0.932 MILES LONG AND ORIGINATES FROM A SIDE VALVE ON THE 6-INCH IOWA FALLS BRANCH LINE. THE POINT OF FIRE WAS LOCATED AT APPROXIMATE MILE POST .49. THE NRC, IUB AND PHMSA OFFICES WERE NOTIFIED. THE AREA OF THE LEAK AND FIRE HAD INCURRED HEAVY RAIN AND THUNDERSTORMS. IT WAS DETERMINED THAT A BOTTLE TRUCK WOULD BE PUT IN SERVICE AT THE OWASA TBS SO THAT THE LINE COULD BE TAKEN OUT OF SERVICE AND THE FIRE EXTINGUISHED. A CONTRACTOR WITH HEAVY EQUIPMENT AND MATS WAS OBTAINED TO ASSIST WITH REPAIRS. DIRT WAS BERMED TO ENABLE PUMPING OUT WATER TO ALLOW EXCAVATION OF THE SITE. UPON EXCAVATION OF THE SITE ALL INDICATIONS WERE THAT THE LEAK WAS CAUSED BY HIGH VOLTAGE ELECTRIC CURRENT DISCHARGE OFF THE PIPE WALL. THERE WAS DISBONDED COATING AT THE DISCHARGE POINT ON AN OTHERWISE WELL COATED LINE. THE PIPE WALL WAS SHINY AND HAD NOT EVEN FLASH RUSTED YET. THERE WERE NO SIGNS OF CORROSION OR PITTING AND NO CORROSION DEPOSITS OR SCALE. A SINGLE HOLE, APPROXIMATELY 3/8 INCH IN DIAMETER WAS LEAKING THE GAS. ALL INDICATIONS WERE THAT FEATURE CHARACTERISTICS WERE CONSISTENT WITH HIGH VOLTAGE DISCHARGE IN A RAPID EVENT. THE PIT CRATER WAS SMOOTH, NO DEPOSITS, ALMOST PERFECTLY SYMMETRICAL AND ALL METAL SURFACES APPEARED CLEAN AND SHINY. REPAIRS WERE MADE BY INSTALLING APPROXIMATELY 10 FEET OF NEW TESTED, COATED PIPE. IT IS POSSIBLE THAT THE LIGHTNING STRUCK AT OR NEAR THE TBS OR TAKE OFF AS THE BLACK BOX FOR THE PHONE LINE WAS ALSO DAMAGED BY THE LIGHTNING STRIKE. THIS INCIDENT IS NOT EXPECTED TO REACH THE $50,000 THRESHOLD LEVEL FOR REPORTING, HOWEVER DUE TO THE FACT THAT THERE WAS A FIRE THIS REPORT IS BEING FILED. A FINAL REPORT WILL BE FILED WHEN ALL COST HAVE BEEN ACCUMULATED. SUPPLEMENTAL/FINAL REPORT: A TOTAL COST OF REPAIRS,INCLUDING GAS LOSS, WAS CALCULATED AT $23,947. THE ROOT CAUSE OF THE LEAK WAS DETERMINED TO BE CAUSED BY A LIGHTNING STRIKING NEAR OR AT THE TBS/TAKEOFF VALVE RESULTING IN A HIGH VOLTAGE ELECTRIC CURRENT DISCHARGE OFF THE PIPE WALL WHICH CAUSED AN APPROXIMATE 3/8 INCH DIAMETER HOLE IN THE LINE FROM WHICH GAS WAS LEAKING. REPAIRS WERE COMPLETED BY REPLACING APPROXIMATELY 10 FEET OF PIPE WITH NEW TWO-INCH, TESTED, COATED PIPE. THIS INCIDENT DID NOT EXCEED THE $50,000 REPORTING THRESHOLD BUT WAS REPORTED DO TO THE IGNITION OF LEAKING GAS. THIS EVENT IS CONSIDERED CLOSED WITH NO FURTHER ACTIONS PENDING OR PLANNED. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080063 | 2008-06-19 13:03 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 300 | 2008-05-20 | 2008 | HEBER SPRINGS | CLEBURNE | AR | 72543 | LINE BM-21 MP40 | 2121+16 | +35.470734 | -92.042050 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16277 | 8829.4564 | 18406.1453 | 2082 | 777.915 | 14195 | 17628.2303 | 0 | 0 | NO | NO | NO | YES | 6 | PRECAUTIONARY | 3 | 55 | 871556 | 2008-05-20 | 365 | 400 | NO | NO | YES | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 4 | 0.19 | B | 35000 | ERW |  | UNKNOWN | 1957 | UNDER GROUND |  | 6 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GOVERNMENT | ROAD WORK |  | NO |  |  |  |  | YES |  | YES | [38 empty] | 5/20/08 @ 15:15 HRS ¿ FIELD OFFICE RECEIVED A CALL FROM SGO EMPLOYEE, INDICATING THE CLEBURNE COUNTY ROAD DEPT. HAD HIT BM-21 AT 15:05HRS, WITH A ROAD GRADER WHILE CLEANING OUT A ROAD DITCH ON BRIDAL VAIL ROAD. NO ONECALL HAD BEEN MADE. PIPELINE WAS WELL MARKED, 3 SIGNS WERE VISIBLE WITHIN 100YRDS OF DAMAGE. HEBER SPRINGS FIRE DEPARTMENT EVACUATED 6 PEOPLE FROM DOWNSTREAM OF LOCATION. CLEBURNE COUNTY SHERRIFFS DEPARTMENT BLOCKADED THE ROAD TO KEEP TRAFFIC FROM COMING NEAR INCIDENT AREA. 19:41HRS THE LINE WAS REPAIRED AND RETURN TO NORMAL SERVICE. WHILE THIS EVENT DID NOT MEET THE NORMAL DEFINITION OF AN INCIDENT, THE OPERATOR DEEMED IT SIGNIFICANT DUE TO THE EVACUATION AND ROAD CLOSURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080064 | 2008-06-23 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 930 | 2008-05-20 | 2008 | LAKE WALES | POLK | FL | 33853 | MP 10.3 | 536+30 | 27.8977808944 | -81.6543862889 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72100 | 40283.936 | 89451.4238 | 100 | 37.3638 | 72000 | 89414.06 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 871567 | 2008-05-20 | 690 | 915 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 8.62 | 0.19 | 5L | 35000 | SMLS |  | REPUBLIC | 1959 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1959 | NO | [57 empty] | DISCOVERED LEAK WHILE INVESTIGATING ILI TOOL RUN CORROSION ANOMALY. PIPELINE HAD LOCALIZED CORROSION PITTING. PIPELINE REPAIR EXCEEDED $50,000 THRESHOLD, BECAUSE STOPPLE BYPASS WAS USED DURING PIPE REPAIR/REPLACEMENT ACTIVITIES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080065 | 2008-06-24 14:54 | ORIGINAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1524 | 2008-05-25 | 2008 | MADISON | MADISON | IL | 62060 |  | LINE A102 4+77 | +38.68609 | -90.17076 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | LIGHTNING STRIKE AND FIRE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6877 | 3242.0179 | 4479.6028 | 4677 | 1747.5065 | 2200 | 2732.0963 | 0 | 0 | YES | YES | NO | NO | 0 |  | 2 | 47 | 872049 | 2008-05-25 | 181 | 200 | YES | NO | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | OTHER | ALUMINUM & RUBBER | NO | NO | NO | REGULATOR/METERING |  | 1990 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | NATURAL | [35 empty] | DURING A STORM, A TRANSFORMER STATION AT THE MAGENSIUM ELEKTRON PLANT WHICH WAS ABOUT 100 YARDS FROM OUR METER STATION ,OFF OF LINE A-102, WAS STRUCK BY LIGHTNING CAUSING THE SECONDARY SIDE OF THE TRANSFORMER STATION TO EXPLODE. APPARENTLY THE SPARKS OR DEBRIS FELL OR WAS BLOWN INSIDE THE METER BUILDING AND LANDED ON THE PRESSURE CONTROLLER FOR THE REGULATOR. THIS RESULTED IN A FIRE FROM LEAKAGE AROUND THE DOOR OF THE CONTROLLER. AS A RESULT OF THE HEAT FROM THE FIRE, THE BOURDON TUBE IN THE PRESSURE CONTROLLER WAS DAMAGED CAUSING THE REGULATOR TO OPEN UP AND THEN THE RELIEF VALVE STARTED BLOWING. THE FIRE WAS CONTAINED TO THE CONTROLLER AND A LITTLE SURFACE DAMAGE TO THE ACTUATOR OF THE REGULATOR. WHILE THIS EVENT DID NOT MEET THE CRITERIA OF AN INCIDENT IN §191.3,PARAGRAPHS (1) OR (2), IT WAS DEEMED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR BECAUSE OF THE FIRE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080066 | 2008-07-03 10:10 | ORIGINAL FINAL | 20044 |  | PRAXAIR, INC | 39 OLD RIDGEBURY RD | DANBURY | FAIRFIELD | CT | 06810 | 2240 | 2008-06-21 | 2008 | TEXAS CITY | GALVESTON | TX | 77590 | VALERO LET-DOWN |  | 29.3684 | -94.9149 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 25 | 874904 | 2008-06-22 |  |  | NO | NO | NO | NO | NO | NO | JAMES R. RYAN | 8154675412 | JIM_R_RYAN@PRAXAIR.COM | TRANSMISSION |  |  |  |  | NO | NO | NO | REGULATOR/METERING | [10 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | VALERO REFINERY, TEXAS CITY CALLED AT ~22:40 TO REPORT A HYDROGEN LEAK FROM PRAXAIR'S SYSTEM IN THE VICINITY OF THEIR ADMIN. BUILDING. FOLLOW-UP COMMUNICATIONS INDICATED THE LEAK INVOLVED A FIRE AS WELL, WHICH SEEMED TO CONFIRM THE POTENTIAL FOR A REAL HYDROGEN LEAK. VALERO REFINERY CONTACTED LOCAL EMERGENCY RESPONDERS (TEXAS CITY PD AND FD) WHO CAME TO THE SITE. FIVE OF PRAXAIR'S PERSONNEL WERE DISPATCHED TO THE SITE, INCLUDING THE PIPELINE MANAGER AND PIPELINE SUPERINTENDENT WHO WAS FIRST ON THE SCENE). THE PRAXAIR PERSONNEL DID NOT SEE ANY FIRE, BUT COULD HEAR LEAKING GAS FROM THE VICINITY OF THE HIGH-PRESSURE H2 METER STATION/LETDOWN STATION (THERE ARE ALSO N2 AND O2 PIPELINES IN THE VICINITY AS WELL AS AN O2 METER STATION). NEITHER THE HIGH-PRESSURE H2 METER STATION, NOR THE LETDOWN STATION WERE IN ACTIVE USE AT THE TIME (IN FACT, THE METER STATION WAS ISOLATED DOWNSTREAM AT THE PSA INSIDE THE VALERO REFINERY). THE EMERGENCY RESPONDERS BLOCKED OFF LOOP 197 IN FRONT OF THE REFINERY AND MADE PREPARATIONS TO PUT WATER ON THE STATION IN CASE OF AN ENERGY RELEASE AS INSTRUCTED BY PX PERSONNEL. AT 00:30, ALL PX PERSONNEL WERE ON-SITE. THE TEXAS CITY FD WAS PUTTING WATER ON THE STATION. A PLAN WAS FORMULATED TO SEND TWO 2-MAN TEAMS TO INVESTIGATE AND ISOLATE THE LEAK. MULTI-USE ANALYZERS AND RAGS FASTENED TO THE END OF PROBING BARS WOULD BE USED TO INDENTIFY THE PRESENCE OF A LEAK AND/OR BURNING H2. THE TEAMS WOULD UNLOCK, OPEN, AND ENTER THROUGH DIFFERENT GATES. PRIOR TO ENTRY, 110V POWER WAS ISOLATED FROM THE STATION. THE PLAN WAS COMMUNICATED TO PRAXAIR OPERATIONS MANAGEMENT, THE PIPELINE CONTROL CENTER, AND PERSONNEL ON-SITE. HWP WAS ISSUED. UPON ENTERING THE GATE, THE TEAM ENTERING THE NORTH GATE NOTED THAT THE LEAK WAS COMING FROM A KUNKLE PRV ON THE INSTRUMENT (N2) GAS PANEL. THE PRV WAS MANUALLY CLOSED AND THE STATION WAS SNIFFED FOR ANY H2 LEAKS. NONE WERE FOUND. 110V POWER WAS RESTORED TO THE STATION. THE FINDINGS WERE COMMUNICATED TO THE VALERO REFINERY AND THE EMERGENCY RESPONDERS, AND THE EMERGENCY WAS CLOSED AT 01:05. INVESTIGATION INTO THE CAUSE OF THE LIFTING OF THE PRV IS ONGOING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080067 | 2008-07-08 09:18 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 915 | 2008-06-12 | 2008 | PINE BLUFF | JEFFERSON | AR | 71601 |  | 12+44 AM-145 | +34.233891 | -92.060258 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | PINHOLE LEAK CAUSED BY TORCH BURN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14497 | 8038.4717 | 17571.7655 | 497 | 185.6983 | 14000 | 17386.0672 | 0 | 0 | YES | YES | NO | NO | 0 |  | 2 | 0 | 873900 | 2008-06-12 | 259 | 400 | NO | YES | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 16 | 0.25 | B | 35000 | ERW |  | UNKNOWN | 1957 | OTHER | PIPE IN EDGE OF CASING | 1 | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | OTHER | NO FORMAL PROCEDURE | 0 | 0 | Y | 2 |  |  | IN PINE BLUFF, JEFFERSON COUNTY ARKANSAS, AT THE SE CORNER OF HWY 65B AND N. HUTCHINSON STREET (LAT. N34.233891, LON. W092.060258) CEGT PERSONNEL, WITH THE ASSISTANCE OF A CONTRACTOR (SOUTHERN PIPELINE CONSTRUCTION), WERE REMOVING PIPELINE CASING FROM CEGT AM-145 HWY 65B ROAD CROSSING. A PRE-JOB SAFETY MEETING WAS HELD PRIOR TO WORK BEGINNING. LATER WHILE REMOVING CASING FROM THE PIPELINE, THE CONTRACT TORCH OPERATOR LOST HIS CUT, AFTER REHEATING HE BEGAN HIS CUT AGAIN AND THE INITIAL BLAST DEFLECTED THROUGH THE CASING AND BURNED A PINHOLE IN THE PIPELINE. LEAKING GAS IGNITED AND THERE WAS A SMALL FLAME APPROX 1.5 TO 2 FEET HIGH THAT WAS EXTINGUISHED IMMEDIATELY BY THE FIRE WATCH PERSONNEL. THE LEAK WAS MONITORED WITH GAS DETECTION INSTRUMENTS ABOVE GROUND UNTIL TEMPORARY LEAK CLAMP WAS INSTALLED. THIS CASING LOCATION WAS 51 FEET FROM A STREET ACCESS TO EDGE OF HUTCHINSON STREET AND 61 FEET TO THE MAIN LANES OF HWY 65B. EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF AN INCIDENT IN §191.3, PARAGRAPHS (1) OR (2), IT WAS DEEMED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR AND THUS REPORTED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080068 | 2008-07-14 18:03 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1500 | 2008-06-13 | 2008 | BUTLER | CUSTER | OK | 73625 |  | LINE AD-WEST 4515+50 | +35.672300 | -99.271200 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | EQUIPMENT FAILURE RESULTED IN RELEASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208250 | 89638.636 | 78027.2411 | 208000 | 77716.7756 | 250 | 310.4655 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 874424 | 2008-06-17 | 900 | 1000 | YES | NO | NO | NO | NO | NO | JOHNNY L. CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1991 | [5 empty] | VERSA VALVE |  | 1991 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | THIS INCIDENT TOOK PLACE AT CEGT RED MOON COMPRESSOR STATION ON LINE AD-WEST. THE COMPRESSOR STATION IN NOT ACTIVE BUT GAS FLOWS THROUGH THE MANIFOLD TO A DELIVERY METER TO NORTHERN NATURAL GAS. CEGT FIELD PERSONNEL HAD BEEN ON SITE THE DAY OF JUNE 12TH TO REPAIR LEAKING ¿O¿ RING ON FILTER SEPARATOR. THE FIELD PERSONNEL RETURNED ON THE MORNING OF JUNE 13TH TO PERFORM OTHER DUTIES AND FOUND DISCHARGE VALVE SYSTEM HAD BEEN ACTIVATED AND BLOWING. FIELD PERSONNEL CHECKED SYSTEM FOR LEAKS AND FOUND TUBING WITH SMALL HOLE, THAT MOST LIKELY ACTIVATED SYSTEM. ALSO FOUND THE VERSA VALVE STICKING ON DISCHARGE VALVE WHICH DID NOT ALLOW SYSTEM TO RESET AND ALLOW FOR THE CONTINUING RELEASE TO HAVE TAKEN PLACE
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080069 | 2008-07-15 11:14 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 848 | 2008-06-10 | 2008 | HOUMA | TERREBONNE | LA |  | 5.868 |  | 29 11.158' | 91 10.428' | OFFSHORE |  | SHIP SHOAL | 7 | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575000 | 311721.9894 | 648953.8481 | 75000 | 28022.8758 | 500000 | 620930.9723 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 42 | 873650 | 2008-06-10 | 755 | 1168 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 16 | 0.31 | API 5LX | 52000 | ERW |  |  | 1959 | UNDER WATER |  | 38 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1959 | NO | [57 empty] | BUBBLES WERE DISCOVERED ON 6-10-08 BY A PATROLLING HELICOPTER. IT WAS LATER DETERMINED TO BE THE 16 INCH FROM SHIP SHOAL 28-C TO MOSQUITO BAY. THE PIPELINE WAS ISOLATED & BLOWN DOWN. DIVERS CLEANED OFF THE CONCRETE COATING, TOOK UT READINGS AT THE PINHOLE LEAK SITE AND INSTALLED A HIGH PRESSURE CLAMP. PIPELINE WAS PRESSURED UP AND A PIPELINE PATROL WAS PERFORMED BY HELICOPTER TO ENSURE NO FURTHER LEAKS WERE DETECTED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080070 | 2008-07-25 09:42 | SUPPLEMENTAL FINAL | 31591 |  | STONE ENERGY | 625 EAST KALISTE SALOOM RD | LAFAYETTE | CAMERON | LA | 70508 | 1600 | 2008-06-30 | 2008 | CAMERON | CAMERON | LA | 70631 | 21 |  | 29.42.11 | 93.36.89 | OFFSHORE |  | WEST CAMERON | 45 | LA | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 875860 | 2008-06-30 | 125 | 281 | NO | NO | NO | NO | NO | NO | COBB LEBOUEF | 3375210213 | LEBOUEFCJ@STONEENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.5 | UNKNOWN |  | WELDED | N/A | UNKNOWN | 1957 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | IMPROPER CATHODIC PROTECTION |  | YES | 1957 | NO | [57 empty] | ON JUNE 30, 2008 WE RECEIVED A REPORT FROM MINERALS MANAGEMENT SERVICE OUT OF LAKE CHARLES LOUISIANA. MMS REPORTED THAT DURING A FLY BY OF THE WEST CAMERON FIELD NEAR THE WC45 PLATFORM, AN OIL SHEEN WAS REPORTED TO BE FLOATING IN THE FIELD AND BUBBLES COMING UP TO THE SURFACE FROM WHAT APPEARED TO BE A LEAKING PIPELINE. STONE ENERGY CORPORATION TOOK IMMEDIATE ACTION TO HAVE THE ONLY PIPELINE IN THE AREA AT WC45 SHUT IN, AND WE ACTIVATED THE EMERGENCY RESPONSE TEAM. WE CONDUCTED AN IMMEDIATE FLY BY FROM THE WC45 FACILITY TO THE BEACH FACILITY AT JOHNSON BAYOU. STONE ENERGY CORPORATION WAS TRANSPORTING HYDROCARBONS TO THE BEACH IN A 16¿ PIPELINE WHICH IS REGISTERED AS A DOT LINE. STONE ENERGY CORPORATION DISPATCHED A JACK- UP BOAT, DIVE BOAT WITH DIVERS, AND SENT A FIELD BOAT INTO THE AREA TO WARN MARINERS OF THE POSSIBLE HAZARD. AT THIS TIME IT WAS STILL UNDETERMINED THAT THE LEAK WAS COMING FROM OUR PIPELINE, ACTIVATION OF A SKIMMER UNIT TO ENSURE THAT NO HYDROCARBONS WOULD REACH THE BEACH IF THE LEAK BECAME WORST. WHEN ARRIVING ON LOCATION WE JUMPED THE DIVERS AND THEY LOCATED A SMALL CRACK IN THE PROTECTIVE CONCRETE COVERING ON THE PIPELINE, THEY COULD NOT FIND THE LEAK WITH OUT REMOVING THE COVERING. DIVERS MECHANICALLY REMOVED THE COVERING AND LOCATED A SMALL PINHOLE LOCATED AT THE 6 O CLOCK POSITION. AREA WAS PREPARED FOR A SPLIT CLAMP REPAIR KIT AND DIVERS INSTALLED IT ON THE PIPELINE AND SEALED THE LEAKING AREA. STONE ENERGY CORPORATION HAS CHOSEN TO REMOVE THE 16¿ PIPELINE FROM SERVICE, THE LINE HAS BEEN FLUSHED AND PICKLED AND IS PREPARED FOR REMOVAL AT THE BEACH AREA. AT THIS TIME WE HAVE NO FURTHER INFORMATION ON THE DOT LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080071 | 2008-07-28 12:34 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 2330 | 2008-07-18 | 2008 | BEATRICE | GAGE | NE | 68130 | APPRO 50.67 |  | 40.1768624 | -96.7798602 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FAILURE OF A DRESSER COUPLING DO TO SUBSIDENCE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 818910 | 402142.3646 | 642004.7565 | 431880 | 161366.9281 | 380500 | 472528.4699 | 6530 | 8109.3585 | NO | NO | NO | NO | 0 |  | 2 |  | 877682 | 2008-07-18 | 490 | 500 | NO | NO | NO | YES | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | OTHER | DRESSER COUPLING | STEEL |  | NO | NO | NO | PIPELINE |  | 1931 | 24 | 0.31 | DSA 5L | 30000 |  |  | A. O. SMITH |  | UNDER WATER |  | 72 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | SUBSIDENCE | [51 empty] | ON JULY 18, 2008, AT APPROXIMATELY 1 A.M., A PRESSURE DROP ON THE BEATRICE A LINE (NEM40101) MAINLINE WAS NOTED BY NORTHERN'S GAS CONTROL DEPARTMENT. PRESSURE ON THE LINE HAD BEEN CONSISTENTLY OPERATING IN THE 490 PSIG PRESSURE RANGE. THIS PIPELINE IS A DRESSER COUPLED PIPELINE. THE BEATRICE AREA HAD BEEN SUBJECT TO VERY HEAVY RAIN AND THUNDERSTORMS AND WARNINGS OF POTENTIAL FLASH FLOODING ON RIVERS AND WATERWAYS. AN ALL-CALL WAS ISSUED TO THE BEATRICE REGION TEAMS. BASED ON THE PRESSURE DROP STEPS WERE TAKEN TO IMMEDIATELY IDENTIFY TOWNS THAT COULD BE ADVERSELY IMPACTED AND THEY WERE SWITCHED OVER TO OTHER GAS SOURCE SERVICES. ONCE THIS WAS COMPLETED STEPS WERE TAKEN TO ISOLATE AN APPROXIMATE 13 MILES OF THIS LINE BY CLOSING BLOCK A BLOCK VALVES ON THE LINE AT THE BEATRICE COMPRESSOR PLANT AND BLOCK VALVE # 6 ON THE MAINLINE. FIVE SMALL VOLUME CUSTOMERS WERE IDENTIFIED AND NOTIFIED. FOUR WERE DOMESTIC USE FARM TAPS AND ONE WAS AN IRRIGATION SETTING. AS THERE WAS NO OUTSIDE NOTIFICATION OF A POTENTIAL DAMAGE SITE APPROPRIATE STEPS WERE TAKEN FOR TWO PEOPLE TEAMS TO VISUALLY CHECK THE 13 MILE SEGMENT OF PIPE FOR POTENTIAL SIGNS OF BLOWING GAS AND/OR DAMAGE.IT WAS FOUND THAT A JOINT OF PIPE APPROXIMATELY 25 FEET LONG, IN A WATERWAY, HAD BLOWN OUT OF THE GROUND. THIS SITE IS LOCATED APPROXIMATELY 500 FEET NORTH OF MILEPOST 50.67 IN SECTION 32, TOWNSHIP 3N, RANGE 6E, ALL IN GAGE COUNTY NEBRASKA. THE NATIONAL RESPONSE CENTER AND PHMSA CENTRAL REGION WAS NOTIFIED. THERE WAS NO FIRE, NO INJURIES AND NO LOSS OF SERVICE TO ANY TOWNS. NORTHERN IS CURRENTLY TAKING APPROPRIATE ACTIONS TO MAKE REPAIRS TO THE LINE. THIS EVENT WAS REPORTED TO THE NRC AND PHMSA AND A 7100 REPORT IS BEING FILED AS THE COST OF THE FAILURE, INCLUDING GAS LOSS WILL EXCEED THE $50,000 REPORTING THRESHOLD LEVEL. A FINAL CAUSE FOR THE FAILURE IS UNDER INVESTIGATION, HOWEVER IT IS CURRENT BELIEVED THAT THE HEAVY RAINS AND FLOODING OF THE WATERWAY RESULTED IN EROSION OF SUPPORTING DIRT AROUND THE PIPELINES DRESSER COUPLING WHICH RESULTED IN ADDITIONAL FORCE OF WATER FLOW ON THE DRESSER COUPLINGS WHICH ULTIMATELY LEAD TO THE FAILURE OF A DRESSER COUPLING. APPROPRIATE SUPPLEMENTAL INFORMATION SUCH AS TOTAL COST OF REPAIRS AND MATERIALS REQUIRED TO EFFECT REPAIRS WILL BE REPORTED. SUPPLEMENTAL/FINAL REPORT: AN INVESTIGATION INTO THE CAUSE OF THE FAILURE DETERMINED THAT THE CAUSE WAS HEAVY LOCALIZED RAIN FALL WASH OUT THE DIRT ON THE BANKS AROUND DRESSER COUPLING WHICH ALLOWED THE WATER FORCE TO SEPARATE THE PIPE FROM A DRESSER COUPLING. APPROXIMATELY 269 FEET OF NEW 24 INCH TESTED PIPE WAS INSTALLED TO COMPLETE THE REPAIR PROCESS. AN UPDATED ESTIMATE OF TOTAL COST HAS BEEN ENTERED ON THIS FINAL REPORT. THIS EVENT IS CONSIDERED COMPLETE AND CLOSED WITH NO FURTHER ACTIONS PENDING OR PLANNED. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20080072 | 2008-07-29 09:55 | ORIGINAL FINAL | 12576 |  | MISSISSIPPI RIVER TRANSMISSION CORP | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 2332 | 2008-07-01 | 2008 | COLLEGE CITY | LAWRENCE | AR | 72476 |  | 82 A-316 M&R ST. | +36.132909 | -90.948495 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | OUTSIDE FORCE DAMAGE PARTED THE PIPE AT A WELD | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 155703 | 80501.3073 | 149340.0892 | 50703 | 18944.585 | 100000 | 124186.1945 | 5000 | 6209.3097 | NO | NO | NO | NO | 0 |  | 1 | 3 | 876016 | 2008-07-02 | 794 | 1440 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1992 | [8 empty] | INSIDE/UNDER BUILDING |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON TUESDAY 7/1/08 AT APPROXIMATELY 2345 HRS. A VEHICLE WENT OF THE ROAD AND RAN INTO MRT¿S INTERCONNECT WITH NOARK PIPELINE IN LAWRENCE COUNTY, ARKANSAS, CAUSING A SEPARATION OF PIPE AT A WELD, A RELEASE OF GAS, AND INJURY TO THE VEHICLE¿S OCCUPANT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080073 | 2008-07-29 10:54 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 400 | 2008-07-14 | 2008 |  |  | LA |  |  |  | 28* 58' 37 | 91* 57' 38 | OFFSHORE |  | SOUTH MARSH ISLAND | 10 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232500 | 127372.2322 | 271368.4301 | 20000 | 7472.7669 | 212500 | 263895.6632 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 877177 | 2008-07-14 |  | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12.75 | 0.38 | API 5L | 46000 | UNKNOWN |  |  | 1968 | UNDER WATER |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 12 | 27 | 1968 | WATER |  | 24 | 2661 | [12 empty] | AN APPROXIMATE 6 FOOT BUBBLE CIRCLE WAS SIGHTED BY A HELICOPTER PILOT IN THE SOUTH MARSH ISLAND BLOCK 10 AREA. UPON FURTHER INVESTIGATION, A PIN HOLE LEAK WAS DISCOVERED ON THE 12-INCH ANR LINE 747. THE LEAK WAS SUBSEQUENTLY REPAIRED USING A REPAIR CLAMP.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080074 | 2008-08-01 13:41 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1207 | 2008-07-21 | 2008 | FREEPORT | BRAZORIA | TX |  |  |  | 28^35.205 | 95^12.607 | OFFSHORE |  | GA | 394 |  | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 99830.5595 | 218325.8084 | 6000 | 2241.8301 | 174000 | 216083.9784 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 878006 | 2008-07-21 | 1250 | 1250 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12 | 0.31 | API5L | 52000 | SMLS |  |  |  | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL | OTHER | INTERNAL | YES | 1990 | NO | [57 empty] | AT THE TIME THIS LEAK WAS GOING TO BE FIXED A SECOND LEAK WAS FOUND. BOTH LEAKS WERE FIXED SIMULTANEOUSLY. NOTE TO PHMSA: THIS LINE IS EXPECTED TO BE ABANDONED SOON
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080076 | 2008-07-12 | ORIGINAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1500 | 2008-07-12 | 2008 | RED LION | WARREN | OH | 45036 | MP 784.40 | 41416+32 | 39.48322 | -84.22274 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55100 | 30145.9501 | 64042.064 | 5050 | 1886.8736 | 50 | 62.0931 | 50000 | 62093.0972 | NO | NO | NO | NO | 0 |  | 0 | 0 | 877236 | 2008-07-14 | 718 | 832 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF, PRINCIPAL ENGINEER | 7136275573 | DETESCHENDORF@SPECTRAENERGY.COM | TRANSMISSION | OTHER | SHORTED WIRE FOR SOLENOID | OTHER | WIRE | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | SOLENOID | [10 empty] | A WIRE TO THE SOLENOID FOR THE ESD SYSTEM SHORTED ACTIVATING THE ESD SYSTEM. WHEN THE ESD SYSTEM ACTIVATED, PIPELINE CONDENSATE WAS RELEASED TO THE ATMOSPHER. THE PIPELINE CONDENSATE CAME TO REST ON HOUSES, CARS, SWIMMING POOLS, AND GARDENS IN A NEARBY NEIGHBORHOOD. THE COST TO CLEAN HOUSES, CARS AND SWIMMING POOLS AND TO BUYS GARDENS EXCEEDED $50,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080077 | 2008-08-21 17:13 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1320 | 2008-07-11 | 2008 | JEFFERSON | MARION | TX | 75657 |  | AM-47 1058+05 | 32.815279 | -94.347571 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 55890.1495 | 124186.1945 | 0 | 0 | 0 | 0 | 100000 | 124186.1945 | NO | NO | NO | NO | 0 |  |  | 0 | 00000 | 2008-07-11 | 325 | 500 | NO | NO | YES | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | BY-PASS VALVES | 1953 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 3 |  |  | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1) OR (2), BECAUSE THERE WAS NO RELEASE OF GAS. WE ALSO DO NOT HAVE A NRC TELEPHONE REPORT # . WHEN OUR SYSTEM CONTROLLER NOTIFIED THE PERSON ON DUTY, THE NRC PERSON SAID THAT UNLESS THERE WAS A RELEASE OF HAZARDOUS MATERIAL, REPORTING ON THIS INCIDENT TO PHMSA WAS NOT NECESSARY. ON JULY 11, FIELD PERSONNEL NOTIFIED SYSTEM CONTROL THAT THE LOCAL DISTRIBUTION COMPANY HAD INFORMED THEM THE TOWNS OF JEFFERSON AND LINDEN TEXAS HAD LOST PRESSURE. INVESTIGATION OF THE PROBLEM FOUND THAT THE BY-PASS VALVES OFF OF LINE AM-47 WERE CLOSED. THE VALVES WERE OPEN AND GAS PRESSURE RESTORED TO THE DISTRIBUTION COMPANY. APPROXIMATELY 1800-2000 CUSTOMERS LOST SERVICE RESULTING IN AN APPROXIMATE RE-LIGHT COST OF $100,000. FURTHER INVESTIGATION DISCOVERED THAT ON JULY 10, AFTER PERFORMING THE ANNUAL VALVE MAINTENANCE AND INSPECTION ON CEGT LINE AM-47, THE FIELD PERSONNEL INADVERTENTLY LEFT THE BY-PAS VALVES SHUT THAT FEED THE TOWN BORDERS JEFFERSON AND LINDEN TX. THE IDENTIFIED PERSON HAD THEIR OQ QUALIFICATION FOR THE COVER TASK ASSOCIATED WITH VALVE INSPECTION AND MAINTENANCE SUSPENDED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080078 | 2008-08-28 17:47 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1057 | 2008-08-28 | 2008 | NEWARK | INDEPENDENCE | AR | 72562 |  | JM-7 893+97 | +35.712618 | -91.444233 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23000 | 12854.7344 | 28562.8247 | 0 | 0 | 23000 | 28562.8247 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 878972 | 2008-07-30 | 0 | 720 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2003 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1) OR (2), BECAUSE THERE WAS NO RELEASE OF GAS. REGULATOR FAILED DUE TO THE PILOT CONTROL LINE BEING BLOCKED BECAUSE OF DEBRIS. THIS REGULATOR FAILURE RESULTED IN THE OUTAGE OF 324 CUSTOMERS.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20080079 | 2008-08-31 18:12 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1600 | 2008-08-02 | 2008 | FLORENCE | SIMPSON | MS | 39073 |  |  | 32.02835 | -90.146542 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  |  | 5 | 879372 | 2008-08-03 |  |  | NO | NO | NO | NO | NO | NO | JACK L. ADAMS | 7134798099 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2008 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 9 |  |  | SMALL AMOUNT OF GAS WAS EXCAPING FROM THE UNIT VENT LINE THAT VENTED TO THE ATMOSPHERE AT A LOCATION APPROXIMATELY 14 FEET FROM ELECTRICAL BOX. EMPLOYEE IMMEDIATELY SHUTDOWN ALL ENGINES AND EXTINGUISHED FIRE ON TOOL BAG. EMPLOYEE WAS CHECKED AT HOSPITAL EMERGENCY ROOM AND MINOR BURNS WERE TREATED AND EMPLOYEE STAYED OVERNIGHT IN HOSPITAL FOR OBSERVATION
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080080 | 2008-09-08 14:29 | SUPPLEMENTAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HWY 56 | OWENSBORO | DAVIESS | KY | 42301 | 330 | 2008-08-15 | 2008 | WELDA | ANDERSON | KS | 66091 |  | 100/21+22 | 38.143716497 | -95.3165079838 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374322 | 165823.3531 | 171985.3255 | 337322 | 126036.4336 | 35000 | 43465.1681 | 2000 | 2483.7239 | NO | NO | NO | YES | 5 | PRECAUTIONARY | 1 | 42 | 880688 | 2008-08-15 | 405 | 500 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 10 | 0.19 | API 5L | 35000 | HIGH FREQUENCY ERW | NA | REPUBLIC STEEL | 1978 | UNDER GROUND |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | OTHER | CARBONIC ACID (CO2) | YES | 1978 | NO | [57 empty] | AT 2:33 AM ON 8/15/08, FREDDY PARTIDA (MANAGER OF SOUTHERN STAR¿S WELDA DISTRICT) WAS NOTIFIED OF BLOWING GAS BY THE ANDERSON COUNTY KANSAS SHERIFF¿S OFFICE NEAR LOUISIANA RD. EMERGENCY OFFICIAL EVACUATED 3 HOUSES. FREDDY ARRIVED ON THE SCENE AND CALLED GAS CONTROL AT 3:08 AM. AT 3:10 AM, GAS CONTROL SHUT GATES AT WELDA STATION TO ISOLATE S. WELDA STORAGE FIELD FROM THE REST OF SOUTHERN STARS SYSTEM. AT 4:15 AM, GATES WERE SHUT IN THE FIELD TO ISOLATE THIS SECTION OF THE LINE FROM THE REST OF THE FIELD AND THE LINE BLEW DOWN. THE CAUSE OF THE INCIDENT IS STILL UNDER INVESTIGATION ON 9/8/08 . THE FAILED SECTION OF PIPE HAS BEEN SENT TO A LAB FOR ANALYSIS. 3/23/09, IT WAS DETERMINED THAT THE PRIMARY CAUSE OF THE RUPTURE WAS DUE TO INTERNAL METAL LOSS RESULTING FROM CARBONIC ACID CORROSION. THE SOURCE OF THE CARBONIC ACID WAS THE DISSOLUTION OF CO2 CONTAINED IN THE GAS STREAM IN WATER THAT WAS ALSO PRESENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080081 | 2008-09-04 | SUPPLEMENTAL FINAL | 14210 |  | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY AVENUE | OKLAHOMA CITY | OKLAHOMA | OH | 73102-3470 | 1605 | 2008-08-07 | 2008 | ELK CITY | BECKHAM | OK | 73644 |  |  | 35.3831 | -95.4175 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210428 | 112768.8755 | 228653.0077 | 37628 | 14059.2636 | 172800 | 214593.744 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 40 | 879899 | 2008-08-07 | 375 | 500 | NO | NO | NO | YES | NO | NO | D.E. ELLIS - STAFF ENGINEER | 4055566458 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 6 | 0.16 | API 5L | 42000 | ERW | N/A | UNKNOWN | 1964 | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | PHONE/CABLE |  | YES | 8 | 4 | 2008 | ONE-CALL SYSTEM | NO | [40 empty] | EXCAVATOR, POWERS ENGINEERS STRUCK A 6-INCH STEEL TRANSMISSION LINE WHILE INSTALLING FIBER OPTIC CABLE USING A TRENCHING MACHINE. THE EXCAVATOR HAD A VALID LOCATE TICKET (LOCATE REQUEST FILED BY ROBINSON BROTHERS CONSTRUCTION, INC.) BUT THE LINE WAS NOT LOCATED DUE TO LINE LOCATION SUBCONTRACTOR ERROR, SM&P. TWO INDIVIDUALS AT THE SCENE RECEIVED MINOR INJURIES AT THE SITE. THEY WERE TRANSPORTED TO A MEDICAL FACILITY, TREATED, AND RELEASED. NATURAL GAS SERVICE WAS INTERRUPTED TO APPROXIMATELY 4,493 ACCOUNTS. FOLLOWING REPAIRS, SERVICE WAS RESTORED OVER THE FOLLOWING 24 HOURS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080082 | 2008-09-11 17:59 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1600 | 2008-08-26 | 2008 | LONGVIEW | HARRISON | TX | 75605 | N/A | N/A | 32.56N | 94.66W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RUPTURE - UNDER INVESTIGATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1068000 | 590475.8832 | 1282897.3769 | 50000 | 18681.9172 | 700000 | 869303.3613 | 318000 | 394912.0984 | NO | YES | NO | NO | 0 |  |  | 15 | 881901 | 2008-08-26 | 2650 | 3000 | NO | YES | NO | NO | NO | NO | KRISTIN VAN DER LAAN | 3039147753 | KRISTIN_VANDERLAAN@KINDERMORGAN.COM | TRANSMISSION | OTHER | UNDER INVESTIGATION | STEEL |  | NO | NO | NO | OTHER | PIPING | 1984 | 4 | 0.34 | API 5L/STM A106 | 35000 | SEAMLESS |  | UNKNOWN |  | UNDER GROUND |  | 144 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | NOT DETERMINABLE | YES | 1984 | NO | [57 empty] | AN UNDERGROUND LIQUID SLUG CATCHER THAT COLLECTED LIQUIDS FROM LATERALS Q AND R RUPTURED AND CAUGHT FIRE. VISUAL EXAMINATION OF THE PIPE REVEALED INTERNAL CORROSION ON THE HORIZONTAL SEGMENT 4.5-INCH OD PIPE BETWEEN THE LOWER FLOAT COLUMN VALVE AND THE 4-INCH SLUG CATCHER NOZZLE. THIS LOCATION APPEARS TO BE THE ORIGIN OF THE FAILURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080083 | 2008-09-12 13:52 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1100 | 2008-09-12 | 2008 | HAMDEN | VINTON | OH |  | VS-2182 |  | 39.1750362 | -82.5317937 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | THIRD PARTY DAMAGE BY LAND OWNER | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80008 | 34580.0563 | 30933.3203 | 78811 | 29446.8115 | 1197 | 1486.5087 | 0 | 0 | NO | NO | NO | NO | 0 | PRECAUTIONARY | 14 | 4 | 881243 | 2008-08-20 | 609 | 900 | NO | NO | YES | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | OTHER | 1 INCH TAP | STEEL |  | NO | NO | NO | OTHER | 1 INCH TAP | 1948 | 24 | [6 empty] | 1948 | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | LANDOWNER |  | NO |  |  |  |  | YES | STAKES | YES | ACCURATE | [37 empty] | THE 1" TAP WAS HIT BY LAND OWNER WHILE HE WAS USING HIS BRUSH HOG, AND DAMAGED THE OUT-OF-SERVICE TAP. THE LAND OWNER IMMEDIATELY SHUT-OFF HIS ENGINE AND CONTACTED EMERGENCY PERSONNEL AND COLUMBIA GAS TRANSMISSION THROUGH THE PHONE NUMBER LOCATED ON THE LINE MARKER AT THE OUT-OF-SERVICE TAP.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080084 | 2008-09-16 14:50 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1545 | 2008-08-16 | 2008 | WESTLAKE | CALCASIEU | LA | 70669 |  | 6+03 | 30.24961 | -93.27901 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 8 |  | 880841 | 2008-08-16 | 890 | 975 | YES | NO | NO | NO | NO | NO | JEFFREY B. MCMAINE | 2706886361 | JEFF.MCMAINE@BWPMLP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1969 | 16 | 0.31 | API 5LX |  | SEAMLESS |  | US STEEL | 1969 | UNDER GROUND |  | 96 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1969 | NO | [57 empty] | LEAK WAS UNDERGROUND INSIDE OF SASOL PLANT. SASOL NOTIFIED THE COMPANY. UPON ARRIVAL AT THE SITE A DETERMINATION WAS MADE THAT A SAFE EXCAVATION TO EXAMINE AND DETERMINE REPAIR REQUIREMENTS COULD NOT BE DONE AT THAT TIME. THEREFORE, THE PIPELINE WAS TAKEN OUT OF SERVICE. EXCAVATION PLANNING IS STILL BEING WORKED ON AND ONCE COMPLETED FINAL DISPOSITION WILL BE MADE. UPDATE: DECISION HAS NOT BEEN MADE YET TO EITHER ABANDON OR REPAIR. PIPELINE IS OUT OF SERVICE AT THIS TIME. UPDATE FOR FINAL: PIPELINE WILL NOT BE PUT BACK INTO SERVICE AND IS BEING ABANDONED. UPDATE 5/15/2013: UNCHECKED PART A, QUESTION 5.D TO REFLECT THAT THE INCIDENT DIDN'T OCCUR IN AN HCA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080085 | 2008-09-18 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1015 | 2008-08-04 | 2008 | LAKE WALES | POLK COUNTY | FL | 33853 | MP 14.89 | 787+66 | 27.84282 | -81.61422 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79988 | 44679.6891 | 99160.4085 | 200 | 74.7277 | 79788 | 99085.6808 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 879622 | 2008-08-05 | 692 | 915 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 8.63 | 0.19 | 5L | 35000 | SMLS |  | REPUBLIC | 1959 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1959 | NO | [57 empty] | DISCOVERED LEAK WHILE RUNNING LEAK SURVEY. PIPELINE HAD LOCALIZED CORROSION PITTING. PIPELINE REPAIR EXCEEDED $50,000 THRESHOLD, BECAUSE SECTION REQUIRED A STOPPLE IN ORDER TO MAKE PIPE REPAIR/REPLACEMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080086 | 2008-09-23 13:22 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1000 | 2008-09-04 | 2008 | BANDERA | BANDERA | TX |  |  |  | 29.81181N | -99.192541W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 12 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240000 | 117415.9836 | 185177.7987 | 130000 | 48572.9847 | 110000 | 136604.8139 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 882593 | 2007-09-03 | 634 | 899 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7133812494 | JMCDONALD@EPCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 30 | 0.31 |  | 60 | ERW |  |  |  | UNDER GROUND |  | 37 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | AT APPROXIMATELY 10 AM ON SEPTEMBER 3, 2008 A 30" PIPELINE OPERATED BY ENTERPRISE PRODUCTS OPERATING LLC IN BANDERA COUNTY TEXAS WAS STRUCK AND PUNCTURED BY A THIRD PARTY EXCAVATOR PERFORMING WORK FOR A LANDOWNER ON PRIVATE PROPERTY. THE EXCAVATOR, TEXAS RANCH LAND ENHANCEMENT SERVICES OF LEANDER, TEXAS FAILED TO MAKE THE REQUIRED ONE CALL AND THIS INFORMATION HAS BEEN REPORTED TO THE STATE OF TEXAS. MR. ALAN VINCIK IS THEIR REPRESENTATIVE AND CAN BE REACHED AT (512) 515-6623. THE NEAREST PERMANENT MARKER ON THE PIPELINE WAS LOCATED WITHIN 30 YARDS OF WHERE THE LINE WAS HIT. THE EQUIPMENT OPERATOR NOTED THAT HE SAW THE MARKER BUT THOUGHT THE LINE WENT A DIFFERENT DIRECTION. THE PIPELINE WAS SHUT IN, ISOLATED GAS VOLUME WAS EVACUATED FROM THE PIPELINE. APPROXIMATE A 40 FOOT PIECE OF REPLACEMENT PIPE WAS INSTALLED. THE LINE WAS PLACED BACK INTO SERVICE ON SEPTEMBER 5, 2008.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080087 | 2008-09-24 16:30 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1100 | 2008-09-04 | 2008 | GRAND ISLE | JEFFERSON | LA | 70358 | LINE 523A-100 |  | 28 35 83 | 90 28 87 | OFFSHORE |  | BAY MAR | 3 | LA | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7160000 | 3723919.2401 | 7016368.5468 | 2160000 | 807058.8235 | 5000000 | 6209309.7233 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 882711 | 2008-09-04 | 900 | 1130 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 6.63 | 0.5 | API 5L | 46000 | UNKNOWN |  | NATIONAL PIPE | 1959 | UNDER WATER |  | 0 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE GUSTAV | [51 empty] | PIPELINE WAS SEVERED DURING WIND AND WAVE ACTION RELATED TO HURRICANE GUSTAV. UPON DETECTION OF INCIDENT, THE APPROPRIATE ISOLATION VALVE WAS CLOSED. THE PRODUCER THAT HAD INPUT INTO THIS LINE HAS REROUTED HIS GAS AND THE TGP 523A-100 PIPELINE IS PLANNED FOR ABANDONMENT.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080088 | 2008-09-30 09:23 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1830 | 2008-09-14 | 2008 | HOUMA |  |  |  | 29.83 |  | 29^00'56 | 91^34'02.943 | OFFSHORE |  | EUGENE ISLAND | 107 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3400000 | 1848817.775 | 3875041.1716 | 400000 | 149455.3377 | 3000000 | 3725585.834 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 883843 | 2008-09-14 | 1168 | 1393 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 24 | 0.5 | AP5L | 60000 | SEAMLESS |  | UNITED STATES STEEL CORPORATION | 1967 | UNDER WATER |  | 480 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE | [51 empty] | WHILE PERFORMING POST HURRICANE IKE DAMAGE ASSESSMENTS, A DRILLING RIG OR A PORTION OF A DRILLING RIG, THE PRIDE WYOMING, WAS SIGHTED OVER THE 24" PIPELINE (MMS SEGMENT 13447) IN EUGENE ISLAND 107 AREA. THERE WERE OBSERVATIONS OF A 30 FOOT DIAMETER CIRCLE OF SURFACE BUBBLES IN THE EI 107 AREA AROUND THE DRILLING RIG AND WGP-TRANSCO 24" SUB-SEA PIPELINE, ALONG WITH A LOSS OF PRESSURE (INDICATIVE OF A SEVERE LEAK OR RUPTURE). THE LINE WAS ISOLATED WITH VALVES LOCKED AND TAGGED OUT. THE RIG REMAINS OVER THE PIPELINE AT THIS TIME PENDING REPAIRS.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080089 | 2008-09-30 09:37 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1400 | 2008-09-14 | 2008 | HOUMA | TERREBONNE | LA | 70360 | 11.56 |  |  |  | OFFSHORE |  | SHIP SHOAL | 208F | LA | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8911000 | 4978956.4216 | 11056681.3292 | 11000 | 4110.0218 | 8900000 | 11052571.3074 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 883810 | 2008-09-14 | 750 | 1440 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 10 | 0.5 | API 5L | 42000 | SEAMLESS |  | US STEEL | 1968 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE | [51 empty] | PRODUCER, CHEVRON, REPORTED SS208F FACILITY TOPPLED DURING HURRICANE IKE. REPORT CONFIRMED DURING COMPANY'S POST HURRICANE IKE DAMAGE ASSESSMENT. THE BOARDING AND DEPARTING 10" RISERS, PLATFORM PIPING, METERING FACILITIES AND CONTROLS WERE DAMAGED WITH THE PLATFORM'S FAILURE. THE BOARDING AND DEPARTING PIPELINES WERE DEPRESSURED DURING THE EVENT. THE LINE HAS BEEN ISOLATED, WITH ALL VALVES LOCKED AND TAGGED. IT IS UNKNOWN AT THIS TIME IF THE PLATFORM FAILED OR WAS STRUCK DURING THE STORM. CORROSION SPECIALIST INSPECTED A PORTION OF THE 10" PIPE AFTER IT WAS RECOVERED; HE REPORTED BOTH INTERNAL AND EXTERNAL OF THE PIPE AND COATING WERE IN EXCELLENT SHAPE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080090 | 2008-10-01 14:17 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 744 | 2008-09-14 | 2008 | APPOMATTOX | APPOMATTOX | VA | 24522 | 1459.73 |  | 37.38013 | 78.85024 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 30 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5416000 | 3014148.6702 | 6639101.9322 | 100000 | 37363.8344 | 1000000 | 1241861.9447 | 4316000 | 5359876.1531 | NO | NO | YES | YES | 50 | THREAT TO THE PUBLIC | 2 | 1 | 883754 | 2008-09-14 | 792 | 800 | YES | NO | NO | NO | NO | NO | CHRIS MASON | 7132152750 | CHRIS.MASON@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1955 | 30 | 0.34 | API 5LX | 52000 | DSAW |  | NATIONAL TUBE | 1955 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | IMPROPER CATHODIC PROTECTION |  | YES | 1955 | NO | [57 empty] | AT 7:44 AM EDT ON SUNDAY SEPTEMBER 14, 2008 WILLIAMS GAS PIPELINE'S 30-INCH LINE B RUPTURED AT MP 1459.73 ON THE UPSTREAM SIDE OF VA HIGHWAY 26 IN APPOMATTOX COUNTY,VA. A VERY SHORT TIME AFTER THE RUPTURE, A 32-FOOT SECTION OF PIPE WAS BLOWN FROM THE PIPELINE. WITHIN ANOTHER MINUTE OR TWO, THE ESCAPING GAS IGNITED AND BURNED UNTIL APPROXIMATELY 9:45 AM EDT. STRESS ENGINEERING SERVICES, INC. HAS CONCLUDED THAT THE FAILURE OF TRANSCO¿S 30-INCH B-LINE AT MP 1459.7 ON SEPTEMBER 14, 2008 WAS CAUSED BY EXTERNAL CORROSION WHICH EVENTUALLY LED TO OVERLOADING OF THE PIPE AT THE OPERATING PRESSURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080091 | 2008-10-03 15:06 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1314 | 2008-09-14 | 2008 | CAMERON | CAMERON | LA | 70631 | VALVE 1342-2 | 5253+42.8 | 29 47 39.37 | -93 44 54.09 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CONTROL TUBING DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74139 | 31907.1989 | 27744.5844 | 74089 | 27682.4913 | 50 | 62.0931 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 883804 | 2008-09-14 | 750 | 1100 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | CONTROL TUBING | STEEL |  | NO | NO | NO | COMPRESSOR |  |  | 1 | 0.22 | [6 empty] | ABOVE GROUND |  | 0 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE ACTION | [51 empty] | HURRICANE IKE DAMAGED CONTROL TUBING WITHIN COMPRESSOR STATION AND TUBING LEAKED UNTIL WORKERS COULD ACCESS SITE TO ISOLATE TUBING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080092 | 2008-10-03 15:17 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1754 | 2008-09-14 | 2008 | CAMERON | CAMERON | LA | 70631 | VALVE XL105AE | 5665+88 | 29 49 04.84 | -93 37 16.08 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CONTROL TUBING FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4644 | 2004.6662 | 1778.5877 | 4594 | 1716.4946 | 50 | 62.0931 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 883841 | 2008-09-14 | 750 | 1100 | NO | YES | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | CONTROL TUBING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  |  | 1 | 0.22 | [6 empty] | ABOVE GROUND |  | 0 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE ACTION | [51 empty] | HURRICANE IKE CAUSED FLOODING AND FLOATING DEBRIS SEPARATED TUBING FROM CONTROLS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080093 | 2008-10-03 15:18 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 2351 | 2008-09-05 | 2008 | LAVACA | SEBASTIAN | AR | 72941 |  | LINE B-106 489+00 | +35.403410 | -94.101310 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50186 | 26738.9247 | 53480.358 | 10186 | 3805.8802 | 40000 | 49674.4778 | 0 | 0 | NO | NO | NO | YES | 2 | PRECAUTIONARY | 1 | 0 | 882915 | 2008-09-06 | 860 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO |  |  | 1960 | 10 | 0.19 | X-42 | 42000 | UNKNOWN | N/A | UNKNOWN | 1960 | UNDER GROUND |  | 40 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1968 | NO | [57 empty] | EXTERNAL CORROSION AT SITE OF COATING DAMAGE APPARENTLY FROM EXTREMELY ROCKY ENVIRONMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080094 | 2008-10-02 | SUPPLEMENTAL FINAL | 32099 |  | ENERGY TRANSFER COMPANY | 800 EAST SONTERRA BLVD. #400 | SAN ANTONIO | BEXAR | TX | 78258 | 740 | 2008-08-28 | 2008 | STAIRTOWN | CALDWELL | TX | 78661 | 153.69 | 8114.93 | N 29.739073 | W 97.71456 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 1800 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233865 | 581201.1545 | 800494.7034 | 842865 | 314926.683 | 379000 | 470665.677 | 12000 | 14902.3433 | NO | YES | NO | NO | 0 |  | 3 | 20 | 882063 | 2008-08-28 | 1041 | 1050 | NO | YES | NO | NO | NO | NO | DANNY NICHOLS, DIRECTOR OF REGULATORY COMPLIANCE | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 36 | 0.44 | API 5L | 6000 | DOUBLE SUBMERGED-ARC WELDED (DSAW) | N/A | STEEL COMPANY OF CANADA | 1969 | UNDER GROUND |  | 48 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | SHIELDING | YES | 1970 | NO | [57 empty] | ENERGY TRANSFER COMPANY EXPERIENCED A RUPTURE ON A SECTION OF 36" OASIS NATURAL GAS TRANSMISSION PIPELINE ON AUGUST 28. 2008. THE RELEASE OCCURRED IN A REMOTE (CLASS I) AREA RELEASING APPROXIMATELY 98.6 MMCF OF DRY NATURAL GAS. PRELIMINARY INVESTIGATIONS REVEALED EXTERNAL CORROSION, CAUSED BY SHIELDING. THE FAILED SECTION OF PIPE WILL BE SUBMITTED TO A THIRD PARTY METURLIGICAL LABORATORY. THE REMAINING SECTION OF PIPELINE WAS INSPECTED WITH A HIGH RESOLUTION MFL SMART TOOL. IDENTIFIED ANOMALIES, WITH A REDUCED WALL THICKNESS OF 50% OF GREATER, WERE REPAIRED PRIOR TO COMING BACK IN SERVICE, AT NORMAL OPERATING PRESSURE. THE OASIS PIPELINE WAS PLACED BACK INTO NORMAL SERVICE ON SEPTEMBER 8. 2008.TEXAS RAILROAD COMMISSION INCIDENT REPORT NUMBER ¿ 08-CA-695. METURLIGICAL REPORT RECEIVED FROM KIEFNER AND ASSOCIATES, INC. CONFIRMED THE PRELIMINARY DETERMINATION THAT THE INCIDENT RESULTED FROM EXTERNAL CORROSION, CAUSED BY SHIELDING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080095 | 2008-10-06 13:24 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 800 | 2008-09-06 | 2008 | BOONEVILLE | LOGAN | AR | 72927 |  | LINE O 721+56 | +35.189280 | -94.000213 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430000 | 188365.8615 | 183238.3016 | 404000 | 150949.8911 | 26000 | 32288.4106 | 0 | 0 | NO | NO | NO | YES | 1 | PRECAUTIONARY | 2 |  | 882930 | 2008-09-06 | 830 | 900 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1963 | 24 | 0.25 | API 5L X-60 | 60000 | DSAW |  | US STEEL (NATIONAL TUBE) | 1963 | UNDER GROUND |  | 35 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1964 | NO | [57 empty] | METALLURGICAL CONCLUSION ¿ ¿THE FAILURE WAS CAUSED BY OVERSTRESS OF AN AREA WITH SEVERELY REDUCED WALL THICKNESS. THE METAL LOSS WAS CAUSED BY EXTERNAL CORROSION. NO OTHER CAUSE WAS FOUND.¿ COPY OF REPORT SENT TO OPS.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080096 | 2008-10-07 09:09 | SUPPLEMENTAL FINAL | 30940 |  | WILLIAMS ENERGY, LLC | ONE WILLIAMS CENTER, MD WRC 3-4 | TULSA | TULSA | OK | 74172 | 304 | 2008-09-08 | 2008 | LAROSE | TERREBONNE | LA | 70373 |  |  | 28DEG 6. 100N | 90DEG 12.1000S | OFFSHORE |  | SOUTH TIMBALIER | 231 |  | YES | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36820000 | 20344667.7958 | 44145189.8493 | 1820000 | 680021.7865 | 35000000 | 43465168.0628 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 883525 | 2008-09-08 | 850 | 1850 | NO | YES | NO | NO | NO | NO | JOE FREISBERG | 9185730810 | JOE.F.FREISBERG@WILLIAMS.COM | GATHERING | OTHER | 18 | STEEL |  | NO | NO | NO | PIPELINE |  |  | 18 | 0.5 | API 5LX | 60 | DSAW | N/A | N/A | 1997 | UNDER WATER |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | CAUSE IS UNDER INVESTAGATION. APPEARS THAT AN OBJECT DURING HURRICANE IKE MAY HAVE CAUSED THE 18-INCH PIPELINE TO BE SEVERED NEAR THE 30-INCH TIE-IN. THE TIE-IN WAS LOCATED IN 220 FOOT OF WATER.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080097 | 2008-10-07 09:35 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1300 | 2008-09-14 | 2008 |  |  |  |  | 17.067 |  | 28^17'13 | 90^47'20 | OFFSHORE |  | SHIP SHOAL | 283 | LA | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2660000 | 1485391.7942 | 3294670.5368 | 10000 | 3736.3834 | 2650000 | 3290934.1533 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 885796 | 2008-09-22 | 750 | 2160 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | OTHER | FIELD WELD/FAB ASSEMBLY | STEEL |  | NO | NO | NO | OTHER | SUB SEA TIE IN ASSEMBLY | 2001 | 6.63 | 0.43 | API-5L | 35000 | SEAMLESS |  | NORTH STAR STEEL | 1995 | UNDER WATER |  | 0 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A WELD ON THE FABRICATED SUBSEA TIE IN ASSEMBLY WAS FOUND PULLED APART WITH A 1.5 TO 3" GAP AT THE 9 O'CLOCK POSITION. THE EVENT OCCURRED DURING HURRICANE IKE. THE FAILURE IS BELIEVED TO HAVE BEEN CAUSED BY OUTSIDE FORCE DAMAGE FROM CONTACT WITH A UNSECURED JACK UP RIG. THE SUB-SEA ASSEMBLY WAS REPLACED AND RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080098 | 2008-10-07 14:50 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1430 | 2008-09-07 | 2008 | [6 empty] | 28.56.1 | 88.58.7 | OFFSHORE |  | MISSISSIPPI CANYON | 21 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17957802 | 9994198.3566 | 22014597.1252 | 330000 | 123300.6536 | 17627802 | 21891296.4716 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 883062 | 2008-09-07 | 900 | 1500 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 20 | 0.5 | API 5L | 65000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | LANDSLIDE | [54 empty] | HURRICANE GUSTAV'S PATH CROSSED OVER THE ENTERPRISE PRODUCTS OPERATING LLC SUBSEA PIPELINE. THIS AREA IS KNOWN FOR MUDSLIDES DURING HURRICANES. SIDE SCAN SONAR DISCOVED DAMAGE TO THE 20" PIPELINE SEGMENT, NUMBER 16045. ONGOING EVALUTIONS WILL TAKE PLACE AS CONTRACTORS AND EQUIPMENT BECOME AVAILIABLE. THE ESTIMATED COST OF GAS LOSS AND DAMAGE TO FACILITIES MAY BE UPWARDS OF $10,000,000. PIPELINE ABANDONE
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20080099 | 2008-10-06 | ORIGINAL | 30792 |  | LAMAR OIL & GAS | 4305 BUSINESS HWY 35 SOUTH | ROCKPORT | ARANSAS | TX | 78382 | 1230 | 2008-09-14 | 2008 | ROCKPORT | ARANSAS | TX | 78381 | N/A | N/A | 28-07.721 | 97-00.137 | OFFSHORE |  | ARANSAS BAY | 84 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100 | 1655.4237 | 3328.8379 | 600 | 224.183 | 2500 | 3104.6549 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 |  |  | 50 | 900 | YES | NO | NO | NO | NO | NO | NEIL SULLIVAN | 3617273309 | NEIL.SULLIVAN@WOODGROUP.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6 | 0.25 | A105B |  | SEAMLESS | N/A |  |  | UNDER WATER |  | 35 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL |  | LOCALIZED PITTING |  | OTHER | BAD SPOT IN COATING | YES | 1990 | NO | [57 empty] | THE WELLS FEEDING THIS GATHERING SYSTEM WERE SHUT IN FOR HURRICANE IKE. WE PUT THE WELLS BACK ON LINE AT 12PM ON 9-14-08. THE SMALL LEAK WAS DISCOVERED AT 12:30 PM ON 9-14-08. THE WELLS WERE SHUT IN AND THE PIPELINE DEPRESSURIZED BY 1:30 PM. NOTIFICATION TO THE RAILROAD COMMISSION WAS MADE BY 12:45PM 9-14-08. WE PUT A DIVER IN THE WATER ON 9-15-08 AT 8 AM AND FOUND THE LEAK THERE WAS A BAD SPOT IN THE COATING CAUSING EXTERNAL CORROSION. THE COATING WAS REPAIRED AND A PLIDCO HIGH PRESSURE CLAMP WAS INSTALLED. WE TESTED THE PIPELINE TO 500PSI NORMAL OPERATING PSI IS 60 PSI. THE WELLS WERE PUT BACK ON LINE AT 3PM 9-15-08.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080100 | 2008-10-09 16:08 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1700 | 2008-09-14 | 2008 |  |  | LA |  | 0.00 |  | 28*25'25 | -91*57'57 | OFFSHORE |  | SOUTH MARSH ISLAND | 108 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248171 | 119645.6451 | 179548.5616 | 148171 | 55362.3671 | 100000 | 124186.1945 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 883838 | 2008-09-14 |  | 1250 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS.SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN, UNDER INVESTIGATION | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 24 | 0.6 | API 5X | 52000 | UNKNOWN |  | UNKNOWN | 1968 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | FOLLOWING THE STORM ON 9-13 TO 9-14 2008, THE PRESSURE READING ON THE 24-INCH ANR LINE 749 WAS APPROXIMATELY 60 PSI. MAOP ON THE LINE WAS 1250 PSIG.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080101 | 2008-10-09 16:33 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1700 | 2008-09-15 | 2008 |  |  | LA |  | 8.32 | 439+06 | 28*20'21 | -91*32'32 | OFFSHORE |  | EUGENE ISLAND | 296 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5276000 | 2942333.3745 | 6508652.44 | 50000 | 18681.9172 | 5226000 | 6489970.5227 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 884032 | 2008-09-15 |  | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS.SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN, UNDER INVESTIGATION | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 16 | 0.5 | API 5X | 52000 | UNKNOWN |  | UNKNOWN | 1978 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | THE 16-IN ANR LINE 606 IN E.I. BLOCK 296 WAS FOUND TO HAVE DAMAGE FOLLOWING HURRICANE IKE. THE INCIDENT INVESTIGATION CONTINUES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080102 | 2008-10-10 17:03 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1100 | 2008-09-10 | 2008 | SHREVEPORT | CADDO | LA | 71106 |  | LINE R 1670+68 | +32.341679 | -93.702786 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BLOWDOWN DAMAGED ON VALVE SETTING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 16506.3172 | 30433.9617 | 10718 | 4004.6558 | 21282 | 26429.3059 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 883364 | 2008-09-10 | 340 | 500 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | 2" BLOWDOWN | 1986 | 6 | 0.28 | API 5L GRADE B | 35000 | UNKNOWN | PLUG | NORDSTROM | 1986 | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1) OR (2 ). AT APPROXIMATELY 1100 HRS. ON SEPTEMBER 10, 2008 OUR SYSTEM CONTROL CENTER RECEIVED A CALL THAT OUR ABOVE GROUND BLOCK VALVE SETTING ON LINE R IN SOUTH SHREVEPORT, LA HAD BEEN STRUCK BY AN OUTSIDE FORCE (LOG SKIDDER). THE COLLISION RESULTED IN DAMAGE TO THE BARRICADE AND TO THE 2 INCH BLOWDOWN ON THE ABOVE GROUND BLOCK VALVE CAUSING A RELEASE OF NATURAL GAS. OUR EMERGENCY RESPONSE PLAN WAS INITIATED AND OUR FIELD PERSONNEL AND EMERGENCY RESPONDERS RESPONDED TO THE LOCATION. EMERGENCY RESPONDER CLOSED LASSO LANE AND PUEBLO LANE, AS WELL AS STOPPING SERVICE ON THE KCS RAILWAY WHICH WAS 100 YARDS WEST OF THE LOCATION. THE LINE WAS ISOLATED AND REPAIRS STARTED. BY 1300 HRS. THE AREA WAS SECURED AND THE ROADS WERE RE-OPENED. BY 1342 THE EMERGENCY RESPONDERS RE-OPENED THE KCS RAILWAY. THE BLOWDOWN VALVE WAS REPAIRED AND LINE R BACK IN SERVICE ON 1845 HRS. SEPTEMBER 11, 2008.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080103 | 2008-10-13 14:44 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1515 | 2008-09-16 | 2008 | [6 empty] | 28.3.16 | 92.19.10 | OFFSHORE |  | VERMILION | 397 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278459 | 126247.1499 | 147454.1397 | 228459 | 85361.0425 | 50000 | 62093.0972 | 0 | 0 | NO | NO | NO | NO | 0 |  | 348 | 0 | 884183 | 2008-09-16 | 765 | 2875 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2003 | 16 | 0.81 | API 5L | 65000 | DSAW |  |  |  | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | MATERIAL DEFECT |  | NO | YES | 7 | 23 | 2004 | NATURAL GAS |  | 3 | 2020 | [12 empty] | HIGH WINDS AND WAVES FROM HURRICANE IKE CAUSED A 3/4" NEEDLE VAVLE TO SHEAR OF AT THE +38 FOOT LEVEL ON VERMILION BLK 397, CAUSING THE PIPELINE TO BLOW DOWN. THE PIPELINE (MMS SEGMENT #14198)WAS ISOLATED AND MONITORED UNTIL REPAIRS COULD BE MADE. REPAIRS HAVE BEEN MADE ON PIPELINE. PIPELINE HAS NOT RETURNED TO SERVICE DUE TO NO FLOW FROM PRODUCERS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080104 | 2008-10-13 16:53 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1140 | 2008-09-16 | 2008 |  |  | LA |  |  |  | 28*3'4 | -91*29'29 | OFFSHORE |  | EUGENE ISLAND | 371 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7889000 | 4396312.0675 | 9710226.5213 | 100000 | 37363.8344 | 7789000 | 9672862.6869 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 884194 | 2008-09-16 |  | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN, UNDER INVESTIGATION | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.5 | API 5L | 42000 | ERW |  |  | 1989 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | THE 16-INCH ANR LINE 685 WAS FOUND TO HAVE DAMAGE FOLLOWING HURRICANE IKE. THE INCIDENT INVESTIGATION CONTINUES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080105 | 2008-10-13 17:13 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1140 | 2008-09-16 | 2008 |  |  | LA |  |  |  | 28*20'21 | -91*32'32 | OFFSHORE |  | EUGENE ISLAND | 296 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000000 | 2781645.6483 | 6122487.3632 | 100000 | 37363.8344 | 4900000 | 6085123.5288 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 884194 | 2008-09-16 |  | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN, UNDER INVESTIGATION | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 30 | 0.5 | API 5L | 60000 |  |  | UNKNOWN | 1968 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | THE 30-INCH ANR LINE 774 IN EUGENE ISLAND BLOCK 296 WAS FOUND TO HAVE DAMAGE FOLLOWING HURRICANE IKE. THE INCIDENT INVESTIGATION CONTINUES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080106 | 2008-10-14 10:42 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1300 | 2008-09-15 | 2008 | GRAND CHENIER | CAMERON | LA | 70643 | LINE 507A-1600 |  | 29.812258 | -93.238479 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK OF GAS IN TRANSPORT THROUGH DAMAGED TUBING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96000 | 41435.8078 | 36737.5046 | 95000 | 35495.6427 | 1000 | 1241.8619 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 884471 | 2008-09-18 | 980 | 1440 | YES | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | TUBING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2005 | 2.38 | 0.15 | API 5L | 35000 | SEAMLESS |  | LONE STAR | 2005 | ABOVE GROUND |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | TUBING IN TENNESSEE GAS PIPELINE'S SANDALWOOD METER STATION WAS SEVERED DUE TO HIGH WINDS AND LIKELY IMPACT BY DRIVEN DEBRIS DURING HURRICANE IKE. GAS IN TRANSPORTATION FROM THE ADJOINING PIPELINE WAS LOST AFTER TUBING WAS SEVERED. REPAIRS TO THE TUBING HAVE BEEN MADE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080107 | 2008-10-14 12:00 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1600 | 2008-09-16 | 2008 | GRAND ISLE | JEFFERSON | LA | 70358 | LINE 523M-100 |  | 28.675815 | -91.090933 | OFFSHORE |  | SHIP SHOAL | 157 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6886709 | 3591755.4149 | 6815894.6301 | 2000000 | 747276.6885 | 4886709 | 6068617.9417 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 884913 | 2008-09-16 | 980 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 26 | 0.5 | API 5L | 52000 | UNKNOWN |  | US STEEL | 1974 | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DAMAGE FROM JACK-UP DRILLING RIG DRIFTING |  | TENNESSEE GAS PIPELINE COMPANY'S 26" 523M-100 PIPELINE WAS DAMAGED DURING HURRICANE IKE APPARENTLY DUE TO A JACK-UP DRILLING RIG DRIFTING OFF LOCATION. CONTACT BETWEEN THE RIG AND THE PIPELINE RESULTED IN A RUPTURE OF THE PIPELINE. THE DAMAGED PORTION OF THE LINE WAS REMOVED AND REPLACED WITH NEW PIPE, WITH THE INTENT OF BEING PLACED BACK INTO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080108 | 2008-10-14 14:47 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1500 | 2008-09-17 | 2008 | GRAND ISLE | JEFFERSON | LA | 70358 | LINE 523Q-100 |  | 28.675803 | -91.09093 | OFFSHORE |  | SHIP SHOAL | 157 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7700000 | 4020581.3166 | 7652245.0529 | 2200000 | 822004.3573 | 5500000 | 6830240.6956 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 884341 | 2008-09-17 | 980 | 1200 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 36 | 0.6 | API 5L | 60000 | UNKNOWN |  | US STEEL | 1979 | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DAMAGE FROM JACK-UP DRILLING RIG DRIFTING |  | TENNESSEE GAS PIPELINE COMPANY'S 36" 523Q-100 LINE WAS APPARENTLY DAMAGED DURING HURRICANE IKE WHEN THE STORM CAUSED A JACK-UP DRILLING RIG TO DRIFT FROM ITS CORRECT LOCATION. IT IS SUSPECTED THAT THE RIG STRUCK THE PIPE CAUSING THE RUPTURE. THE DAMAGED PORTION OF THE PIPELINE IS BEING REPLACED WITH NEW PIPE, WITH THE INTENT OF RETURNING THE LINE TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080109 | 2008-10-14 15:20 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1400 | 2008-09-18 | 2008 | GRAND ISLE | JEFFERSON | LA | 70358 | LINE 524C-600 |  | 29.005424 | -90.152862 | OFFSHORE |  | BAY MAR | 5 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10250000 | 5696585.7568 | 12512029.0326 | 250000 | 93409.5861 | 10000000 | 12418619.4465 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 40 | 884490 | 2008-09-18 | 900 | 1138 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1962 | 12.75 | 0.38 | API 5L | 52000 | UNKNOWN |  | NATIONAL TUBE | 1962 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | TENNESSEE GAS PIPELINE COMPANY'S 12" 524C-600 LINE WAS DAMAGED DURING HURRICANE IKE DUE TO SEVERE WAVE AND WIND ACTION, RESULTING IN THE PIPELINE'S RUPTURE. UPON DETECTION OF THE INCIDENT, THE APPROPRIATE ISOLATION VALVES WERE CLOSED. THE PRODUCER DELIVERING INTO THIS LINE HAS SINCE REROUTED HIS PRODUCTION AND THIS PIPELINE IS PLANNED FOR ABANDONMENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080110 | 2008-10-13 | SUPPLEMENTAL FINAL | 2714 |  | DOMINION TRANSMISSION INC | 445 W. MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 630 | 2008-09-14 | 2008 | RENOVO | CLINTON | PA | 17764 | WELL # RW-30 | RW-30 | 41°28'22.52 | 77°44'58.41 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | UNKNOWN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | YES | NO | NO | 0 |  |  |  | 883739 | 2008-09-14 | 4075 | 4240 | NO | NO | YES | NO | NO | NO | ERIC TAYLOR, P.E. - MANAGER, PIPELINE INTEGRITY | 6818423034 | ERIC.V.TAYLOR@DOM.COM | TRANSMISSION | OTHER | UNKNOWN, DUE TO EXTENT OF FIRE DAMAGE | STEEL |  | NO | NO | NO | OTHER | STORAGE WELL | 1969 | [8 empty] | ABOVE GROUND |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | NARRATIVE UPDATED BY PHMSA PER OPERATOR ON 11/20/2015: IT WAS DISCOVERED AT 6:30 AM ON 9-14-08 THAT WELL #RW-30 HAD CAUGHT FIRE. THE ISOLATION OF GAS WAS NOT POSSIBLE, AS THE WELLHEAD WAS ENGULFED (REPORT # 883739). "WILD WELL" OF HOUSTON, TX WAS CONTRACTED TO BRING THE FIRE UNDER CONTROL, WHICH WAS ACHIEVED ON 9-25-08. THE CAUSE OF THE INCIDENT CANNOT BE DETERMINED DUE TO THE SEVERITY OF THE FIRE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080111 | 2008-10-15 18:55 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1745 | 2008-09-16 | 2008 | [6 empty] | 28.34.38 | 93.42.48 | OFFSHORE |  | HIGH ISLAND | 264 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25554091 | 14131417.5723 | 30716680.0725 | 1172478 | 438082.7386 | 24381613 | 30278597.3339 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 10 | 884210 | 2008-09-16 | 800 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1979 | 42 | 0.81 | API 5L | 60000 |  |  |  |  | UNDER WATER |  | 60 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | HURRICANE IKE |  | FOLLOWING HURRICANE IKE, PRESSURE ON THE HIGH ISLAND OFFSHORE SYSTEM 42" PIPELINE, MMS SEGMENT NUMBER 7364, WAS READING 60 PSIG. MINIMAL PRESSURE WAS APPLIED TO THE PIPELINE AND BUBBLES WERE REPORTED APPOXIMATELY 6 MILES NORTH OF HIA-264 PLATFORM. A DIVER INSPECTION REVEALED THE 42" PIPELINE WAS DAMAGED BY AN APPARENT ANCHOR DRAG AND SEVERED. PIPELINE REPAIRED AND PUT BACK IN SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080112 | 2008-10-16 15:39 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 930 | 2008-10-01 | 2008 |  |  | LA |  |  |  | 28*47'47 | -91*43'44 | OFFSHORE |  | EUGENE ISLAND | 175 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 182753.6962 | 347829.3206 | 100000 | 37363.8344 | 250000 | 310465.4862 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  |  | 2008-10-01 | 942 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN, UNDER INVESTIGATION | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 10.75 | 0.34 | API 5L | 46000 |  |  |  | 1967 | UNDER WATER |  | 36 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE PROBABLE CAUSE OF THE INCIDENT REMAINS UNDETERMINED. ONCE REPAIRS ARE UNDERWAY, THE PIPE WILL BE EXAMINED MORE CLOSELY. |  | A SMALL LEAK WAS DISCOVERED ON ANR'S 10-INCH LINE 736 BY APACHE IN EUGENE ISLAND BLOCK 175, NEAR THE LOCATION OF A SUB-SEA TIE-IN. AT THE PRESENT, REPAIRS ON THE PIPE ASSEMBLY ARE ON HOLD, PENDING A DECISION BY THE PRODUCER AS TO POSSIBLY TAKING OWNERSHIP OF THE LINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080113 | 2008-10-17 11:33 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1430 | 2008-09-18 | 2008 | GRAND ISLE | JEFFERSON | LA | 70358 | LINE 523M-3600 |  | 28.16294 | -92.487721 | OFFSHORE |  | EUGENE ISLAND | 349 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 80619.7675 | 164573.7017 | 25000 | 9340.9586 | 125000 | 155232.7431 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 884485 | 2008-09-18 | 1250 | 1440 | YES | NO | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 16 | 0.5 | API 5L | 52000 | UNKNOWN |  | UNKNOWN |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | THE PRODUCTION PLATFORM TO WHICH TENNESSEE GAS PIPELINE COMPANY'S 16" 523M-3600 PIPELINE WAS ATTACHED OFFSHORE LOUISIANA IN EUGENE ISLAND BLOCK 349 WAS TOPPLED DURING HURRICANE IKE. THESE FACILITIES WERE PLANNED FOR ABANDONMENT BUT THERE WAS SOME GAS LEFT IN THE PIPELINE THAT WAS RELEASE WHEN THE PIPE WAS SEVERED FROM THE TOPPLED PLATFORM. THIS PIPELINE IS TO BE ABANDONED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080114 | 2008-10-21 09:59 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1015 | 2008-09-23 | 2008 | GRAND ISLE | JEFFERSON | LA | 70358 | LINE 524C-400 |  | 29.01264 | -90.14227 | OFFSHORE |  | BAY MAR | 5 | LA | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3750000 | 2063726.0388 | 4439926.3923 | 250000 | 93409.5861 | 3500000 | 4346516.8063 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 884987 | 2008-09-23 | 900 | 1069 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 16 | 0.41 | API 5L | 42000 | UNKNOWN |  | NATHIONAL TUBE | 1961 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | POST STORM INSPECTION OF TENNESSEE GAS PIPELINE COMPANY'S 16" 524C-400 PIPELINE REVEALED THAT THE FACILITY HAD INCURRED A SUBSTANTIAL DECREASE IN PRESSURE. PRELIMINARY SURVEY OF THE PIPELINE INDICATED THAT DAMAGE WAS SUSTAINED DURING WIND AND WAVE ACTION RELATED TO HURRICANE IKE. UPON DETECTION OF INCIDENT, THE APPROPRIATE ISOLATION VALVES WERE CLOSED. DAMAGE WAS ACTUALLY TO A SUBSEA TIE-IN ASSEMBLY IN THE PIPELINE. THE ASSEMBLY HAS BEEN REPAIRED AND THE PIPELINE WAS RESTORED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080115 | 2008-10-20 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1129 | 2008-09-16 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28.238056N | 91.696389W | OFFSHORE |  | EUGENE ISLAND | 330 |  | YES | NO | INTERSTATE | OTHER | PIPES DAMAGED BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25778457 | 14400945.6992 | 31968243.0362 | 51878 | 19383.61 | 25726579 | 31948859.4261 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 884136 | 2008-09-15 |  | 1306 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT ASSOCIATE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 24 | 0.5 | API 5LX | 60000 | SAW | N/A | KAISER | 1972 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | HURRICANE IKE CAUSED THE DEVON ENERGY EI-330A PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO SEA ROBIN PIPELINE COMPANY'S 24 INCH PIPELINE. SEA ROBIN USED THIS DEVON ENERGY EI-330A PLATFORM AS A VALVE PLATFORM. SEPARATE REPORTS (#884136 AND 884141) WERE MADE TO THE NATIONAL RESPONSE CENTER (NRC) FOR BOTH THE UPSTREAM AND DOWNSTREAM SEGMENTS OF 24" LINE, WHICH WERE BOTH DAMAGED WHEN THE PLATFORM TOPPLED. THE OTHER NRC REPORT # 884141, WILL BE RESCINDED, SINCE IT WAS A SINGLE INCIDENT (EI-330A PLATFORM TOPPLING) THAT CAUSED THE DAMAGE. DIVERS HAVE NOT BEEN AVAILABLE TO INVESTIGATE THE FAILURE. (ADDITION) JUST AS NRC # 884141 WAS RESCINDED, NRC # 884142 IS ALSO BEING REQUESTED TO BE RESCINDED DUE TO ALL THE DAMAGE BEING CAUSED BY ONE INCIDENT: THE TOPPLING OF DEVON ENERGY EI-330A. THE TOTAL DAMAGES FOR ALL THREE SEPARATE REPORTS ARE INCLUDED IN THE TOTAL OF THIS FINAL REPORT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080116 | 2008-10-20 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1129 | 2008-09-16 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28^13'36 | 91^41'04 | OFFSHORE |  | EUGENE ISLAND | 330 |  | YES | NO | INTERSTATE | OTHER | PIPE DAMAGED BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630000 | 351774.1775 | 780119.9849 | 2595 | 969.5915 | 627405 | 779150.3934 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 | 0 | 884142 | 2008-09-16 | 895 | 1306 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT PIPELINE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 16 | 0.5 | API 5LX | 60000 | SMLS | N/A | KAISER | 1972 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | HURRICANE IKE CAUSED THE DEVON ENERGY EI-330C PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO SEA ROBIN PIPELINE COMPANY'S 16 INCH PIPELINE. PIPE WAS ISOLATED AND ABANDONED IN PLACE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080117 | 2008-10-20 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1730 | 2008-09-16 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28.62528 | 92.89167 | OFFSHORE |  | EAST CAMERON | 229 |  | YES | NO | INTERSTATE | OTHER | PIPE DAMAGED BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630000 | 351868.8405 | 780758.9975 | 1859 | 694.5937 | 628141 | 780064.4038 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 | 0 | 884251 | 2008-09-17 | 895 | 1250 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT ASSOCIATE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 6 | 0.31 | APIL 5L | 35000 | SMLS | N/A | ARMCO | 1972 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICAN IKE | [51 empty] | HURRICANE IKE CAUSED THE CONN ENERGY EC-229 PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO SEA ROBIN PIPELINE COMPANY'S 6 INCH PIPELINE. PIPE WAS ISOLATED AND ABANDONED IN PLACE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080118 | 2008-10-20 | SUPPLEMENTAL FINAL | 18152 |  | SEA ROBIN PIPELINE CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1653 | 2008-09-15 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28.43750N | 92.87778W | OFFSHORE |  | EAST CAMERON | 265 |  | YES | NO | INTERSTATE | OTHER | COMPANY PLATFORM TOPPLED DAMAGING PIPELINES | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19283566 | 10770154.008 | 23897169.8037 | 58000 | 21671.024 | 19225566 | 23875498.7798 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 884011 | 2008-09-15 |  | 1250 | YES | NO | NO | NO | NO | NO | JOE CRAYCRAFT ASSOCIATE ENGINEER | 7139897414 | JOE.CRAYCRAFT@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 30 | 0.63 | API 5LX | 60000 | SAW | N/A | USS | 1977 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | HURRICANE IKE CAUSED THE SEA ROBIN EC-285 PLATFORM TO TOPPLE, WHICH RESULTED IN DAMAGE TO SEA ROBIN COMPANY'S 30 INCH PIPELINE. IN ADDITION, BOTH A 24 INCH AND 12 INCH PIPELINE, WHICH ALSO TERMINATED ON THE EC-265 PLATFORM WERE DAMAGED WHEN THE PLATFORMO TOPPLED. DIVERS HAVE NOT BEEN AVAILABLE TO INVESTIGATE THE FAILURE. PIPELINES FAILED IN TORSIONAL STRESS FROM TOPPLING PLATFORM. PIPE HAS BEEN REPLACED AND LINES ARE BACK IN SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080119 | 2008-10-22 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056-5306 | 930 | 2008-09-03 | 2008 | RAYVILLE | RICHLAND | LA | 71269 | MP 167.55/VS 65 | 63+31 | 32°33'03.8 | 91°39'03.7 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAKING BODY BLEED PLUG | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168238 | 72454.2982 | 63294.2796 | 167738 | 62673.3486 | 500 | 620.931 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 30 | 882615 | 2008-09-03 | 780 | 1480 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS, PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | OTHER | BODY BLEED PLUG | STEEL |  | NO | NO | NO | PIPELINE |  | 2001 | 12 |  | N/A |  | N/A | BALL | GROVE | 2001 | UNDER GROUND |  | 60 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | VALVE BODY BLEED | [8 empty] | MATERIAL DEFECT |  | NO | YES | 3 | 2 | 2001 | WATER |  | 8 | 2218 | [12 empty] | TRUNKLINE GAS COMPANY RECEIVED A REPORT OF BLOWING GAS AT THE CENTERPOINT MEASURING STATION CLOSE TO THE TAKE-OFF TAP VALVE (65A). THE EMPLOYEE WHO RESPONDED FELT THAT THE AMOUNT OF GAS VENTING AROUND THE TAP VALVE PRECLUDED SAFELY CLOSING THE VALVE. THE DECISION WAS MADE TO BLOW DOWN THE ENTIRE VALVE SECTION TO SAFELY ISOLATE THE TAP VALVE. DAMAGE WAS MINIMAL AND GAS LOSS DUE TO THE BLOW DOWN WAS THE ONLY REASON THAT IT REACHED THE LEVEL OF A REPORTABLE INCIDENT. IT WAS DETERMINED THAT THE CAUSE OF THE LEAK WAS A LEAKING BODY BLEED PLUG ON THE TAP VALVE, WHICH WAS REMOVED AND REPLACED WITH ANOTHER VALVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080120 | 2008-10-28 11:29 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1525 | 2008-10-03 | 2008 |  |  | LA |  |  |  | 28*16'16 | -91*5'6 | OFFSHORE |  | SHIP SHOAL | 291 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470000 | 260111.3373 | 566310.642 | 20000 | 7472.7669 | 450000 | 558837.8751 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 866092 | 2008-10-03 |  | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN, UNDER INVESTIGATION | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 10.75 | 0.31 | API 5L | 35000 |  |  |  | 1978 | UNDER WATER |  | 36 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE DAMAGE | [51 empty] | FOLLOWING AN INVESTIGATION OF HURRICANE-RELATED DAMAGE, THE 10-INCH ANR LINE 613 WAS FOUND TO HAVE A LEAK. THE LEAK OCCURRED AT THE BASE OF THE RISER AT THE SHIP SHOAL BLOCK 291 PLATFORM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080121 | 2008-10-29 09:18 | SUPPLEMENTAL | 2714 |  | DOMINION TRANSMISSION INC | 445 W. MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 1500 | 2008-09-30 | 2008 | DELMONT | WESTMORELAND | PA | 15626 |  |  | 40 24 37.24 N | 79 32 15.30 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 154457.6767 | 156820.1285 | 320000 | 119564.2702 | 30000 | 37255.8583 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 885790 | 2008-09-30 | 1179 | 1225 | NO | NO | YES | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN.A.MILLER@DOM.COM | TRANSMISSION | OTHER | DRIP | STEEL |  | NO | NO | NO | OTHER | DRIP | 1950 | 12 | [7 empty] | UNDER GROUND |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1952 | NO | [57 empty] | AT 3:00 PM ON SEPTEMBER 30, 2008, A STEPLADDER DRIP ON PIPELINE JP45 IN THE OAKFORD STORAGE POOL RUPTURED. THE PRESSURE ON THE PIPELINE AT THE TIME WAS 1179 PSIG (MAOP = 1225 PSIG). THE RUPTURED SEGMENT WAS ISOLATED BY 5:00 PM. AFTER A THOROUGH REVIEW WITH PHMSA (MR. MIKE YAZEMBOSKI), A REINSTATEMENT PLAN WAS AGREED-UPON, AND THE PIPELINE WAS PLACE BACK INTO SERVICE ON OCTOBER 3, 2008. THE RUPTURED DRIP HAS BEEN SENT TO KIEFNER AND ASSOCIATES FOR ANALYSIS. DTI AWAITS THE FINAL REPORT. UPDATE - DTI HAS RECEIVED THE FINAL FAILURE INVESTIGATION REPORT FROM KIEFNER AND ASSOCIATES. THE REPORT INDICATES THAT THE CAUSE OF THE FAILURE WAS INTERNAL CORROSION (MIC). A COPY OF THE FINAL REPORT HAS BEEN FURNISHED TO MR. MIKE YAZEMBOSKI, PHMSA, EASTERN REGION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080122 | 2008-10-27 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1647 | 2008-09-15 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28^19'23 | 91^12'18 | OFFSHORE |  | SHIP SHOAL | 274 |  | YES | NO | INTERSTATE | OTHER | PIPELINE DAMAGED BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24830900 | 13870721.6161 | 30787234.6609 | 56800 | 21222.658 | 24774100 | 30766012.003 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 |  | 884010 | 2008-09-15 | 895 | 1200 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 20 | 0.47 | API 5LX | 60000 | ERW | N/A | USS | 1972 | UNDER WATER |  | 30 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | HURRICANE IKE CAUSED THE TRUNKLINE GAS COMPANY SS274 PLATFORM A (T-27) TO TOPPLE, WHICH RESULTED IN DAMAGE TO THE 20-INCH PIPELINE, OPERATED BY TRUNKLINE GAS COMPANY. DAMAGE ALSO RESULTED TO THE TARPON PIPELINE THAT INTERSECTED AT THIS PLATFORM. TOPPLED PLATFORM WAS BY-PASSED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080123 | 2008-10-27 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1113 | 2008-09-25 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28^31'47 | 90^6'17 | OFFSHORE |  | GRAND ISLE | 94 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4890000 | 2731761.4209 | 6064152.9069 | 9850 | 3680.3377 | 4880150 | 6060472.5692 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 |  | 885242 | 2008-09-25 | 895 | 1219 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1977 | 20 | 0.47 | API GLX | 52000 | SSAW? | N/A | KAISER | 1977 | UNDER WATER |  | 30 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | HURRICANE IKE CAUSED DAMAGE TO THE 20 INCH PIPELINE, OPERATED BY TRUNKLINE GAS COMPANY. HURRICANE DISPLACED A PORTION OF THE PIPELINE RESULTING IN DAMAGE. A SUBSEA TIE-IN ASSEBBLY WAS REPLACED AND PIPELINE ANCHORS INSTALLED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080124 | 2008-09-15 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1637 | 2008-09-15 | 2008 | N/A | N/A |  | N/A | N/A | N/A | 28^30.91' N | 90^43.76 W | OFFSHORE |  | SOUTH TIMBALIER | 196 |  | YES | NO | INTERSTATE | OTHER | PIPE DAMAGE BY TOPPLED PLATFORM | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1370000 | 765367.0717 | 1699136.894 | 2550 | 952.7778 | 1367450 | 1698184.1162 | 0 | 0 | NO | NO | NO | NO | 0 |  | 72 |  | 884005 | 2008-09-15 | 985 | 1200 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | OTHER | DAMAGE FROM PLATFORM FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 10 | 0.37 | API 5LX | 52000 | SMLS | N/A | JONES & LAUGHLIN | 1971 | UNDER WATER |  | 30 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | HURRICANE IKE CAUSED THE BERYL OIL ST 196 PLATFORM A TO TOPPLE, WHICH RESULTED IN DAMAGE TO THE 10 INCH PIPELINE, OPERATED BY TRUNKINE GAS COMPANY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080125 | 2008-10-30 | ORIGINAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1100 | 2008-10-01 | 2008 | CLINTON | HINDS | MS | 39213 | MP 317.54 | 167661+12 | 32.4083 | -90.2590 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120010 | 51639.5759 | 44849.0199 | 120000 | 44836.6013 | 10 | 12.4186 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 57 | 885867 | 2008-10-01 | 952 | 1100 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@SPECTRAENERGY.COM | TRANSMISSION | OTHER | 1-INCH NIPPLE | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 1 | 0.18 | UNKNOWN |  | N/A | N/A | UNKNOWN |  | ABOVE GROUND |  | 0 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | COMPANY PERSONNEL BACKED VEHICLE INTO 1-INCH NIPPLE AT LAUNCHER BARREL CAUSING A CRACK IN THE NIPPLE AND NATURAL GAS TO LEAK. A 12 MILE VALVE SEGMENT WAS BLOWN DOWN IN ORDER TO REPLACE THE NIPPLE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080126 | 2008-10-31 13:27 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 900 | 2008-10-03 | 2008 | CAMERON | CAMERON | LA | 70631 | LINE 509A-302 | 302 + 857 + 20 | 28.259845 | -92.855348 | OFFSHORE |  | EAST CAMERON | 313 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425000 | 234317.6786 | 506085.7365 | 25000 | 9340.9586 | 400000 | 496744.7779 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 886044 | 2008-10-03 | 1150 | 1250 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 20 | 0.5 | API 5L | 60000 | UNKNOWN |  | US STEEL | 1973 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | POST STORM INSPECTION OF TENNESSEE GAS PIPELINE COMPANY'S 509A-300 PIPELINE REVEALED THAT THIS 20" LINE SEPARATED AT A VALVE DUE TO FORCES BROUGHT TO BEAR DURING HURRICANE IKE. UPON DETECTION OF THE INCIDENT, APPROPRIATE ISOLATION VALVES WERE CLOSED. PIPELINE IS BEING ABANDONED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080127 | 2008-11-06 21:00 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1700 | 2008-10-08 | 2008 | [6 empty] | 29.08703 | -91.69764 | OFFSHORE |  | EUGENE ISLAND | 95 |  | YES | NO | INTERSTATE | OTHER | HURRICANE DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 39123.1047 | 86930.3361 | 0 | 0 | 70000 | 86930.3361 | 0 | 0 | NO | NO | NO | NO | 0 |  | 14 |  | 886591 | 2008-10-08 | 920 | 1440 | NO | YES | NO | NO | NO | NO | JACK L. ADAMS | 7134798099 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | OTHER | ALIGNMENT BALL | STEEL |  | NO | NO | NO | PIPELINE |  | 2003 | 10 | [5 empty] | UNKNOWN |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | PRODUCER AT EUGENE ISLAND BLOCK 95F REPORTED BUBBLING NEAR THE GULF SOUTH SUB-SEA TIE-IN. ALL PRODUCERS ON THIS SEGMENT WERE SHUT-IN AND ISOLATED. DIVE VESSEL WAS DISPATCHED TO AREA AND DETERMINED A LEAKING FLANGE AT THE SSTI ON THE PIPELINE GOING TO EUGENE ISLAND BLOCKS 110 & 113. ADDITIONAL INFORMATION WILL BE PROVIDED ONCE INVESTIGATION IS COMPLETE. UPDATE: AN ALIGNMENT BALL AT BLOCK 95 SUB SEA ASSEMBLY SLIPPED POSITION DUE T THE ROUGH SEAS OF HURRICANE IKE. THE PIPE LEADING TO THE ALIGNMENT BALL SHIFTED AND WAS LEAKING AT CONNECTION. THE PIPE WAS REPLACED AND A NEW ALIGNMENT BALL WAS INSTALLED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080128 | 2008-11-07 11:09 | ORIGINAL FINAL | 31286 |  | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | TULSA | OK | 74103 | 920 | 2008-10-09 | 2008 | NORMAN | CLEVELAND | OK | 73072 | T9N R3W SECTION 15 NW/4 | N/A | 35.25785N | -097.50733W | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70589 | 31944.7206 | 36982.713 | 58371 | 21809.6438 | 12218 | 15173.0692 | 0 | 0 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 1 | 35 | 886661 | 2008-10-09 | 527 | 686 | NO | NO | YES | NO | NO | NO | PATTI FORD - SENIOR PIPELINE SAFETY ENGINEER | 9185887131 | PATTI.FORD@ONEOK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1945 | 12 | 0.25 | GRADE B | 35000 | DSAW | N/A | UNKNOWN |  | UNDER GROUND |  | 18 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | NO |  |  |  |  | YES |  | YES | ACCURATE | YES | [36 empty] | LINE A-1000 RUNS THROUGH A PARCEL OF LAND THAT IS CURRENTLY UNDERGOING DEVELOPMENT FROM AN OPEN FIELD TO A HOUSING SUBDIVISION. THE ONEOK REGION OFFICE HAS BEEN IN CONTACT WITH THE DEVELOPER(S) FOR MORE THAN FIVE YEARS. A ONEOK PIPELINE OPERATOR PERFORMED A LINE LOCATE AND INSTALLED NUMEROUS PERMANENT LINE MARKERS LAST YEAR. THERE WERE THREE ONECALLS INITIATED BY AN ENGINEERING FIRM UNDER CONTRACT TO THE DEVELOPER IN THE FOUR WEEKS PRIOR TO THE LINE DAMAGE (OKS08091707420122 OPENED AND CLOSED ON 9/17/08, OKS08092308460323 OPENED AND CLOSED ON 9/23/08, AND OKS08100116141956 OPENED ON 10/1/08 AND CLOSED ON 10/2/08). THE ONEOK PIPELINE OPERATOR TALKED TO THE ENGINEERING FIRM EMPLOYEES ONSITE ON THE SECOND ONECALL AND POINTED OUT THE PERMANENT MARKERS AND STATED THAT EQUIPMENT WAS NOT BE BE ON THE PIPELINE. THE ONEOK PIPELINE OPERATOR EMPHASIZED TO THE ENGINEERING FIRM THEY NEEDED TO STAY AT LEAST 100 FEET AWAY FROM THE MARKED PIPELINE. THE ENGINEERING FIRM INDICATED THEY WOULD BE DOING SOIL TEST BORINGS AND THEIR EQUIPMENT WOULD NOT BE CLOSE TO THE PIPELINE. THE ONEOK PIPELINE OPERATOR DID NOT RECEIVE ANY FURTHER PHONE CALLS FOR ASSISTANCE AFTER THE LAST ONECALL WAS CLEARED. ON 10/9/08, A BULLDOZER OPERATOR WORKING FOR THE ENGINEERING FIRM WAS REMOVING DIRT FROM OVER THE TOP OF THE PIPELINE. THE BULLDOZER BLADE MADE CONTACT WITH THE A-1000 PIPELINE AND PUNCTURED A HOLE IN THE PIPELINE AT 920AM. THE ESCAPING HIGH PRESSURE NATURAL GAS DID NOT EXPLODE OR IGNITE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080129 | 2008-11-10 14:12 | SUPPLEMENTAL FINAL | 31336 |  | CHEVRON U.S.A. INC | 100 NORTHPARK BLVD | COVINGTON | ST. TAMMANY | LA | 70433 |  | 2008-10-10 | 2008 |  |  | GM | [5 empty] | OFFSHORE |  | GRAND ISLE | 79 | GM | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1380660 | 735554.9343 | 1470913.4768 | 280660 | 104865.3377 | 1100000 | 1366048.1391 | 0 | 0 | NO | NO | NO | NO | 0 |  | 49 | 9 | 888661 | 2008-10-30 | 850 | 1480 | NO | NO | NO | NO | NO | NO | ERIN DUNAWAY | 9857736554 | ERIN.DUNAWAY@CHEVRON.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1997 | 24 | 0.48 |  | 65000 |  |  |  |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DAMAGE CAUSED BY HURRICANE IKE WAVE ACTION. |  | THE CAUSE OF THE LEAK WAS A BREAK AT THE MARITECH RESOURCES INC. 8" HOT TAP CLAMP. PIPELINE WAS REPAIRED AND REACTIVATED ON 11/10/08. A PLIDCO SPLIT SLEEVE FULL ENCIRCLEMENT CLAMP RATED FOR THE MAOP OF THE LINE WAS INSTALLED IN PLACE OF THE EXISTING HOT TAP CLAMP. THE LINE WAS LEAK TESTED FOR 2 HOURS AT THE OPERATING PRESSURE OF THE LINE; DURING THE LEAK TEST DIVERS VISUALLY INSPECTED THE REPAIR AREA FOR ANY SIGN OF LEAKAGE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080131 | 2008-11-12 14:28 | SUPPLEMENTAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25325 | 800 | 2008-10-15 | 2008 | LEESBURG | LOUDOUN | VA |  | LINE VC LEESBURG GATE SET |  |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | CONTROLLED BLOW DOWN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13000 | 7265.7194 | 16144.2053 | 0 | 0 | 0 | 0 | 13000 | 16144.2053 | NO | YES | NO | NO | 0 |  |  | 45 | 887187 | 2008-10-15 | 80 | 899 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | OTHER | NO FAILURE, INCIDENT FIRE AT VALVE SETTING | STEEL |  | NO | NO | NO | OTHER | VALVE SETTING | [9 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | DURING CONTROLLED BLOWDOWN OF A PIPELINE AT A VALVE SETTING, RELEASED GAS CAUGHT FIRE DUE TO DAMAGE TO ADJACENT HIGH VOLTAGE ELECTRIC LINES |  | DURING CONTROLLED BLOWDOWN OF A PIPELINE AT A VALVE SETTING, RELEASED GAS CAUGHT FIRE DUE TO DAMAGE TO ADJACENT HIGH VOLTAGE ELECTRIC LINES
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080132 | 2008-11-13 08:04 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 2345 | 2008-10-19 | 2008 | INVERNESS | SUNFLOWER | MS | 38753 | 7SH-1D |  | 33.31138 | -90.52522 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELEASE OF GAS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58233 | 25056.683 | 21758.0817 | 58233 | 21758.0817 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 19 | 887643 | 2008-10-19 | 825 | 1008 | NO | YES | NO | NO | NO | NO | MARK A. NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1970 | [5 empty] | PLUG | ROCKWELL | 1970 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | CONTROLLER | [10 empty] | THIS COMPRESSOR STATION WAS EXPERIENCING ELECTRICAL POWER SURGES WHEN THE STATION ESD SYSTEM WAS ACTIVATED. THE 8" FIRE VALVE CONNECTED TO THE STATION ESD SYSTEM FAILED TO CLOSE WHICH WOULD HAVE ISOLATED THE SUCTION SIDE OF THE COMPRESSOR STATION FROM THE PIPELINE. THE VALVE BLEW FOR 19 MINUTES RESULTING IN APPROXIAMTELY 6734 MCF OF GAS LOST. DURING OUR INVESTIGATION IT WAS DISCOVERED THAT THE SHAFER CONTROLS (MANUFACTURED AND INSTALLED IN 1970) TO VALVE 7SH-1D WAS NOT OPERATING PROPERLY. THE ACNR MODULE (NODE 3) INSIDE THE SUCTION SIDE TEST STAND WAS THE SOURCE OF THE FAILURE. THE NODE WAS REPLACED ON 11/3/08. THE CONTROLS TO THE VALVE WERE CLEANED AND THE O-RING, POPPET'S SPRINGS, AND VALVE PACKING WERE REPLACED OR REINSTALLED. THE CONTROLS TO THE VALVE WERE TESTED TO MAKE SURE THE VALVE AND ESD SYSTEM WERE FUNCTIONING PROPERLY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080133 | 2008-11-14 09:27 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1430 | 2008-10-15 | 2008 |  |  |  |  | 527A-1300 LINE |  | 28.888707 | -89.063609 | OFFSHORE |  | SOUTH PASS | 49 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8050000 | 4492726.1218 | 9953577.4744 | 50000 | 18681.9172 | 8000000 | 9934895.5572 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 887203 | 2008-10-15 | 980 | 1440 | YES | NO | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12.75 | 0.5 | API 5L | 42000 |  |  | US STEEL | 1990 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | TENNESSEE GAS PIPELINE COMPANY'S 12.75" 527A-1300 PIPELINE WAS APPARENTLY SUBJECTED TO FORCES DURING HURRICANE IKE THAT SEVERED THE PIPELINE AND ALSO DISPLACED IT. THE PIPELINE'S DAMAGE WAS DISCOVERED ONLY AFTER PERSONNEL BEGAN PLACING NATURAL GAS BACK INTO THE PIPELINE AND FOUND THAT THE LINE WOULD NOT HOLD PRESSURE. THE PIPELINE IS NOT IN SERVICE AND IS PLANNED FOR ABANDONMENT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080134 | 2008-11-17 14:56 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1149 | 2008-11-07 | 2008 | OTTAWA | LA SALLE | IL |  |  |  | 41.4109 | -88.8645 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53344 | 23145.9557 | 21233.6992 | 51844 | 19370.9063 | 1500 | 1862.7929 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 889435 | 2008-11-07 | 529 | 714 | NO | YES | NO | NO | NO | NO | BRUCE R. HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 2 | 0.25 | GR. B | 35000 |  |  |  |  | ABOVE GROUND |  |  | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | OPERATOR'S CONTRACTOR WAS SPREADING ROCK IN A FENCED VALVE AREA AND STRUCK AN ABOVE GROUND 2-INCH BLOWOFF. THE VALVE WAS IN PLAIN SIGHT AND CLEARLY MARKED. OPERATOR ERROR.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080135 | 2008-11-18 14:11 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1420 | 2008-10-21 | 2008 | FREEPORT |  | TX |  |  |  | 28^35'45 | 95^12'82 | OFFSHORE |  | GA | 394 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906000 | 505593.0449 | 1119917.5803 | 6000 | 2241.8301 | 900000 | 1117675.7502 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 38 | 887809 | 2008-10-21 | 995 | 1250 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 12.75 | 0.31 | API 5L | 52000 | SMLS |  | USS TUBULAR | 1990 | OTHER | OCS | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | -- | MICROBIOLOGICAL |  | YES | 1990 | NO | [57 empty] | ASSUMPTION OF LEAK DUE TO INTERNAL CORROSION. THE PIPELINE WAS UNPIGGABLE
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080136 | 2008-11-18 16:39 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1700 | 2008-10-20 | 2008 |  |  |  |  | 523M-106 LINE | 0 + 05 | 28.585710 | -92.449633 | OFFSHORE |  | VERMILION | 245 |  | YES | NO | INTERSTATE | OTHER | HALF INCH VALVE SHEARED OFF SIDE VALVE ASSEMBLY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 37836.9219 | 78248.1001 | 10000 | 3736.3834 | 60000 | 74511.7167 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 | 887718 | 2008-10-20 | 850 | 1250 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 30 | 0.6 | API 5L | 60000 |  | 2022-01-02 | BETHLEHEM | 1974 | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | FOLLOWING COMPLETION OF MORE POST STORM INSPECTIONS, NATURAL GAS PRESSURE BEGAN TO BE PUT BACK ONTO A SIDE VALVE ASSEMBLY IN TENNESSEE GAS PIPELINE COMPANY'S 30" 523M-106 PIPELINE. A SMALL GAS BUBBLE WAS OBSERVED. UPON FURTHER INVESTIGATION BY DIVERS, A 1/2" VALVE AND NIPPLE HAD BEEN SHEARED OFF OF THE SIDE VALVE ASSEMBLY. THIS IS BELIEVED TO HAVE BEEN CAUSED BY HEAVY WAVE ACTION DURING HURRICANE IKE OR BY DEBRIS DRIVEN UNDERWATER STRIKING THE VALVE & NIPPLE DURING HURRICANE IKE. REPAIRS WERE MADE BY INSTALLING A NEW 1/2" VALVE AND NIPPLE. THE PIPELINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20080137 | 2008-11-19 15:41 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1330 | 2008-10-28 | 2008 | BELCHER | CADDO | LA | 71004 |  | LINE S 1078+80 | +32.665900 | -93.825100 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | VALVE ACTUATOR BLEW APART | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 13526 | 7559.7016 | 16797.4247 | 0 | 0 | 13526 | 16797.4247 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 5 | 888447 | 2008-10-28 | 700 | 930 | NO | NO | NO | NO | YES | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | VALVE ACTUATOR | STEEL |  | NO | NO | NO | OTHER | INTERCONNECT STATION | 1989 | [8 empty] | ABOVE GROUND |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 6 |  |  | A CEGT EMPLOYEE WAS INJURED WHILE ATTEMPTING TO REDIRECT NATURAL GAS FLOW BETWEEN TWO NATURAL GAS PIPELINES ON LINE S AT CEGT¿S DIXIE INTERCONNECT STATION. A PNEUNATIC VALVE OPERATOR WAS OVER-PRESSURED CAUSING HIS INJURIES. THE INJURED EMPLOYEE IMMEDIATELY SECURED THE SITE BY CLOSING A ONE ¿ INCH VALVE, MAKING THE AREA SAFE. THE EXTENT OF THE EMPLOYEE¿S INJURIES CAUSED HIM TO BE HOSPITALIZED. THE CAUSE OF THIS INCIDENT WAS ¿INCORRECT OPERATIONS- FAILURE TO FOLLOW PROCEDURE.¿
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080138 | 2008-11-20 | SUPPLEMENTAL FINAL | 32099 |  | ENERGY TRANSFER COMPANY | 800 E. SONTERRA BLVD. #400 | SAN ANTONIO | BEXAR | TX | 78258 | 1230 | 2008-10-07 | 2008 | CHESTER | TYLER | TX | 75936 | 123.445 | 6514 + 50 | N 31°00.183 | W 94°39.355 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 6023.9651 | 5230.9368 | 14000 | 5230.9368 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 12 | 45 |  |  | 839 | 985 | NO | YES | NO | NO | NO | NO | DANNY NICHOLS, DIRECTOR OF REGULATORY COMPLIANCE | 8326681006 | DANNY.NICHOLS@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | REPAIR SLEEVE | STEEL |  | NO | NO | NO | PIPELINE |  | 1929 | 10 | 0.31 | UNKNOWN | 24000 | UNKNOWN | MANUAL | UNKNOWN |  | UNDER GROUND |  | 32 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | REPAIR SLEEVE |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 9 | 9 | 2006 | WATER |  | 8 | 1383 | [12 empty] | A NATURAL GAS LEAK WAS DISCOVERED ON ENERGY TRANSFER COMPANY'S VANTEX 10" PIPELINE ON OCTOBER 7, 2008. THE LEAK OCCURRED ON A BELOW GROUND SECTION OF PIPE THAT HAD PREVIOUSLY BEEN REPAIRED BY INSTALLING A WELD ON REPAIR SLEEVE. THE PREVIOUS REPAIR SLEEVE HAD BEEN INSTALLED SOME >= 20 YEARS PRIOR. THE LEAK TOOK PLACE IN A RURAL (CLASS I) AREA. THE SECTION OF PIPE WAS DEPRESSURIZED, REPLACED AND SERVICE WAS REINSTATED ON OCTOBER 11, 2008.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080139 | 2008-11-20 | ORIGINAL FINAL | 32335 |  | REGENCY INTRASTATE GAS LLC | 201 OAK STREET | DUBACH | LINCOLN | LA | 71235 | 852 | 2008-11-05 | 2008 | HAUGHTON | BOSSIER | LA | 71037 |  |  | 32.39322 | -93.48820 | ONSHORE |  |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119700 | 54746.0824 | 66603.7445 | 94500 | 35308.8235 | 25200 | 31294.921 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 58 | 889207 | 2008-11-05 | 850 | 1000 | NO | NO | NO | NO | NO | NO | ANGELA MORGAN | 9032436541 | ANGELA.MORGAN@REGENCYGAS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO |  |  | 1974 | 12 | 0.22 | API 50 X52 | 52000 | ERW |  |  |  | UNDER GROUND |  | 27 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | THIRD PARTY COMPRESSOR STATION CONSTRUCTION | NO |  |  |  |  | YES | FLAGS | YES | ACCURATE | YES | [36 empty] | PETROHAWK CONTRACTED DURRETT CONSTRUCTION TO BUILD A COMPRESSOR STATION PAD IN THE AREA OF THE S ELM GROVE 12¿ PIPELINE NEAR HWY 157 & CHINANOOK ROAD. DURRETT CONSTRUCTION DID A LA ONE CALL ON 9/24/08 (#80402646). THIS LOCATE WAS UPDATED 2 TIMES (#80417509 AND #80435865). ON ALL LOCATES, THE TYPE OF WORK LISTED WAS STATED AS ¿CLEARING TO INSTALL A COMPRESSOR PAD¿. A NEW LOCATE WAS ISSUED ON 10/17/08 AND UPDATED ON 10/29/08 WHICH ALSO STATED TYPE OF WORK AS ¿CLEARING TO INSTALL A COMPRESSOR PAD¿ (#80441251 AND #80459406). THE LOCATES DID NOT INDICATE THAT DURRETT WOULD BE DIGGING TO BURY DEBRIS. ON 9/25/08, IN RESPONSE TO THE ORGINAL ONE CALL LOCATE, JIM NASS AND TODD WOODWARD (REGENCY EMPLOYEES) MARKED THE S ELM GROVE 12¿ PIPELINE WITH YELLOW PIN FLAGS AND THE ROW WAS MARKED BY SURVEYOR STAKES. DURING THE CONSTRUCTION OF THE COMPRESSOR STATION PAD, DURRETT CONSTRUCTION PILED DEBRIS (TREES, LIMBS, ETC) ON THE S ELM GROVE 12¿ ROW. TODD WOODWARD CONTACTED PETROHAWK 3 TIMES DURING THE WEEK PRIOR TO THIS INCIDENT (ED LARY ON 10/30/08, LANE JOHNSON ON 10/31/08 AND JEFF MOODY ON 11/4/08) AND REQUESTED TO HAVE THIS DEBRIS REMOVED FROM OUR ROW. AT NO TIME DURING HIS CONVERSATIONS WITH ANY OF THE PETROHAWK EMPLOYEES, WAS BURYING THE DEBRIS MENTIONED. DURRETT CONSTRUCTION RECEIVED INSTRUCTIONS FROM LANE JOHNSON (PETROHAWK) TO BURY THE DEBRIS. WILLIAM RABO (DURRETT EMPLOYEE) WAS SENT TO THE LOCATION TO BURY THE DEBRIS ON 11/5/2008. HE WAS USING A TRACKHOE, WORKING ALONE AND DID NOT HAVE A SPOTTER OR SUPERVISOR. BY THIS TIME, THE MAJORITY OF THE YELLOW PIN FLAGS AND ROW STAKES HAD BEEN DISTURBED AND WERE NO LONGER VISIBLE ON THE PIPELINE OR ROW IN THE IMMEDIATE DIGGING AREA DUE TO THE CLEARING AND PILING OF DEBRIS ON THE ROW. REGENCY¿S PIPELINE MARKER AT THE ROAD (100 FEET FROM INCIDENT) WAS KNOCKED DOWN AND PARTIALLY COVERED IN DIRT. RABO WAS AWARE THAT THERE WAS A PIPELINE NEAR THE LOCATION. THE ONLY PIPELINE MARKERS THAT WERE STILL VISIBLE WERE YELLOW PIN FLAGS ON THE NORTH SIDE OF THE LOCATION AND A ROW STAKE ON THE SOUTH SIDE OF THE LOCATION. HE ASSUMED THAT THE PIPELINE WAS IN A STRAIGHT LINE BETWEEN THESE MARKERS. THIS WOULD HAVE PLACED THE PIPELINE ON THE EAST SIDE OF THE DEBRIS PILE. IN REALITY, THE PIPELINE CURVED BETWEEN THESE MARKERS. RABO DUG A HOLE AND BURIED SOME DEBRIS TO THE WEST OF THE PIPELINE. HE THEN MOVED EAST OF HIS ORIGINAL HOLE AND BEGAN TO DIG. AT THIS POINT, HE WAS DIGGING DIRECTLY OVER THE S ELM GROVE 12¿ PIPELINE. AT 8:52 AM RABO HIT THE PIPELINE WITH THE TRACKHOE BUCKET AND RUPTURED THE PIPELINE. HE IMMEDIATELY JUMPED FROM THE TRACKHOE AND RAN EAST (LEAVING THE TRACKHOE RUNNING). THE BUCKET ON THE TRACKHOE DEFLECTED THE GAS AWAY FROM THE TRACKHOE. RABO WAS NOT INJURED. THE GAS DID NOT IGNITE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080140 | 2008-11-21 09:44 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1653 | 2008-10-28 | 2008 | COBLESKILL | SCHOHARIE | NY | 12043 | LINE 200-1, 249-1 + 2.62 | 138+11 | 42.7434 | -74.3535 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | ANOMALY IN A DENT ON BOTTOM OF PIPE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51002 | 25321.5346 | 41847.1723 | 24752 | 9248.2963 | 26250 | 32598.876 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 888463 | 2008-10-28 | 598 | 760 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 24 | 0.28 | API 5L | 52000 |  |  | REPUBLIC | 1951 | UNDER GROUND |  | 44 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | PIPELINE WAS RESTING UNDERGROUND ON LARGE ROCK THAT APPARENTLY RESULTED IN ABRASION OVER TIME, LEADING TO A CRACK IN A DENT. |  | TENNESSEE GAS PIPELINE COMPANY PERSONNEL HAD ISOLATED A SECTION OF ITS 200-1 PIPELINE TO INVESTIGATE ANOMALIES INDICATED DURING A RECENT SMART PIG RUN. UPON EXCAVATION OF ONE OF THE ANOMALY SITES, A SMALL LEAK WAS DISCOVERED ON THE BOTTOM OF THE PIPE THAT APPARENTLY RESULTED FROM ABRASION CAUSED BY ROCK IN CONTACT WITH THE PIPE. PERSONNEL CUT OUT DAMAGED PIPE AND INSTALLED NEW PIPE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20080141 | 2008-11-24 15:42 | SUPPLEMENTAL | 11272 |  | LAVACA PIPELINE CO | 103 FANIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 | 1050 | 2008-09-22 | 2008 | POINT COMFORT | CALHOUN | TX | 77978 |  |  | 28.6419 | 96.5435 | OFFSHORE |  | LAVACA BAY | 26 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 884858 | 2008-09-22 | 450 | 600 | NO | YES | NO | NO | NO | NO | ROBERT C. SERRATA | 3619878914 | ROBERTS@FTPC.FPCUSA.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1954 | 10 | 0.37 | UNKNOWN | 24000 | SEAM LESS |  | UNKNOWN |  | UNDER WATER |  | 108 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWD | YES | 1952 | NO | [57 empty] | LEAK WAS CAUSED BY INTERNAL CORROSSION. CORRISION INHEBITER ARE BEING INJECTED INTO THE PIPELINE AT THE PRESCRIBED AMOUNT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080142 | 2008-11-25 15:07 | SUPPLEMENTAL FINAL | 31846 |  | CAROLINA GAS TRANSMISSION | 601 OLD TAYLOR ROAD | CAYCE | LEXINGTON | SC | 29033 | 1820 | 2008-11-16 | 2008 | COLUMBIA | RICHLAND | SC | 29229 | 67.5 | 3575.10 | 34.09087 | -80.55917 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 38702.1554 | 71434.0558 | 25000 | 9340.9586 | 50000 | 62093.0972 | 0 | 0 | YES | NO | NO | YES | 30 | PRECAUTIONARY | 0 | 55 | 890375 | 2008-11-18 | 852 | 974 | NO | YES | NO | NO | NO | NO | LAURA COMSTOCK | 8032172199 | LCOMSTOCK@SCANA.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1967 | 12 | 0.22 | API 5L | 52000 | ERW |  | STUPP | 1967 | UNDER GROUND |  | 84 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 10 | 31 | 1967 | WATER |  | 24 | 1364 | [12 empty] | A MEMBER OF THE PUBLIC REPORTED A SMELL OF GAS INTO RICHLAND COUNTY 911. THE LOCAL DISTRIBUTION COMPANY RESPONDED, DETERMINED THE SMELL WAS ORIGINATING FROM OUR RIGHT OF WAY AND NOTIFIED US AT 6:20 P.M. ON 11/16/08. THE FIRE DEPARTMENT CLOSED THE NEARBY ROAD BY 6:40. WE LOCATED THE SOURCE OF THE LEAK AND ISOLATED THE LINE AND DEPRESSURIZED 13 MILES OF PIPE. THE LEAK WAS STOPPED BY 2:00 A.M. ON 11/17/08 AND THE ROAD WAS RE-OPENED TO TRAFFIC. UPON EXCAVATION, IT WAS DETERMINED THAT THE LEAK WAS CAUSED BY A CRACK IN A CIRCUMFERENTIAL WELD ON THE BOTTOM OF THE PIPE WHERE THE MAINLINE WAS APPARENTLY TIED IN AT A ROAD CROSSING DURING ORIGINAL CONSTRUCTION IN 1967. A CUTOUT REPAIR WAS MADE THE FOLLOWING DAY AND THE LINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080143 | 2008-12-02 13:10 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1414 | 2008-11-05 | 2008 |  | PIKE | PA |  |  | 7382+82 | 41.33269870 | 74.84080223 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1849692 | 1012702.2278 | 2154673.4337 | 164000 | 61276.6885 | 1685692 | 2093396.7452 | 0 | 0 | NO | NO | NO | YES | 0 | PRECAUTIONARY | 0 | 30 | 889241 | 2008-11-05 | 986 | 1000 | NO | NO | NO | NO | YES | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 14 | 0.31 | X42 | 45000 |  |  |  |  | UNDER WATER |  | 6 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | BARE | OTHER | STRESS CORROSION CRACKING | STRESS CORROSION CRACKING |  | YES | 1970 | NO | [57 empty] | PIPELINE 1278 WAS UNDERGOING A RESTORATION OF THE PREVIOUSLY ESTABLISHED MAOP. THE PRESSURE RESTORATION PLAN WAS COMPLETED SUCCESSFULLY WHERE TEH PIPELINE WAS BEING PATROLLED UPON EACH INCREMENTAL INCREASE OF 50 PSIG FROM 800 PSIG TO 1000 PSIG. UPON CONDUCITNG NECESSARY SAFETY CHECKS, NO LEAKS WERE DETECTED BY THE LEAK DETECTION INSTRUMENTS. AFTER SEVERAL HOURS FROM THE COMPLETION TO THE PRESSURE RESTORATION PROCEDURE, THE PIPELINE EXPERIENCED A RUPTURE DUE TO AN UNIDENTIFIED REASON. A THOROUGH INVESTIGATION IS TAKING PLACE TO IDENTIFY THE ROOT CAUSE TO THIS INCIDENT. ======================== THE FAILURE WAS CAUSED BY NEAR-NEUTRAL-PH STRESS CORROSION CRACKING IDENTIFIED BY AN INVESTIGATIVE CONSULTANT. A TOTAL OF 510 FEET REPLACED THE RUPTURED SECTION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080144 | 2005-11-17 | ORIGINAL FINAL | 30910 |  | K O TRANSMISSION COMPANY | 139 EAST FOURTH STREET | CINCINNATI | HAMILTON | OH | 45202 | 2008 | 2005-09-10 | 2005 |  | CAMPBELL | KY |  | 461.7 |  | 39.053876 | -84.431838 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141000 | 85269.7338 | 189466.7279 | 0 | 0 | 141000 | 189466.7279 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 772071 | 2005-09-10 | 300 | 388 | NO | NO | YES | NO | NO | NO | SUSAN M. GILB / REGULATORY COMPLIANCE SPECIALIST | 5132872752 | SGILB@CINERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 12 | 0.5 | API 5L |  | ERW | N/A | UNKNOWN |  | UNDER GROUND |  | 180 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | GALVANIC |  | YES |  | NO | [57 empty] | A SMALL GAS LEAK OCCURRED UNDER THE RIVERBED APPROX. 80' FROM THE SHORELINE OF THE OHIO RIVER. THERE WAS 15' OF COVER TO THE PIPELINE IN 15' OF WATER. THE REASON FOR REPORTING THIS INCIDENT WAS DUE TO THE COAST ASSOCIATED WITH HIRING AN EXCAVATION CONTRACTOR AND DIVERS TO MAKE THE REPAIR IN A COMMERCIALLY NAVIGABLE WATERWAY.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080145 | 2008-12-05 11:04 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 940 | 2008-11-19 | 2008 | HOUMA | TERREBONNE | LA | 70360 | 131.00 |  | 29^16'17.7 | 91^10'36.96 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | BOLTS AT FLANGE CORRODED INTERNALLY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101990 | 50797.4323 | 84771.7886 | 48243 | 18025.4346 | 53747 | 66746.3539 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 890442 | 2008-11-19 | 1440 | 1440 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | OTHER | VALVE | STEEL |  | NO | NO | NO | OTHER | VALVE | 1967 | 12 |  |  |  |  | BALL | COOK | 1967 | OTHER | ON PLATFORM |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | UNDETECTABLE SEVERE CORROSION TO BOLTS HOLDING BODY FLANGE. THE BOLTS WHICH HOLD THE BODY FLANGE ONTO THE 12 INCH COOK VALVE WERE SEVERLY CORRODED INTERNAL OF THE FLANGE, FAILED. THE BOLTS WERE CORRODED INTERNALLY OF THE VALVE AND WAS UNDETECTABLE. |  | A TECHNICIAN DISCOVERED A LEAKING FLANGE ON THE MOSQUITO BAY PLATFORM DURING ROUTINE MAINTENANCE. THE VALVE WAS REMOVED FROM THE SYSTEM AND BLIND FLANGES INSTALLED.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20080146 | 2008-12-09 16:48 | SUPPLEMENTAL FINAL | 22655 |  | WILLISTON BASIN INTERSTATE PIPELINE CO | 1250 WEST CENTURY AVENUE | BISMARCK | BURLEIGH | ND | 58501 | 1312 | 2008-11-10 | 2008 | SAVAGE | RICHLAND | MT | 59262 | SOUTH OF MP 71.44 | 3773+86 | 47.4698N | 104.3596W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 41100 | 20784.3408 | 36280.7247 | 17000 | 6351.8519 | 4100 | 5091.634 | 20000 | 24837.2389 | NO | NO | NO | NO | 0 |  |  | 43 | 889655 | 2008-11-10 | 390 | 450 | NO | NO | NO | NO | YES | NO | CRAIG WAGNER | 4063597216 | CRAIG.WAGNER@WBIP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 12 | 0.25 | API 5L STD A | 25000 | FURNACE LAP WELD |  | YOUNGSTOWN SHEET AND TUBE | 1928 | UNDER GROUND |  | 40 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | THIS INCIDENT OCCURRED WHEN A CONTRACT TRACKHOE OPERATOR STRUCK WBI'S PRESSURIZED PIPELINE. THE LINE HAD BEEN PREVIOUSLY LOCATED AND MARKED BY WBI PERSONNEL. THE CONTRACTOR HAD VERIFIED THE LOCATE AND REMARKED PRIOR TO THE TRACKHOE OPERATOR DIGGING IN THE WRONG PLACE. THE CONTRACTOR WAS CONSTRUCTING A NEW PIPELINE INTENDED TO REPLACE THE OLD LINE THAT WAS STRUCK. SECTION F3 EXCAVATION NUMBER "8" WAS MARKED AS THE APPARENT CAUSE HOWEVER IT MAY ALSO BE CONSIDERED "9. THIRD PARTY EXCAVATION DAMAGE". ALSO THE MATERIAL LISTED IN PART "D" IS A BEST ESTIMATE BASED ON OUR RECORDS. THIS WAS A "RECONDITIONED" PIECE OF PIPE THAT WAS HIT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20080147 | 2008-12-12 14:57 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC | 445 W. MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 935 | 2008-11-13 | 2008 | LUSBY | CALVERT | MD | 20657 |  |  | 38 23 21.08 N | 76 24 55.05 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231000 | 99524.0431 | 87178.6811 | 230000 | 85936.8192 | 1000 | 1241.8619 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 889931 | 2008-11-13 | 910 | 1250 | YES | NO | NO | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN.A.MILLER@DOM.COM | TRANSMISSION | OTHER | 1" STUB CONNECTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 1 | 0.19 | [6 empty] | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | WHILE RECLAIMING SPOIL, DURING THE CONSTRUCTION OF TL-532, THAT WAS STORED OFF TO THE SIDE OF TL-522 ON A SLOPE BETWEEN THE FENCE FOR THE DOMINION COVE POINT LNG FACILITY AND RECEIVING PIT FOR GRAY'S CREEK BORE, A BULLDOZER WAS BELIEVED TO HAVE HIT 36" TL-522 AS GAS BEGAN TO BLOW FROM THE PIPE. ALL EQUIPMENT WAS SHUT OFF AND EMPLOYEES EVACUATED THE AREA AT AROUND 9:30 AM. DOMINION TRANSMISSION INC. (DTI) MANAGEMENT IN CLARKSBURG WAS CONTACTED ABOUT THE ACCIDENT AND BEGAN KEEPING CONSTANT CONTACT WITH STAFF AT COVE POINT BY PHONE UNTIL GARY BAKER; DTI¿S CONSTRUCTION SUPERVISOR ARRIVED ON SITE. AFTER LOWERING THE PRESSURE TO GET A BETTER LOOK AT THE DAMAGED AREA IT WAS DETERMINED THAT A ONE-INCH TAP WAS BROKEN OFF OF TL-522, AS YOU COULD SEE A ONE-INCH HOLE IN THE PIPE. LYING OFF TO THE SIDE WAS A SHORT PIECE OF ONE-INCH PIPE, A ONE-INCH VALVE, AND THEN ANOTHER PIECE OF ONE-INCH PIPE SEVERAL FEET LONG WITH PART STILL COVERED BY DIRT. BASED ON RECORDS FROM WHEN COLUMBIA GAS OWNED THE PIPELINE 30 YEARS AGO, DTI DETERMINED THAT COLUMBIA PUT THE TAP ON THE PIPELINE AS PART OF A LEAK DETECTION SYSTEM THAT WAS ONLY UTILIZED FOR A SHORT TIME. THE PIPELINE SECTION TO WHICH THE ONE-INCH TAP WAS CONNECTED IS APPROXIMATELY 7 MILES IN LENGTH AND ONLY ONE CUSTOMER TAP WAS CONNECTED IN THIS SECTION BEING A FEED TO WASHINGTON GAS & LIGHT (WGL) CALLED THE PATUXENT METER STATION. BY REDUCING THE PRESSURE FROM 910 PSIG TO 350 PSIG, DTI WAS ABLE TO KEEP FEEDING THE PATUXENT METER STATION TO KEEP WGL IN SERVICE. AFTER SEVERAL CONFERENCE CALLS ON HOW TO REPAIR THE BROKEN TAP AND STILL MAINTAIN 100% SERVICE TO WGL AT PATUXENT, DTI DECIDED TO CONTRACT IN LNG TANK TRUCKS TO FEED WGL WHILE THE TL-522 LINE WAS BLOWN DOWN AND THE BROKEN TAP REPAIRED. DTI FINISHED REPAIRING THE TAP AND PLACED TL-522 BACK IN SERVICE AT 6:30 A.M., ON SUNDAY MORNING THE 16TH OF NOVEMBER. NO SERVICE INTERRUPTIONS WERE EXPERIENCED BY WGL OR ITS CUSTOMERS BECAUSE OF THE LNG USED TO KEEP WGL¿S SYSTEM WHOLE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20080148 | 2008-12-17 10:20 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 930 | 2008-11-17 | 2008 | [6 empty] | 28.4.60 | 93.32.60 | OFFSHORE |  | HIGH ISLAND | 332 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6049025 | 3378892.704 | 7499117.4181 | 14900 | 5567.2113 | 6034125 | 7493550.2068 | 0 | 0 | NO | NO | NO | NO | 0 |  | 36 |  | 890245 | 2008-11-17 | 850 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858578002 | NGRAY@EPCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1988 | 10.75 | 0.44 | API 5L | 35000 |  |  |  |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | HURRICANE IKE, POSSIBLE THIRD PARTY DAMAGE INCLUDING ANCHOR DRAG. |  | THE 10" PIPELINE, MMS SEGMENT NUMBER 8299, PULLED AND RIPPED FORM THE SUBSEA TIE ASSEMBLY AT HIGH ISLAND 332. THIS SECTION OF PIPELINE WAS PULLED APPROXIMATELY 850 FEET SOUTH. FURTHER INVESTIGATION WILL NEED TO TAKE PLACE BY THE PIPELINE OWNER, GATEWAY, TO HELP DETERMINE WHAT MIGHT HAVE CAUSED THE INCIDENT. THE PIPELINE IS ISOLATED AT ITS BEGING POINT UNTIL REPAIRS ARE MADE. REPAIRED SUBSEA TAP, RECONNECTED PIPELINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080149 | 2008-12-17 17:56 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 840 | 2008-11-22 | 2008 | HUMPHREY | ARKANSAS | AR | 72160 |  | LINE T 3266+81 | 34.433906 | -91.692906 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | REGULATOR FREEZE UP -LOSS CUSTOMERS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3010 | 1682.2935 | 3738.0045 | 0 | 0 | 3010 | 3738.0045 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 890705 | 2008-11-22 | 820 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1984 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1) OR (2), BECAUSE THERE WAS NO RELEASE OF GAS. DURING THE EARLY MORNING OF NOVEMBER 22 A COMBINATION OF LOW TEMPERATURE AND A HEATER FAILURE RESULTED IN A REGULATOR FREEZING UP. THE FROZEN REGULATOR CAUSED THE OUTAGE OF 25 CUSTOMERS AND DUE TO THE WEATHER CONDITIONS THIS OPERATOR CONSIDERED IT TO BE SIGNIFICANT.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20080150 | 2008-12-19 11:07 | ORIGINAL FINAL | 31286 |  | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | TULSA | OK | 74103 | 1700 | 2008-08-18 | 2008 | VELMA | STEPHENS | OK | 73491 | NW/4 SEC 12 T1S R6W | N/A | N34.49212 | 097.78963 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | CRACK IN WELDING FITTING ON BRANCH CONNECTION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53705 | 26091.79 | 40205.5619 | 30509 | 11399.3322 | 23196 | 28806.2297 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 | 881471 | 2008-08-18 | 640 | 725 | NO | NO | YES | NO | NO | NO | PATTI FORD | 9185887131 | PATTI.FORD@ONEOK.COM | TRANSMISSION | OTHER | CRACK IN WELDING FITTING ON BRANCH CONNECTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 20 | 0.31 | X-42 | 42000 | SEAMLESS | N/A | UNKNOWN |  | UNDER GROUND |  | 42 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | BRANCH |  |  |  | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 12 | 5 | 1952 | WATER |  | 0 | 620 | [12 empty] | NOTE FOR F5(E.): LINE WAS TESTED TO 620 PSI BUT RECORDS ARE UNCLEAR AS TO THE DURATION OF THE PRESSURE TEST. THIS FORM WAS NOT ORIGINALLY FILED WITH PHMSA AS THE ORIGINAL TOTAL COST FOR THE INCIDENT WAS $45,838.77. THE COST OF GAS WAS RECENTLY ADJUSTED THEREBY INCREASING THE GAS LOSS COST BY $7,866.01. THEREFORE, THE NEW TOTAL COST OF THIS INCIDENT IS NOW $53,704.78. THIS NOW MAKES THIS INCIDENT REPORTABLE TO PHMSA. A LATERAL PIPELINE WAS REMOVED ABOUT THIRTY YEARS AGO. THE REMOVAL PROCESS DID NOT REMOVE THE LATERAL BACK TO THE 20 INCH PIPE BUT LEFT A 6 FOOT LATERAL LINE STUB. THIS STUB APPEARS TO HAVE EXERTED STRESSES ON THE WELD AT THE TOP OF THE CONNECTION WHERE THE LATERAL WAS CONNECTED TO THE TRANSMISSION LINE. THE STUB WAS NOT SUPPORTED.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090001 | 2009-01-09 13:30 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1035 | 2009-01-05 | 2009 | [6 empty] | 2815,296 | 9619.536 | OFFSHORE |  | MI | 559 | TX | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370000 | 205571.8612 | 440271.9543 | 20000 | 10586.4198 | 350000 | 429685.5346 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 894002 | 2009-01-05 | 900 | 1250 | NO | YES | NO | NO | NO | NO | JAMES R. MCDONALD | 7133812494 | JMCDONALD@EPCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 | 0.38 | API 5LX 42 | 42000 |  |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNKNOWN | YES | 1983 | NO | [57 empty] | PIN HOLE LEAK IDENTIFIED ON PIPELINE. CLAMP WAS INSTALLED OVER LEAK, HOWEVER UPON REVIEW IT APPEARS LEAK IS LOCALIZED PITTING. FLOW VOLUME ON THIS LINE IS MINIMAL AND ALTHOUGH LINE IS TREATED WITH CHEMICAL FOR INTERNAL PROTECTION, WE CANNOT BE CERTAIN OF FULL COVERAGE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090002 | 2009-01-11 20:36 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1632 | 2008-12-12 | 2008 | HOT SPRINGS VILLAGE | GARLAND | AR | 71909 |  | LINE BT-1-AS 1360+27 | +34.639150 | -93.05769 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | 1" DOMESTIC TAP BROKEN OFF AT OUTLET OF BV | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11876 | 5624.5167 | 7910.2234 | 7876 | 2942.7756 | 4000 | 4967.4478 | 0 | 0 | YES | NO | NO | NO | 0 |  | 2 | 2 | 892371 | 2008-12-12 | 875 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | TAP RISER FOR DOMESTIC M/R | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1990 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE A STATE HIGHWAY WAS CLOSED BY EMERGENCY RESPONDER PERSONNEL. AT APPROXIMATELY 16:32 HRS ON DECEMBER 12, 2008 A HIGHWAY CONSTRUCTION VEHICLE BACKED THROUGH A 2¿ BARRICADE AND OVER A TAP RISER AND REGULATOR/METERING SYSTEM BREAKING A 1¿ PIPE NIBBLE FROM THE OUTLET OF THE ABOVE GROUND BLOCK VALVE CAUSING A GAS RELEASE. THE EQUIPMENT OPERATOR NOTIFIED THE CENTERPOINT ENERGY GAS TRANSMISSION (CEGT) CONTROL CENTRAL AND THEY DISPATCHED COMPANY PERSONNEL TO THE SITE. EMERGENCY RESPONDERS CLOSED STATE HIGHWAY 7 DUE TO THE LOCATION OF THE ESCAPING GAS BEING WITHIN 150 FEET OF THE HIGHWAY. CEGT PERSONNEL WERE ABLE TO CLOSE A VALVE TO SECURE THE GAS RELEASE AND THE SITE WAS MADE SAFE AT 18:35 HRS. SINCE THERE HAVE NOT BEEN ANY CUSTOMERS ATTACHED TO THIS DOMESTIC TAP FOR THE PAST 12 MONTHS THE RISER WAS REMOVED AND THE BELOW GROUND VALVE WAS PLUGGED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090003 | 2009-01-12 09:05 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC | 445 W. MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 1400 | 2008-12-12 | 2008 | CHURCHVILLE | LEWIS | WV | 26338 |  |  | 39.108182 | -80.583919 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 19783.6944 | 32310.0058 | 20000 | 7472.7669 | 20000 | 24837.2389 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 892334 | 2008-12-12 | 900 | 1050 | YES | NO | NO | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN.A.MILLER@DOM.COM | TRANSMISSION | OTHER | WELDOLET | STEEL |  | NO | NO | NO | PIPELINE |  | 1993 | 2 | [7 empty] | UNDER GROUND |  | 48 | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | FITTING |  |  |  | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | NO | [19 empty] | A LEAK WAS DISCOVERED IN THE FILLET WELD OF A 2" WELDOLET ON THE BOTTOM OF PIPELINE TL344. THE CAUSE WAS DETERMINED TO BE A CRACK, WHICH HAD FORMED DUR TO THE PIPE SETTLEING ON THE 2" FITTING. THE CRACK HAD PROPAGATED INTO THE 20" CARRIER PIPE, THEREFORE A 3' SEGMENT OF 20" PIPE WAS REMOVED AND REPLACED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090004 | 2009-01-20 15:13 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 1330 | 2008-12-30 | 2008 | ROLLING FORK | ISSAQUENA | MS | 39159 | 58.771 | NORTH MAIN LOOP PIPELINE | 32.693921 | -91.024476 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK IN VALVE BODY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71954 | 37678.5886 | 72233.8285 | 19722 | 7368.8954 | 52232 | 64864.9331 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 893669 | 2008-12-30 | 408 | 500 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1946 | 22 | 0.25 | API 5L OR EQUIV. | 42000 | FLASH WELD | GATE | CRANE | 1946 | OTHER | IN A GATE BOX BELOW GRADE | 0 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | LANDOWNER HEARD A SOUND INDICATING A GAS LEAK AND CONTACTED SOUTHERN NATURAL GAS COMPANY GAS CONTROL. LOCAL TECHNICIANS WERE DISPATCHED AND CONFIRMED GAS LEAKING FROM NEAR A VALVE GATE BOX. FURTHER INVESTIGATION REVEALED A CRACK IN THE VALVE BODY AS THE CAUSE OF THE LEAK. A MAINTENANCE CREW REPLACED THE VALVE WITH A JOINT OF 22" PIPE AND PLACED THE PIPELINE SEGMENT BACK IN SERVICE JANUARY 6, 2009.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090005 | 2009-01-22 15:30 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 230 | 2008-12-26 | 2008 | FRANKLIN | ST. MARY | LA | 70538 | LINE 300 VALVE 1207 |  | 29.73864 | -91.44587 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86350 | 37154.9564 | 32263.671 | 86350 | 32263.671 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 35 | 893355 | 2008-12-26 | 839 | 840 | NO | YES | NO | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | OTHER | RELIEF VAVLE ACTIVATED | STEEL |  | NO | NO | NO | PIPELINE |  | 2005 | [5 empty] | D-3 S/N 3632 | AXELSON | 1986 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | GAS SUPPLY EXCEEDED MARKET CAUSING OVERPRESSURE AND ACTIVATION OF RELIEF VALVE. |  | RELIEF VALVE ACTIVATED AT SET PRESSURE AND BLEW GAS FOR APPROXIMATELY 35 MINUTES. RELIEF VALVE SET AT 839 PSIG FOR 840 PSIG MAOP. DUE TO HOLIDAYS, MARKET REQUIREMENTS HAD FALLEN.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090006 | 2009-01-28 10:37 | SUPPLEMENTAL FINAL | 31336 |  | CHEVRON U.S.A. INC | 100 NORTHPARK BLVD | COVINGTON | ST. TAMMANY | LA | 70433 | 1345 | 2009-01-01 | 2009 |  |  | GM |  |  |  | 29.13639 | -89.7175 | OFFSHORE |  | WEST DELTA | 32/33 | GM | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109800 | 613741.061 | 1355627.5973 | 9800 | 5187.3457 | 1100000 | 1350440.2516 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 893794 | 2009-01-01 | 50 | 960 | YES | NO | NO | NO | NO | NO | ERIN DUNAWAY | 9857736554 | ERIN.DUNAWAY@CHEVRON.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 26 | 0.58 | API-5LX-T52 | 52000 | SEAMLESS | N/A | U.S. STEEL (LORIAN, OHIO) | 1965 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL CORROSION | OTHER | EROSION / CORROSION | YES | 1966 | NO | [57 empty] | AFTER THE LEAK WAS DISCOVERED ON JANUARY 1, 2009 (NRC #893794), A TEMPORARY CLAMP WAS INSTALLED AND A LEAK TEST WAS PERFORMED. A SECOND LEAK WAS DISCOVERED ON JANUARY 9, 2009 (NRC #894371 - SEE SUBSEQUENT REPORT #20090007) DURING THE LEAK TEST. DURING A FLYOVER, 3 ADDITIONAL LEAKS WERE OBSERVED. DIVERS HAVE FOUND A TOTAL OF 6 LEAKS ALONG THE LINE. AS OF 1/15/09, DIVERS HAVE INSTALLED 2 REPAIR CLAMPS (AVAILABLE INVENTORY) AND 4 TEMPORARY PATCHES TO PREVENT FURTHER HYDROCARBON RELEASE WHILE ASSESSING FUTURE PIPELINE UTILITY. BELOW ARE THE ESTIMATED LEAK HOLE SIZES. NOTE THAT HOLE SIZES ARE ESTIMATED BY DIVERS DUE TO VISIBILITY RESTRICTIONS AT THE TIME OF INSPECTIONS. LEAK #1 - 1" HOLE LEAK #2 - 1/4" HOLE LEAK #3 - 3/4" HOLE LEAK #4 - 3/16" HOLE LEAK #5 - 1/2" HOLE LEAK #6 - 3/4" HOLE UPDATE: AS OF 6/1/2009, OPERATOR OF PIPELINE IS VENICE GATHERING SYSTEM, LLC. ACCORDING TO MMS PIPELINE PERMITS DATABASE, APPLICATION TO DECOMMISSION PIPELINE AND RELINQUISH RIGHT-OF-WAY SUBMITTED ON 9/2/09 AND APPROVED BY MMS ON 9/30/2009.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090007 | 2009-01-28 10:54 | SUPPLEMENTAL FINAL | 31336 |  | CHEVRON U.S.A. INC | 100 NORTHPARK BLVD | COVINGTON | ST. TAMMANY | LA | 70433 | 612 | 2009-01-09 | 2009 |  |  | GM |  |  |  | 29.13583 | -80.71806 | OFFSHORE |  | WEST DELTA | 32/33 | GM | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 894371 | 2009-01-01 | 100 | 960 | YES | NO | NO | NO | NO | NO | ERIN DUNAWAY | 9857736554 | ERIN.DUNAWAY@CHEVRON.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 26 | 0.58 | API-5LX-T52 | 52000 | SEAMLESS | N/A | U.S. STEEL (LORIAN, OHIO) | 1965 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL CORROSION | OTHER | EROSION / CORROSION | YES | 1966 | NO | [57 empty] | THIS REPORT IS A SUBSEQUENT REPORT TO F7100.2 REPORT #20090006. SEE NARRATIVE DESCRIPTION IN REPORT #20090006. TOTAL ESTIMATED PROPERTY DAMAGE / LOSS DOLLAR AMOUNT FOR THIS REPORT AND #20090006 IS PROVIDED IN REPORT #20090006. UPDATE: AS OF 6/1/2009, OPERATOR OF THIS PIPELINE IS TARGA RESOURCES INC ON BEHALF OF VENICE GATHERING SYSTEM, LLC. PER THE MMS PIPELINE PERMITS DATABASE, APPLICATION TO DECOMMISSION THIS LINE AND RELINQUISH RIGHT-OF-WAY WAS SUBMITTED 9/2/09 AND WAS APPROVED BY MMS ON 9/30/09.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090008 | 2009-01-28 11:23 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 700 | 2009-01-07 | 2009 |  |  | LA |  |  |  | 28* 27' 28 | 91* 47' 47 | OFFSHORE |  | EUGENE ISLAND | 266 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125000 | 71917.0743 | 118541.5211 | 50000 | 26466.0494 | 75000 | 92075.4717 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 894180 | 2009-01-07 |  | 1250 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 12.75 | 0.38 | API 5X | 46000 |  |  | UNKNOWN | 1970 | OTHER | ABOVE WATER |  | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1970 | NO | [57 empty] | ON JANUARY 7, 2009, ANR CONFIRMED A SMALL LEAK AT THE E.I. BLK. 266C PLATFORM, ON ITS 12-INCH LINE 750. THE LEAK IS LOCATED ABOVE WATER AT THE CELLAR DECK. A DIVER WAS SENT TO CLOSE THE VALVE AT THE BASE OF THE RISER. EXTERNAL CORROSION IS THE SUSPECTED CAUSE. A WELDED SLEEVE IS GOING TO BE USED FOR THE REPAIR. THE REPAIR HAS BEEN SCHEDULED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090009 | 2009-01-28 17:18 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 600 | 2009-01-08 | 2009 | GRANITE FALLS | SNOHOMISH | WA |  | 1415.828 | 18564+64 | 48.096178N | -122.064514W | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128035 | 72023.7124 | 141488.2497 | 22477 | 11897.5478 | 105558 | 129590.7019 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 894343 | 2009-01-08 | 740 | 960 | NO | YES | NO | NO | NO | NO | BOYD SCHOW | 8015846741 | BOYD.SCHOW@WILLIAMS.COM | TRANSMISSION | OTHER | GIRTH WELD | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 30 | 0.4 | X-60 |  | SUB ARC |  | REPUBLIC STEEL | 1971 | UNDER GROUND |  | 66 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 8 | 14 | 1971 | WATER |  | 13 | 1680 | [12 empty] | LEAK SECTION WAS CUT OUT AND SENT TO ANTECH TECH IN HOUSTON FOR ANALYSIS. ANALYSIS REPORT HAS NOT BE RECEIVED BACK AS OF THIS TIME. UPDATED REPORT 9/28/2009: A SECONDARY ANALYSIS WAS COMPLETED BY STRESS ENGINEERING SERVICES INC. IN HOUSTON, TEXAS WITH A WRITTEN REPORT DATED SEPTEMBER 14, 2009. THIS REPORT WAS FORWARDED TO PETER KATCHMAR (DOT)ON SEPTEMBER 15, 2009. THIS ANALYSIS STATES, "WE BELIEVE THIS LEAK WAS CAUSED BY A COMBINATION OF FACTORS: FAILURE TO PROPERLY CROP OR CONDITION THE INGOT OR PLATE AND FAILURE TO REMOVE THE ORIGINAL SUCK-BACK INDICATION FROM THE WELD. HAD EITHER CONDITION BEEN ABSENT, WE BELIEVE IT IS UNLIKELY THAT THE LEAK WOULD HAVE OCCURRED."
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090010 | 2009-02-02 11:12 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACCORKLE AVENUE | CHARLESTON | KANAWHA | WV | 25314 | 1530 | 2009-01-04 | 2009 | ELKVIEW | KANAWHA | WV | 25071 | LINE X52CW7329 |  | 38.44811 | -81.44553 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 480 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29011 | 17684.1744 | 15356.1312 | 29011 | 15356.1312 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 893963 | 2009-01-04 | 1700 | 1800 | NO | NO | YES | NO | NO | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 6.63 | 0.28 | UNKNOWN | 35000 | ERW |  | UNKNOWN | 1956 | UNDER GROUND |  | 24 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | SULFUR AND CHLORIDE CONTAINING COMPOUNDS | YES | 1970 | NO | [57 empty] | FAILURE INVESTIAGTION SHOWED THAT THE CAUSE OF FAILURE FOR THIS PIPE WAS INTERNAL CORROSION PITTING COMPLICATED BY LOW IMPACT TOUGHNESS OF THE PIPE MATERIAL. THE CORROSION PITTING IS THE RESULT OF SULFUR AND CHLORIDE CONTAINING COMPOUNDS, AND THIRD PARTY INVESTIGATOR SPECULATED THAT THE LOW POINT IN THE PIPELINE UNDER CREEK RETAINED FREE LIQUIDS. THIS LINE REMAINS OUT-OF-SERVICE AS OF MARCH 2010. FUTURE PLANS ARE TO REPLACE THE ENTIRE WELL LINE IN 2010. A MEANS FOR LIQUID REMOVAL WILL BE INCLUDED IN THE REPLACEMENT PROJECT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090011 | 2009-02-02 11:22 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 1910 | 2009-01-06 | 2009 | YAZOO CITY | YAZOO | MS | 39194 | 97.269 | NORTH MAIN LOOP PIPELINE | 32.82244 | -90.39205 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247796 | 137926.4867 | 291784.5762 | 17796 | 9419.7963 | 230000 | 282364.7799 | 0 | 0 | NO | NO | NO | YES | 15 | PRECAUTIONARY | 1 | 45 | 894157 | 2009-01-06 | 420 | 500 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1941 | 22 | 0.31 | API 5L OR EQUIV | 35000 | SEAMLESS |  | NATIONAL TUBE | 1941 | UNDER GROUND |  | 60 | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | WASHOUT | [52 empty] | A LOCAL LANDOWNER CONTACTED SOUTHERN NATURAL GAS COMPANY THE NIGHT OF JANUARY 6, 2009, TO REPORT A LOUD NOISE IN THE VICINITY OF THE COMPANY'S NORTH MAIN LOOP PIPELINE. A COMPANY TECHNICIAN RESPONDED AND CONFIRMED THAT A PARTIAL SEPARATION HAD OCCURRED IN THE PIPELINE CAUSING NATURAL GAS TO RELEASE. THE CAUSE SEEMS TO BE A WASHOUT OF SUPPORTING SOIL BENEATH THE PIPELINE AT A JOINT MADE BY A DRESSER COUPLING. HEAVY RAINS PRECEDED THIS EVENT AND APPEAR TO HAVE WASHED OUT ENOUGH SOIL IN THIS LOCATION OF LOW ELEVATION TO CAUSE THE PIPE TO SAG AND OPEN A PARTIAL CIRCUMFERENCE AT THE DRESSER JOINT. THE PIPELINE SEGMENT HAS BEEN REPAIRED AND RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090012 | 2009-01-30 | ORIGINAL | 9011 |  | J - W GATHERING CO | 2601 STONEMALL - FRIERSON RD. | FRIERSON | DESOTO | LA | 71027 | 949 | 2009-01-08 | 2009 | SHREVEPORT | CADDO | LA | 71106 |  |  | 32.3821983 | -93.6721191 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4366 | 2490.2169 | 4406.0713 | 1366 | 723.0525 | 3000 | 3683.0189 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 20 | 900121 | 2009-01-08 | 525 | 800 | NO | YES | NO | NO | NO | NO | MICHAEL G. GARDNER | 3189257330 | MGARNER@JWOPERATING.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 6 | 156 | 5LX42 |  | ERW | N/A | UNKNOWN | 1972 | UNDER GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | CONTRIBUTING FACTOR - APPEARS UNKNOWN PARTY DAMAGED PIPE DURING UNKNOWN EXCAVATION. ALSO NOTIFIED: LOUISIANA STATE POLICE LOUISIANA OFFICE OF CONSERVATION LOUISIANA DEPT. OF ENVIRONMENTAL QUALITY LOUISIANA DEPT OF NATURAL RESOURCES HOMELAND SECURITY + EMERGENCY PLANNING COMMITTEE
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090013 | 2009-02-13 09:56 | ORIGINAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 309 | 2009-01-14 | 2009 | BAKERSFIELD | KERN | CA |  | 0.00 |  | 35.3689 | -119.2076 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 27911.0471 | 57891.888 | 5000 | 2646.6049 | 35000 | 42968.5535 | 10000 | 12276.7296 | NO | NO | NO | YES | 20 | PRECAUTIONARY | 5 | 21 | 894781 | 2009-01-14 | 375 | 400 | NO | NO | NO | YES | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1963 | 4 |  |  |  |  | PLUG |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | ON JANUARY 14, 2009, AN ABOVE-GROUND HIGH PRESSURE REGULATOR STATION WAS DAMAGED WHEN A DRIVER LOST CONTROL OF HER VEHICLE ON THE ROADWAY, CRASHING THROUGH STEEL POSTS AND FENCING, SHEARING OFF A 4¿ VALVE. ESCAPING GAS FROM THE DAMAGED PIPING DID NOT IGNITE. EIGHT CUSTOMERS WERE OUT OF SERVICE AS A RESULT OF THIS INCIDENT. ALL REPAIRS WERE COMPLETED AND CUSTOMERS RESTORED THE SAME DAY. THIS INCIDENT MET PHMSA REPORTING REQUIREMENTS WHEN ESTIMATE OF DAMAGE, INCLUDING GAS LOST, EXCEEDED $50,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090014 | 2009-02-13 10:47 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 947 | 2009-01-18 | 2009 |  |  |  |  | 0.00 | 523M-2700 LINE | 28 21 12 | -91 23 65 | OFFSHORE |  | EUGENE ISLAND | 255 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500000 | 829629.3676 | 1831034.1544 | 15000 | 7939.8148 | 1485000 | 1823094.3396 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 895155 | 2009-01-18 | 850 | 1250 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1973 | 12.75 | 0.5 | API 5L | 42000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | WHILE REPRESSURING A PORTION OF TENNESSEE GAS PIPELINE'S OFFSHORE TRANSMISSION SYSTEM THAT HAD BEEN OUT OF SERVICE DUE TO DAMAGE INCURRED DURING HURRICANE IKE, BUBBLES WERE NOTICED ON THE WATER'S SURFACE INDICATING A LEAK IN THE COMPANY'S 12" 523M-2700 PIPELINE. THE LEAK WAS NEAR A PLATFORM WHERE A VALVE WAS IMMEDIATELY CLOSED TO ISOLATE THE LEAK. DIVERS WERE DISPATCHED TO THE LOCATION AND IDENTIFIED WHAT APPEARED TO BE DAMAGE TO A WELD AT A SUBSEA TIE-IN. THE PIPELINE WILL NOT BE REPAIRED AS IT IS TO BE ABANDONED DURING 2010.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090015 | 2009-02-19 16:01 | SUPPLEMENTAL FINAL | 32177 |  | CORNHUSKER ENERGY LEXINGTON, L.L.C. | 1111 EAST INDUSTRY DRIVE | LEXINGTON | DAWSON | NE | 68850 | 1131 | 2008-12-20 | 2008 | LEXINGTON | DAWSON | NE | 68850 |  |  | 40.766656 | -99.724553 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 546039.668 | 1155039.5846 | 100000 | 37363.8344 | 0 | 0 | 900000 | 1117675.7502 | NO | NO | YES | YES | 13 | COMPANY POLICY |  | 19 |  | 2008-12-20 | 300 | 100 | NO | YES | NO | NO | NO | YES | DOUGLAS J. GLAZE | 3083246800 | DOUGLASG@CORNHUSKERENERGY.COM | TRANSMISSION | JOINT |  | PLASTIC |  | NO | NO | YES | PIPELINE |  | 2005 | 6 | [7 empty] | UNDER GROUND |  | 60 | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | MULTIPLE REGULATOR MALFUNCTION INVOLVING PRESSURE CONTROL REGULATORS AND MONITOR REGULATORS. THE REGULATOR STATION WAS INSPECTED AND SERVICED AFTER THE INCIDENT BY RON FICHTNER WITH KAL INC. UTILITY OPERATIONS SERVICE AND HIS REPORT STATES THE FOLLOWING: "THE FAILURE OF THE REGULATORS AT CORNHUSKER ENERGY WAS CAUSED BY FREEZE OFF IN THE PILOT REGULATORS CAUSING THE OPERATING RUN REGULATORS TO FAIL OPEN AND OVER PRESSURING THE PLASTIC PIPELINE. THE INSPECTION OF THE FIRST CUT OPERATING REGULATOR RUN FOUND THE WORKING REGULATOR'S PILOT REGULATOR COMPLETELY FULL OF LIQUIDS CAUSING THE FREEZE OFF. THE PILOT REGULATOR SEAT WAS TORN WHICH COULD ALSO CAUSE THE REGULATOR TO FAIL IN AN OPEN POSITION. THE PILOT FILTER WAS ALSO INSPECTED AND IT TOO HAD LIQUIDS IN IT. THE MONITOR REGULATOR PILOT, IN THE FIRST CUT OPERATING REGULATOR RUN, HAD SOME LIQUID IN IT AND ALSO THE PILOT FILTER HAD TRACES OF LIQUID IN IT. THE DIAPHRAM OF THE MONITOR REGULATOR HAD SOME SEPARATION SPOTS AROUND THE CAGE SLOTS WHICH WOULD PREVENT 100% LOCK UP OF THE MONITOR REGULATOR. THE STAND BY REGULATORS OF THE FIRST CUT REGULATOR RUN HAD TRACES OF LIQUIDS IN TEH PILOTS OF BOTH THE WORKING AND MONITOR REGULATOR WITH TRACES OF LIQUID FOUND IN BOTH OF THE PILOT FILTERS. WELDING SLAG WAS FOUND IN THE CAGE SLOTS OF BOTH TEH OPERATING AND MONITOR REGULATORS WHICH WOULD PREVENT 100% LOCK UP OF THE REGULATORS. THERE WERE ALSO SMALL SPOTS OF DIAPHRAGM SEPARATION IN THE DIAPHRAGMS OF BOTH REGULATORS WHICH CAN PREVENT 100% LOCKUP. THE STRAINERS FOR THE FIRST CUT REGULATOR RUNS WERE ALSO INSPECTED. THEY WERE MODERATELY CLEAN WITH SOME PLUG GREASE FOUND ALONG WITH TRACES OF LIQUID IN THEM. THE INSPECTION OF THE SECOND CUT OPERATING REGULATOR RUN FOUND BOTH THE WORKING AND THE MONITOR REGULATOR PILOTS COMPLETELY FULL OF LIQUIDS CAUSING THE FREEZE OFF. THE FILTERS FOR BOTH OF THE PILOT REGULATORS WERE ALSO COMPLETELY FULL OF LIQUIDS. THE BODIES OF BOTH OF THE WORKING AND MONITOR REGULATORS HAD ICE CRYSTALS IN THE CAGE SCREEN. THERE WERE ALSO SMALL SPOTS OF SEPARATION IN BOTH REGULATORS WHICH CAN PREVENT 100% LOCKUP. THE STRAINER FOR THIS RUN WAS INSPECTED AND FOUND TO CONTAIN QUITE A BIT OF PLUG GREASE IN IT ALONG WITH TRACES OF LIQUID. THE INSPECTION OF THE SECOND CUT STAND BY REGULATOR RUN SHOWED NO GAS FLOW WHICH IS EXACTLY AS IT SHOULD HAVE BEEN. THE REGULATOR BODIES OF BOTH TEH WORKER AND MONITOR WERE CLEAN AND DRY AS WERE THE PILOTS AND THE PILOT FILTERS. THE STRAINER FOR THIS RUN WAS ALSO INSPECTED AND FOUND TO BE CLEAN AND DRY." FOLLOWING THE INSPECTION BY KAL INC. ALL REGULATORS WERE SERVICED AND REPAIRED. IN CONSIDERATION OF THE FINDINGS OF KAL INC., CORNHUSKER ENERGY HAS ADDED SAFETY MEASURES TO PREVENT SIMILAR INCIDENTS IN THE FUTURE. A FULL RELIEF POP-OFF HAS BEEN INSTALLED FOLLOWING THE REGULATOR STATION AND THE RELIEF IS SET TO A VALUE EQUAL TO THE MAOP OF THE PLASTIC LINE. IN THE EVENT OF OVERPRESSURIZATION DUE TO MULTIPLE REGULATOR FAILURE THE RELIEF WILL LIFT AND RELIEVE PRESSURE TO THE MAOP VALUE. IN ADDITION, WITH CONSIDERATION OF THE FINDINGS OF KAL INC., CORNHUSKER ENERGY HAS INITIATED COMMUNICATIONS WITH KINDER MORGAN IN AN EFFORT TO EXPLAIN THE FINDINGS OF THE REPORT.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090016 | 2009-02-24 15:08 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 630 | 2009-02-18 | 2009 | CORPUS CHRISTI |  | TX |  |  |  | 27DEG,51MIN,36SECS | -96DEG,33MIN,54SEC | OFFSHORE |  | MATAGORDA ISLAND | 686 | TX | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2283650 | 1283640.5995 | 2535652.6133 | 383650 | 203073.9969 | 1900000 | 2332578.6164 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 897807 | 2009-02-18 | 790 | 1250 | NO | YES | NO | NO | NO | NO | BYRON WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2007 | 24 | 0.75 | API 5L | 52000 | DSAW |  |  |  | UNDER WATER |  | 60 | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | OTHER | MECHANICAL COUPLING | [8 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 7 | 31 | 2007 | WATER |  | 4 | 2179 | [12 empty] | ON FEBRUARY 18, 2009, NORTHERN RECEIVED NOTIFICATION OF A POSSIBLE LEAK IN BLOCK 686 (OFFSHORE) IN MATAGORDO ISLAND. NOTIFICATION WAS MADE TO THE NRC (TICKET # 897807 DTD 2/18/09). ADDITIONAL NOTIFICATIONS WERE MADE TO THE COAST GUARD, MMS AND SW OPNS OF PHMSA. IT WAS DETERMINED THAT THE LEAK WAS ON NORTHERN'S 24-INCH PIPELINE (TOS80631). ACTIONS WERE TAKEN TO SHUT IN THE LINE AND MAKE SURE THAT ALL PLATFORMS WERE ISOLATED FROM THE LINE. PRELIMINARY INDICATIONS ARE THAT A MECHANICAL COUPLING ON A 24 INCH BYPASS PIPING, THAT WAS INSTALLED PRIOR TO REMOVAL OF PLATFORM 686, HAD SEPARATED FROM THE PIPELINE. THE ROOT CAUSE OF THE EVENT IS STILL UNDER INVESTIGATION. PLANS ARE CURRENTLY UNDERWAY TO EVALUATE NECESSARY REPAIRS AND DEVELOP A REPAIR PLAN. THIS REPORT IS BEING FILED AS THE COST OF REPAIRS AND GAS LOSS ARE DEFINATELY GOING TO EXCEED THE $50,000 REPORTING THRESHOLD LEVEL. THERE WAS NO FIRE, NO INJURIES, NO EXPLOSIONS AND NO EVACATIONS EXPERIENCED DURING THIS EVENT. ADDITIONAL SUPPLEMENTAL/FINAL REPORTS WILL BE FILED UPON COMPLETION OF THE INVESTIGATION AND FINAL COST OF REPAIRS IS DETERMINED. SUPPLEMENTAL REPORT - APRIL 27, 2009: A REPAIR PLAN HAS BEEN SUBMITTED AND APPROVED BY THE MINERALS MANAGEMENT SERVICE (MMS). BIDS HAVE BEEN RECEIVED FROM CONTRACTORS TO COMPLETE THE REPAIRS AND ARE CURRENTLY BEING EVALUATED. TO DATE IT HAS NOT BEEN DETERMINED WHAT WAS THE ROOT CAUSE. THE INTENT, DURING THE REPAIR PROCESS, IS TO BRING BACK TO SHORE ALL MATERIALS OF THE BYPASS PIPING AND TO CONDUCT A FAILURE ANALYSIS. IT IS EXPECTED THAT THIS WILL BE COMPLETED SOME TIME IN JUNE 2009, CONTINGENT UPON CONTRACTOR, MATERIALS AND WEATHER CONDITIONS. A FINAL REPORT WILL BE SUBMITTED UPON PROJECT AND FAILURE ANALYSIS COMPLETION. SUPPLEMENTAL REPORT: THE TOTAL ESTIMATED COST FOR GAS LOSS AND OPERATOR DAMAGE HAS BEEN UPDATED. COMPLETION OF THIS REPAIR WAS INCLUDED WITH TWO OTHER MMS APPROVED PROJECTS. AVAILABILITY OF CONTRACTORS, MATERIALS AND WEATHER CONDITIONS HAVE HAMPERED EXPEDITED COMPLETION OF REPAIRS. CURRENTLY PIPING IS BEING DE-WATERED AND BARRING ADVERSE WEATHER CONDITIONS IT IS POSSIBLE THAT THIS PROJECT WILL BE COMPELTED BY SEPTEMBER 1ST. THE PIPING WITH THE FAILED MECHANICAL COUPLING HAS BEEN RETREIVED AND IS BEING ANALYZED BY AN OUTSIDE LABORATORY TO ASSIST WITH DETERMINING THE ROOT CAUSE OF THE EVENT. A FINAL REPORT ON THIS EVENT WILL BE FILED UPON COMPLETION OF PROJECT AND CONCURRENCE ON THE ROOT CAUSE. FINAL REPORT: REPAIRS WERE COMPLETED AS OUTLINE IN A REPAIR PLAN THAT WAS SUBMITTED AND APPROVED BY THE MINERALS MANAGEMENT SERVICES (MMS). THE LINE WAS RETURNED TO SERVICE EFFECTIVE AUGUST 13, 2009. A FAILURE ANALYSIS WAS COMPLETED BY STORK TESTING & METALLURGICAL CONSULTING, INC. AFTER EXTENSIVE ANALYSIS AND TESTING IT APPEARS THAT THE FAILURE IS LIKELY TO BE ATTRIBUTABLE TO A COMBINATION OF FACTORS WHICH ARE AN INCOMPLETE ENGAGEMENT BY THE SLIP ANCHOR AROUND ITS CIRCUMFERENCE ON THE MECHNAICAL COUPLING, PIPE OVALITY AND IT'S STRENGHT. ALL BYPASS PIPING, THE FAILED COUPLING AND ANOTHER MECHANICAL COUPLING WERE REMOVED AND REPAIRS WERE COMPLETED BY INSTALLATION OF APPROXIMATELY 133 FEET OF NEW 24-INCH, PREFABRICATED, WELDS RADIOGRAPHED, COATED PIPING, WHICH WAS HYDRO TESTED ON SHORE TO A PRESSURE BETWEEN 2,150 AND 2,300 PSIG, WHICH IS 1.5 TO 1.6 OF MAOP WITH WATER PRIOR TO INSTALLATION/COMPLETION OF REPAIRS. NO FURTHER ACTIONS ARE PENDING OR BEING CONSIDERED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090017 | 2009-02-25 10:01 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1320 | 2009-02-02 | 2009 |  |  |  |  | 4494 | 523M-2300 | 28 19 | -91 24.76 | OFFSHORE |  | EUGENE ISLAND | 302 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1731541 | 975987.2641 | 1889723.0926 | 338000 | 178910.4938 | 1393541 | 1710812.5987 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 896422 | 2009-02-02 | 850 | 1250 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 30 | 0.75 | API 5L | 60000 |  |  |  | 1972 | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1972 | NO | [57 empty] | BUBBLES WERE REPORTED AT THE WATER'S SURFACE BY TENNESSEE GAS PIPELINE HELICOPTER DURING ROUTINE AERIAL PATROL. THIS WAS DETERMINED TO BE A LEAK ON COMPANY'S 30" 523M-2300 PIPELINE. DIVERS INSTALLED A CLAMP TO REPAIR THE LEAK WHICH WAS APPARENTLY CAUSED BY INTERNAL CORROSION IN A WELD AT THE 5 O'CLOCK POSITION ON THE PIPELINE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090018 | 2009-02-13 | ORIGINAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1040 | 2009-01-09 | 2009 |  | MATAGORDA | TX |  |  |  | N 29 29 0.92 | W 95 59 35.755 | OFFSHORE |  | BRAZOS | 445 L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 46963.8365 | 104352.2013 | 0 | 0 | 85000 | 104352.2013 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 894381 | 2009-01-09 | 350 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER VP-MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 3 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON OR ABOUT JANUARY 8, 2009, PANTHER BECAME AWARE OF A POTENTIAL LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 445-L. ON JANUARY 9, PANTHER WAS ABLE TO CONFIRM THE LEAK WAS ON ITS PIPELINE AND NOT ON A FLOW LINE IN AREA WHERE PRODUCER HAS BEEN CONDUCTING OPERATIONS. PINHOLE LEAK PROBLEM WAS DISCOVERED ON THE PANTHER PIPELINE. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE DURING REPAIRS. PANTHER REPAIRED THE PROBLEM WITH CLAMPS ON 1/11/09 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 1/12/09.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090019 | 2009-03-05 | SUPPLEMENTAL FINAL | 19269 |  | TGG PIPELINE LTD | 12377 MERIT DRIVE SUITE 300A | DALLAS | DALLAS | TX | 75251 | 1006 | 2009-02-11 | 2009 | CARTHAGE | PANOLA | TX | 75633 |  |  | 32.190442 N | 94..261342 W | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 89 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000000 | 5526298.2763 | 12262762.5204 | 20000 | 10586.4198 | 20000 | 24553.4591 | 9960000 | 12227622.6415 | YES | YES | YES | YES | 50 | PRECAUTIONARY | 3 |  | 09CA317 | 2009-02-11 | 750 | 1000 | NO | NO | NO | NO | YES | NO | CHARLES ROSS DIRECTOR OF REGULATORY AFFAIRS | 2142106958 | CROSS@TGGTHOLDINGS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1989 | 16 | 0.24 | X60 | 1762 |  |  | AMERICAN STEEL |  | UNDER GROUND |  | 120 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1989 | YES |  | 6 | [55 empty] | FOR PART F1 B. VISUAL EXAMINATION TGG WOULD LIKE TO ALSO CHECK "GENERAL CORROSION" AS AN ADDITIONAL CAUSE ON THIS FINAL REPORT. FOR PART F1 C. CAUSE OF CORROSION TGG WOULD LIKE TO ALSO CHECK "OTHER: WATER/CHLORIDES" AS AN ADDITIONAL CAUSE ON THIS FINAL REPORT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090020 | 2009-03-09 16:30 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 930 | 2009-02-17 | 2009 |  |  | LA |  |  |  | 29* 17' 31 | 91* 33' 51 | OFFSHORE |  | EUGENE ISLAND | 32 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659000 | 369813.0794 | 739201.2812 | 100000 | 52932.0988 | 559000 | 686269.1824 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 897733 | 2009-02-17 | 862 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 6.63 | 0.29 | API | 42000 | UNKNOWN |  | UNKNOWN |  | UNDER WATER |  | 12 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | WE WERE NOTIFIED OF A LEAK IN EUGENE ISLAND BLK 32, BY ENBRIDGE, VERY CLOSE TO OUR 6-IN. 795 PIPELINE. IT IS SUSPECTED THAT A VESSEL MAY HAVE DAMAGED OUR PIPELINE. THE PIPELINE WAS FOUND TO HAVE A DENT AND CRACK ON THE TOP OF THE PIPE, WITH A CUT CABLE IN NEAR PROXIMITY OF THE DAMAGE. THE PIPELINE WAS REPAIRED IN JANUARY, 2010 BY REPLACING A 51 FT. SECTION OF PIPE. THE PIPELINE WAS THEN PLACED BACK INTO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090021 | 2009-03-09 17:04 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1700 | 2009-01-09 | 2009 | BOSSIER CITY | BOSSIER | LA |  | STOCKWELL TB LINE FM-52 | 39+10 | +32.578508 | -93.635396 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CONTROLLER FROZE AND LOSS 450 CUSTOMERS | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9385 | 5185.3601 | 11521.7107 | 0 | 0 | 9385 | 11521.7107 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 896180 | 2009-01-29 | 100 | 1654 | NO | NO | NO | NO | YES | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | CONTROLLER | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1978 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | CONTROLLER FROZE | [10 empty] | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1) OR (2), BECAUSE THERE WAS NO RELEASE OF GAS. DURING THE EARLY MORNING OF JANAURY 29 LOW TEMPERATURE CAUSED A CONTROLLER FAIL SHUTTING THE REGULATORS RESULTING IN THE OUTAGE OF ABOUT 450 CUSTOMERS AND DUE TO THE WEATHER CONDITIONS THIS OPERATOR CONSIDERED IT TO BE SIGNIFICANT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090022 | 2009-02-19 | SUPPLEMENTAL FINAL | 15350 |  | DOMINION PEOPLES | 501 MARTINDALE | PITTSBURGH | ALLEGHENY | PA | 15212 | 1420 | 2009-01-15 | 2009 | ELIZABETH | ALLEGHENY | PA | 15037 |  |  | 40.21474 | -79.86105 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2455333 | 1361250.3132 | 2957546.8614 | 81333 | 43051.2639 | 2374000 | 2914495.5975 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 20 | 895016 | 2009-01-16 | 660 | 1000 | NO | NO | YES | NO | NO | NO | PAUL R SEKINGER - SENIOR LEAD ENGINEER | 4122442582 | PAUL.R.SEKINGER@PEOPLES-GAS.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1949 | 12.75 | 0.31 | B | 35000 | ERW LF | N/A | UKNOWN | 1948 | OTHER | CREEK BED | 36 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | LF ERW |  | MATERIAL DEFECT |  | NO | NO | [19 empty] | THE PORTION OF THE PIPELINE THAT FAILED IS COMPRISED OF A BARE 12.75 INCH DIAMETER BY 0.312-INCH NOMINAL WALL THICKNESS LINE PIPE THAT CONTAINS A LONGITUDINAL SEAM WELD. THE FAILURE OCCURRED AT A LOW POINT IN THE UNPIGGABLE PIPELINE. THE PIPE WAS INSTALLED IN 1948 AND HAS AN IMPRESSED CURRENT CATHODIC PROTECTION (CP) SYSTEM THAT WAS ENERGIZED IN 1961. A TEN-FOOT SECTION OF PIPE THAT INCLUDED THE RUPTURED JOINT AND A PORTION OF THE ADJACENT UPSTREAM JOINT WAS SHIPPED TO DNV FOR ANALYSIS. THE OBJECTIVES OF THE FAILURE ANALYSIS WERE TO DETERMINE THE CAUSE OF THE FAILURE AND IDENTIFY ANY CONTRIBUTING FACTORS. THE FOLLOWING IS A SUMMARY OF THE FINDINGS: • THE RUPTURE OCCURRED AT A GROOVE LOCATED AT THE LONGITUDINAL SEAM WELD. • INTERNAL CORROSION WAS PRESENT IN THE VICINITY OF THE GROOVE. • THE MORPHOLOGY OF THE GROOVE AND ASSOCIATED CORROSION ATTACK IS CONSISTENT WITH SELECTIVE SEAM CORROSION ASSOCIATED WITH ELECTRIC RESISTANCE WELD (ERW) SEAMS. • THE WELD MICROSTRUCTURE IS CONSISTENT WITH AN ELECTRIC RESISTANCE WELD (ERW) SEAM. • THE RESULTS OF THE CHEMICAL ANALYSIS ARE CONSISTENT WITH COMPOSITION SPECIFICATIONS FOR API 5L GRADES B AND C LINE PIPE STEEL IN PLACE AT THE TIME OF MANUFACTURE. • THE RESULTS OF THE MECHANICAL ANALYSIS ARE CONSISTENT WITH THE SPECIFICATIONS FOR API 5L GRADES B AND C LINE PIPE THAT WERE IN PLACE AT THE TIME OF MANUFACTURE. • THE CHARPY V-NOTCH RESULTS INDICATE THAT THE BASE METAL AND WELD METAL EXHIBITED LOW TOUGHNESS VALUES, WHICH IS CONSISTENT WITH THE VINTAGE AND GRADE OF PIPE. THE RESULTS OF THE ANALYSIS INDICATE THAT THE FAILURE OCCURRED DUE TO INTERNAL SELECTIVE SEAM CORROSION. THE SYNERGISTIC EFFECT OF THE SELECTIVE SEAM CORROSION, THE ORIENTATION OF THE SEAM WELD (5:30 O’CLOCK ORIENTATION), AND THE LOW TOUGHNESS OF THE BASE AND WELD METALS WERE THREE OF THE MAIN CONTRIBUTING FACTORS TO THE FAILURE. THE PIPELINE HAS BEEN REPLACED IN IT’S ENTIRETY.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090023 | 2009-03-10 16:44 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1015 | 2009-02-11 | 2009 | CARTHAGE | PANOLA | TX | 75633 |  |  | N32.11.413 | W094.15.698 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201000 | 111968.4952 | 235588.6327 | 16000 | 8469.1358 | 185000 | 227119.4969 | 0 | 0 | YES | YES | YES | YES | 20 | PRECAUTIONARY | 7 | 0 | 897770 | 2009-02-11 | 964 | 1050 | NO | YES | NO | NO | NO | NO | MATTHEW STRATMANN | 7133818209 | MSTRATMANN@EPROD.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1990 | 16 | 0.5 | B | 35000 | ERW |  | UNKONWN |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | NATURAL | [35 empty] | RECEIVED A CALL FROM TROY HAMNER THAT DCP HAD A MAJOR EXPLOSION NEAR OR AT THEIR PLANT. REQUESTED TROY TO CONFIRM THE REPORTING. CALL FROM TROY HAMNER CONFIRMING THAT THE EXPLOSION WAS NOT AT DCP¿S PLANT BUT AT CENTERPOINT COMPRESSOR STATION ADJACENT TO THE DCP FACILITY. TROY ALSO CONFIRMS THAT ALL EPCO EMPLOYEES AND CONTRACTORS WERE ACCOUNTED FOR. MANAGEMENT ARRIVED AT CARTHAGE AND TRAVELED ON CR 301. TRAFFIC WAS STOP BY LAW ENFORCEMENT. POLICE OFFICERS INDICATED THAT A REPORT CAME IN THAT ANOTHER PIPELINE WAS PRESSURING UP AND EVERYONE WAS EVACUATED FROM THE AREA. MANAGEMENT NOTICED THAT THE THE 16¿ LINE 225-10 EAST TEXAS PIPELINE HAD RUPTURED. CAUSE OF INCIDENT WAS FLAME IMPINGEMENT FROM ONTHER FAILED PIPELINE IN THE AREA WHICH CAUSDED THE ENTERPRISE PIPELINE TO FAIL. REPAIRS TO OUR PIPELINE HAVE BEEN COMPLETED AND THE PIPELINE IS BACK IN SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090024 | 2009-03-10 17:28 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1245 | 2009-02-11 | 2009 | CARTHAGE | PANOLA | TX | 75633 | CHAMPLIN COMPRESSOR | 211+00 | +32.190103 | -94.261214 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR STATION DESTROYED | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000620 | 3315472.2717 | 7366365.9149 | 620 | 328.179 | 6000000 | 7366037.7358 | 0 | 0 | YES | YES | NO | YES | 4 | THREAT TO THE PUBLIC | 2 | 0 | 897215 | 2008-02-11 | 735 | 1000 | NO | YES | NO | NO | YES | NO | JOHNNY CAVITT | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | COMPRESSOR STATION | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1978 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | A THIRD PARTY PIPELINE RUPTURE AND CAUGHT FIRE. THE FIRE IMPENDED UPON OUR COMPRESSOR STATION AND MANIFOLD PIPING, DESTROYING THE STATION AND DAMAGING SOME OF THE MANIFOLD PIPING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090025 | 2009-03-12 15:50 | SUPPLEMENTAL FINAL | 19610 |  | TRANSWESTERN PIPELINE COMPANY LLC | 711 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1000 | 2009-02-24 | 2009 | BUCKEYE | MARICOPA | AZ |  | 163.5 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK ON 1/2 INCH NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132000 | 79036.6585 | 87329.1696 | 107000 | 56637.3457 | 25000 | 30691.8239 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 57 | 898400 | 2009-02-24 | 965 | 1008 | YES | NO | NO | NO | NO | NO | JOSE DE LA FUENTE | 2817142327 | JOSE.DELAFUENTE@ENERGYTRANSFER.COM | TRANSMISSION | OTHER | 1/2 INCH NIPPLE | STEEL |  | NO | NO | NO | PIPELINE |  | 2008 | [8 empty] | UNDER GROUND |  | 72 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | LEAK WAS CAUSED BY A SMALL CRACK ON A 1/2" THREADED NIPPLE CONNECTD TO A 1" X 1/2" REDUCER CONNECTED TO A 1" STREET ELL ON THE VALVE BODY BLEED LOCATED ON THE BOTTOM OF A 24" SIDE VALVE. A 13 MILE SECTION OF PIPE HAD TO BE BLOWN DOWN FOR REPAIRS. COST OF GAS ONLY MADE THIS INCIDENT REPORTABLE. |  | THE 1/2" NIPPLE WAS FOUND RESTING ON SKIDS. THE LEAK WAS REPAIRED BY RE-PIPING THE BODY BLEED LINE FROM UNDER THE VALVE. A CONCRETE REST BLOCK WAS THEN INSTALLED UNDER THE VALVE. THE CONCRETE REST BLOCK HAD BEEN INADVERTENTLY OMITTED FROM ENGINEERING DESIGN BECAUSE THIS SIDE VALVE WAS A MUCH LATER ADDITION NOT INCLUDED IN THE ORIGINAL DESIGN. THE LATER DRAWING DID NOT SHOW A REST BLOCK FOR THIS SIDE TAP VALVE. A REVIEW WAS MADE OF OTHER SIDE VALVES AND THE ENGINERINGS DRAWINGS SHOWED REST BLOCKS WERE DESIGNED, AND AS-BUIILT DRAWINGS INDICATED, THAT REST BLOCKS WERE INSTALLED BY THE CONTRACTOR ON THE OTHER SIDE VALVES.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090026 | 2009-03-17 | ORIGINAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1730 | 2009-02-19 | 2009 |  | MATAGORDA | TX |  |  |  | N 28 29 0.84 | W 95 59 0.89 | OFFSHORE |  | BRAZOS | 445 L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 38676.1006 | 85937.1069 | 0 | 0 | 70000 | 85937.1069 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 897990 | 2009-02-19 | 330 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER VP - MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 3 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON FEBRUARY 19. 2009, AT APPROX. 5:30 PM, PANTHER BECAME AWARE OF A POTENTIAL NATURAL GAS LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 45-L. A SMALL SHEEN WAS REPORTED. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE BY 7 PM THAT SAME EVENING. THE FOLLOWING DAY A BOAT WENT TO THE LEAK AREA TO GATHER MORE INFO AND EXACT COORDINATE REPAIRS AND NO SHEEN WAS REPORTED. UPON INVESTIGATION, A PINHOLE LEAK PROBLEM WAS DISCOVERED ON THE PANTHER PIPELINE. PANTHER REPAIRED THE LEAK WITH A CLAMP ON 3/4/09 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 3/4/09.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090027 | 2009-03-19 11:37 | SUPPLEMENTAL FINAL | 31356 |  | VECTOR PIPELINE, L.P. | 119 N 25TH ST EAST | SUPERIOR | DOUGLAS | WI | 54880 | 1025 | 2009-02-19 | 2009 | JOLIET | WILL | IL | 60421 | 0.00 | N/A | 41 27 672 | -88 7 975 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 4705.3867 | 6329.6238 | 5000 | 2646.6049 | 3000 | 3683.0189 | 0 | 0 | NO | YES | NO | NO | 0 |  |  | 20 | 897962 | 2009-02-19 | 790 | 1000 | NO | YES | NO | NO | NO | NO | RON CARLBERG, SR. COMPLIANCE COORDINATOR | 2184645743 | RON.CARLBERG@ENBRIDGE.COM | TRANSMISSION | OTHER | NO SPECIFIC FAILURE. | OTHER | GROUNDING SYSTEM | NO | NO | NO | COMPRESSOR |  | 2007 | [8 empty] | ABOVE GROUND |  | 0 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | SEE NARRATIVE |  | WITH THE JOLIET COMPRESOR STATION OFF LINE AND ISOLATED, STAFF WERE INSTALLING A FACTORY REPAIRED ETHERNET AND CENTRAL PROCESSING UNIT (CPU) CARD TO VERIFY THE RELIABILITY OF THE CARDS. THE JOLIET COMPRESSOR STATION IS EQUIPPED WITH A REDUNDANT EMERGENCY SHUTDOWN PROGRAMMABLE LOGIC CONTROLLER WHICH AFFORDS THE OPPORTUNITY FOR THIS TYPE OF FIELD TESTING. REPLACEMENT OF THESE BOARDS INVOLVED REPROGRAMMING OF THE ERASABLE PROGRAMMABLE READ ONLY MEMORY (EPROM) ON EACH BOARD AND CARD WITH THE CURRENT CUSTOM INSTRUCTION SETS SUITED TO VECTOR OPERATIONS. DURING THE ETHERNET CARD REPROGRAMMING PROCESS; AN EMERGENCY SHUTDOWN (ESD) WAS INADVERTENTLY TRIGGERED, SENDING GAS TO THE SILENCER, AS DESIGNED. THE GAS WAS THEN IGNITED (STATIC CHARGE) AND A FIRE PLUME FROM THE TOP OF THE SILENCER ENSUED. OPERATIONS PERSONNEL IMMEDIATELY CONTACTED THE CONTROL ROOM AND MANAGEMENT TO INFORM THEM THAT THE EVENT HAD OCCURRED (CONTROL CENTRE WAS ALREADY AWARE VIA SCADA LINK) AND THAT THE SYSTEM WAS FUNCTIONING AS DESIGNED, WITH THE EXCEPTION OF THE RESULTANT FIRE. ONCE EVACUATION OF THE GAS WAS COMPLETED, THE FIRE DISSIPATED. NO INJURIES OCCURRED AND DAMAGE WAS LIMITED TO PORTIONS OF THE SILENCER AND SOME NEARBY TREES (ON VECTOR PROPERTY) WERE SINGED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090028 | 2009-03-23 | ORIGINAL FINAL | 15350 |  | DOMINION PEOPLES | 501 MARTINDALE | PITTSBURGH | ALLEGHENY | PA | 15212 | 2010 | 2009-02-11 | 2009 | PITTSBURGH | ALLEGHENY | PA | 15239 |  |  | 40.46028 | 79.70944 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53123 | 32077.1317 | 31851.8101 | 47778 | 25289.8981 | 5345 | 6561.9119 | 0 | 0 | NO | NO | NO | YES | 100 | PRECAUTIONARY | 3 | 15 |  |  | 235 | 350 | NO | NO | YES | NO | NO | NO | PAUL A. HESS TECHNICAL SPEC. II | 7248010722 | PAUL.A.HESS@DOM.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | COUPON HOLDER | 2008 | 2 | 0.22 | GRADE B | 6361 | N A | SCREW | [5 empty] | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [65 empty] | HIGH WINDS BROKE OFF A SECTION OF A LARGE TREE. THE BROKEN SECTION FELL ACROSS A RIGHT OF WAY, STRIKING A 2" COUPON HOLDER. A THREADED VALVE WAS KNOCKED OFF A THREADED RISER.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090029 | 2009-03-27 18:18 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 845 | 2009-02-28 | 2009 | ELGIN | COMANCHE | OK | 73538 | ELGIN TB | 915+02 LINE 11 | +34.78074 | -98.29961 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39900 | 22045.3774 | 48984.1509 | 0 | 0 | 39900 | 48984.1509 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 30 | 898732 | 2009-02-28 | 41 | 1000 | YES | NO | NO | NO | YES | NO | JOHNNY L CAVITT , DOT COMPLIANCE MANAGER | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 2003 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | ROTARY METER FAILURE |  | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1) OR (2), BECAUSE THERE WAS NO RELEASE OF GAS. DURING THE EARLY MORNING OF FEBRUARY 28 A ROTARY METER FAILURE CAUSED THE OUTAGE OF 428 CUSTOMERS AND DUE TO THE WEATHER CONDITIONS THIS OPERATOR CONSIDERED IT TO BE SIGNIFICANT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090030 | 2008-09-23 | ORIGINAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056-5306 | 900 | 2008-08-25 | 2008 | PILOT GROVE | COOPER | MO | 65276 | VS 2 | 1140+00 | 38°54'09.5 N | 92° 58' 25 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK |  | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046359 | 534226.5581 | 957964.5534 | 393296 | 146950.4662 | 628063 | 779967.5385 | 25000 | 31046.5486 | NO | NO | NO | NO | 0 |  | 0 | 38 | 881717 | 2008-08-25 | 790 | 800 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1937 | 24 | 0.28 | ASME | 48000 | EFW |  | A O SMITH | 1937 | UNDER GROUND |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1955 | NO | [57 empty] | TENSILE OVERLOAD AT AN AREA OF WALL THINNING AT THE 6:00 CLOCK ORIENTATION DUE TO EXTERNAL CORROSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090031 | 2009-04-02 13:16 | SUPPLEMENTAL FINAL | 12684 |  | MONTANA - DAKOTA UTILITIES CO | 400 N. 4TH ST | BISMARCK | BURLEIGH | ND | 58502 | 809 | 2008-02-20 | 2008 | PIERRE | HUGHES | SD | 57501 | PIERRE TBS |  | 44.36950 | -100.32110 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 83063.5146 | 181069.9501 | 6000 | 2241.8301 | 144000 | 178828.12 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 11 | 862871 | 2008-02-20 | 790 | 1100 | NO | YES | NO | NO | NO | NO | SCOTT A. BESMER | 7012227883 | SCOTT.BESMER@MDU.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | JOINT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1993 | 2 | 0.15 | API 5L-GR. B | 35000 | ERW |  | UNKNOWN |  | ABOVE GROUND |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | GAS STREAM CONTAMINATED WITH DEBRIS FROM TRANSMISSION COMPANY PIPELINE. GASKET BETWEEN STRAINER AND REGULATOR FAILED DUE TO THE SUDDEN INCREASE IN PRESSURE AND DEBRIS CONTAINED WITHIN THE GAS STREAM CAUSED BY THE TRANSMISSION COMPANIES PIGGING OPERATIONS. THE FILTERING SYSTEM WAS INUNDATED AND FAILED CAUSING DEBRIS TO EAT AWAY AT THE GASKET MATERIAL. NOTE: THIS INCIDENT WAS ORIGINALLY COMPLETED ON INCIDENT REPORT ¿ GAS DISTRIBUTION SYSTEM (7100.1). DUE TO THE PIPE MATERIAL LEADING UP THE FAILED GASKET THE REPORT HAD TO BE COMPLETED ON THIS FORM. THAT IS WHY THE PREPARATION DATE IS 4/1/09. NOTE: SUPPLEMENTAL REPORT SUBMITTED 7/27/2010 DUE TO INCORRECT DATE ENTERED DURING ELECTRONIC FILING ON 4/2/2009. ALSO SENDING RESCISSION LETTER FOR THE DISTRIBUTION REPORT MENTIONED ABOVE.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090032 | 2009-04-03 13:38 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1010 | 2009-03-15 | 2009 |  |  |  |  | 3.19 |  | N28^00'05 | W95^43'53 | OFFSHORE |  | BRAZOS | A70 |  | YES | YES | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756912 | 418600.1258 | 924413.3836 | 6912 | 3658.6667 | 750000 | 920754.717 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 0 | 899975 | 2009-03-15 | 980 | 1250 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 16 | 0.44 | API-5LX | 52000 | SEAMLESS |  | KAISER STEEL CORPORATION | 1977 | UNDER WATER |  | 72 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1978 | NO | [57 empty] | A CONDENSATE LEAK/SHEEN WAS REPORTED BY A PRODUCER ON THE BA 133A PLATFORM. THE FOLLOWING DETAILS WERE NOTED: SLICK ¿ 1 ½ MILES LENGTH SEAS ¿ 4-5 FT WINDS ¿ NORTH, 20 MPH CURRENT ¿ EAST COORDINATES ¿ 27.59.9 N, 95.53.5 W IT WAS LATER ESTIMATED THAT APPROXIMATELY 3 GALLONS OF CONDENSATE WAS RELEASED. ACTIONS WERE TAKEN TO ISOLATE AND BLOW DOWN THE GAS PRESSURE. A REPAIR CLAMP WAS INSTALLED ON 3/29/09. AFTER A LEAK CHECK, OPERATION RESUMED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090033 | 2009-04-13 13:01 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1630 | 2009-03-19 | 2009 | ARBUCKLE | COLUSA | CA | 95912 | ARBUCKLE REG STATION A01 |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | DIG-IN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52000 | 28844.922 | 62442.2898 | 2000 | 1058.642 | 50000 | 61383.6478 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 900455 | 2009-03-19 | 145 | 150 | NO | NO | NO | NO | NO | NO | LARRY DENISTON | 9259744313 | LCD1@PGE.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1992 | 2 | [7 empty] | UNDER GROUND |  | 58 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | A PG&E CREW EXCAVATING TO REPAIR A VALVE, STRUCK A 2-INCH STUB ON A STEEL GAS MAIN NEAR THE INTERSECTION OF GRIMES/ARBUCKLE RD AND FIRST STREET IN ARBUCKLE. EMERGENCY USA WAS NOTIFIED PRIOR TO EXCAVATION. THERE WERE NO INJURIES AND NO FATALIES AS A RESULT OF THIS INCIDENT. REPAIRS TO THE GAS MAIN, INCLUDING THE RESTORATION OF SERVICE TO APPROXIMATELY 1,040 CUSTOMERS, EXCEED $50,000. SERVICE RESTORATION FOR ALL CUSTOMERS THAT PG&E WAS ABLE TO GAIN ACCESS TO WAS COMPLETE BY 1700 HOURS ON 3/20/09. THE CAUSE OF THE DIG-IN WAS THAT THE PLAT MAP DID NOT SHOW THE 2 INCH STUB OFF THE TRANSMISSION LINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090034 | 2009-04-13 16:48 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1730 | 2009-03-15 | 2009 | MALVERN | MILLS | IA | 51551 | 590 | 26158+94.5 | N41.03558 | W95.60646 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83000 | 48312.0487 | 71867.7207 | 43000 | 22760.8025 | 40000 | 49106.9182 | 0 | 0 | NO | NO | NO | YES | 10 | PRECAUTIONARY | 4 | 0 | 900-007 | 2009-03-15 | 450 | 712 | NO | YES | NO | NO | NO | NO | REJI GEORGE | 7134205433 | REJI_GEORGE@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1942 | 26 | 0.25 | 5LX | 52000 |  |  | A.O. SMITH | 1941 | OPEN DITCH |  | 0 | OTHER OUTSIDE FORCE DAMAGE | VANDALISM | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [65 empty] | THE INCIDENT WAS CAUSED BY A HIGH CALIBER RIFLE BULLET, CREATING A 1/2" DIAMETER HOLE. THE PIPELINE HAS BEEN REPAIRED AND PUT BACK INTO SERVICE. INCIDENT IS BEING INVESTIGATED BY LAW ENFORCEMENT. UPDATED BY PHMSA 6/4/2015: UPDATED "TIME OF INCIDENT" TO 17:30. LEAK WAS CONFIRMED TO BE ON THE NGPL SYSTEM AT 18:00. THAT CONFIRMED DISCOVERY TIME WAS USED TO COMPLETE INCIDENT REPORT IN APRIL 2009. 17:30 IS APPROXIMATELY WHEN COMPANY PERSONNEL INITIALLY RECEIVED A REPORT OF BLOWING GAS. R.G./REJI GEORGE - CODES AND STANDARDS KINDER MORGAN
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090035 | 2009-04-14 11:46 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 N NEVADA AVE | COLORADO SPRINGS | EL PASO | CO | 80903 | 1015 | 2009-03-20 | 2009 | SELIGMAN | MOHAVE | AZ |  | 354+2089 | LINE NO. 1204 | 35.19106046 | -113.3525302 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LEAK THROUGH A 2 INCH LONG CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86092 | 52478.9198 | 45570.3025 | 86092 | 45570.3025 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 900500 | 2009-03-20 | 750 | 894 | NO | NO | YES | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1957 | 34 | 0.41 | API 5L | 52000 | EFW |  | A.O. SMITH | 1957 | UNDER GROUND |  | 192 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | A ROCK BEARING AGAINST PIPE FROM ORIGINAL CONSTRUCTION CAUSED A SMALL CRACK THROUGH WHICH GAS LEAKED. |  | DURING EXCAVATION OF EL PASO NATURAL GAS COMPANY'S 1204 PIPELINE, BEING PERFORMED DUE TO AN ANOMALY INDICATION FOUND DURING AN INSTRUMENTED PIG RUN, THE ODOR OF NATURAL GAS WAS DETECTED. FURTHER EXCAVATION AND SUBSEQUENT EVALUATION REVEALED A 2-INCH LONG CRACK APPARENTLY CAUSED BY A ROCK SURFACE BEARING ON THE PIPE. GAS WAS LEAKING THROUGH THE CRACK. THE PIPELINE WAS BLOWN DOWN TO ATMOSPHERIC PRESSURE AND REPAIRED WITH A FULL ENCIRCLEMENT WELD-OVER SPLIT SLEEVE. THIS WAS THE SAME REPAIR METHOD PLANNED FOR THE ANOMALY THAT HAD BEEN DETECTED BY THE SMART PIG RUN AT THIS POINT ON THE PIPELINE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090036 | 2009-04-22 12:11 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1530 | 2009-03-23 | 2009 | [5 empty] | LINE 523M-6400 | 28 39 58 | -91 05 40 | OFFSHORE |  | SHIP SHOAL | 181B |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000000 | 1657547.1698 | 3683018.8679 | 0 | 0 | 3000000 | 3683018.8679 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 900731 | 2009-03-23 | 800 | 1440 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1983 | 8.63 | 0.5 | API 5L | 35000 |  |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE IKE | [51 empty] | DURING HURRICANE IKE, DAMAGE WAS SUSTAINED TO TENNESSEE GAS PIPELINE (TGP) COMPANY'S EAST LEG OF ITS BLUEWATER HEADER, ALSO KNOWN AS THE 523 SYSTEM. SEVERAL INDIVIDUAL PIPELINES WERE DAMAGED, WITH DAMAGE TO THE 523M-100 LINE BEING FOUND EARLIER. UPON REPAIR OF THAT LINE AND THE RETURN OF PART OF THE SYSTEM TO SERVICE, DISCOVERY WAS MADE THAT THE HURRICANE HAD ALSO SEVERED TGP'S 8-INCH 523M-6400, WHICH IS THE SUBJECT OF THIS REPORT. THIS PIPELINE WAS NOT REPAIRED BUT TGP IS NO LONGER THE OPERATOR OF THE PIPELINE. IT WAS SOLD TO CHEVRON USA.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20090037 | 2009-04-22 | ORIGINAL FINAL | 7050 |  | HAMPSHIRE GAS CO | HC 779 BOX 69-A | ROMNEY | HAMPSHIRE | WV | 26757 | 1015 | 2009-03-24 | 2009 | ROMNEY | HAMPSHIRE | WV | 26757 |  | 0+00 | 39.18775 | -78.75006 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 901003 | 2009-03-26 | 3 | 2467 | NO | YES | NO | NO | NO | NO | CLAY BEAN - SUPERVISOR HAMPSHIRE GAS | 3048225664 | CBEAN@WASHGAS.COM | TRANSMISSION | OTHER | VALVE AND SAFETY INTERLOCK BLOCKAGE | STEEL |  | NO | NO | NO | OTHER | PIG RECEIVER | 1997 | [8 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | 3/4" BALL VALVE USED FOR VENTING THE RECEIVER BECAME BLOCKED WITH DEBRIS RESULTING FROM PIGGING OPERATION AND DID NOT ALLOW FULL PRESSURIZATION. PORT ON RECEIVER ACTING AS SAFETY INTERLOCK FOR MAIN DOOR ALSO PLUGGED WITH DEBRIS DURING OPERATION. |  | WHILE PERFORMING PIPELINE CLEANING WITH A SCRAPER PIG, THE PIG ARRIVED IN THE PIG RECEIVER. RECEIVER ISOLATION VALVES WERE CLOSED. PRESSURE IN THE RECEIVER WAS RELEASED THROUGH MANUALLY OPERATED BALL VALVES (4) LOCATED IN FRONT AND BEHIND THE PIG. AFTER VENTING GAS STOPPED, AND WITH VENT VALVES IN THE OPEN POSITION, THE SAFETY INTERLOCK DEVICE WAS REMOVED FROM THE HINGED CLOSURE TO PERMITE OPENING OF THE MAIN DOOR. WITH NO FURTHER GAS ESCAPING FRO EITHER THE VALVES OR THE PRESSURE WARNING INTERLOCK DEVICE, PERSONNEL BEGAN REMOVING THE CLAMP WHICH SECURES THE MAIN DOOR. AS THE CLAMP WAS LOOSENED, THE 14" NOMINAL DIAMETER MAIN DOOR OPENED ABRUPTLY AND WITH FORCE DUE TO UNVENTED GAS PRESSURE TRAPPED IN THE VESSEL BEHIND THE BLOCKED VENT VALVES AND SAFETY INTERLOCK. THE DOOR STRUCK AN EMPLOYEE IN THE ABDOMEN AS IT SWUNG OPEN. THE ESTIMATED PRESSURE IN SECTION A.8.A IS BASED IN THE NATURE OF THE BLOCKAGE, TYPE OF DEBRIS, ARE OF THE DOOR, AND RELTIVELY MINOR INJURY TO THE EMPLOYEE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090038 | 2009-04-24 11:04 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC | 445 W. MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 900 | 2009-03-31 | 2009 | LUSBY | CALVERT | MD | 20657 |  |  | 38.393028 | -76.435920 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 112956.3883 | 215505.4566 | 43000 | 22760.8025 | 157000 | 192744.6541 | 0 | 0 | YES | NO | NO | NO | 0 |  | 0 | 1 | 901403 | 2009-03-31 | 900 | 1250 | YES | NO | NO | NO | NO | NO | SHAWN MILLER | 3046273404 | SHAWN.A.MILLER@DOM.COM | TRANSMISSION | OTHER | STOPPLE FITTING | STEEL |  | NO | NO | NO | OTHER | STOPPLE FITTING | 1990 | [8 empty] | UNDER GROUND |  | 60 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE LEAK OCCURRED AT A STOPPLE FITTING BLIND FLANGE. REPAIR WAS MADE BY CUTTING OUT STOPPLE FITTING, AND REPLACING WITH A CYLINDER OF PIPE (36") |  | A LEAK WAS DISCOVERED NEAR PIPELINE TL522 DURING THE COMMISSIONING OF PARALLEL PIPELINE TL532. ON 3/31/09, AT 9:00 AM, IT WAS DETERMINED THAT THE LEAK WAS INDEED THE 36" STOPPLE FITTING ON TL522. THE REPAIR WAS MADE VIA REPLACEMENT. THIS OCCURENCE WAS REPORTED AS AN "INCIDENT" DUE TO THE REPAIR COSTS AND GAS LOSS EXCEEDING $50,000. THE FITTING IS BEING EVALUATED BY THE MANUFACTURER (TD WILLIAMSON) TO DETERNMINE THE REASON OF FAILURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090039 | 2009-04-23 | ORIGINAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 1008 | 2009-03-24 | 2009 | CHIPLEY | WASHINGTON | FL | 32428 | MP 8.5 | 449+74 | 33° 44' 43" N | -85° 35' 50" W | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | 34282.7894 | 75787.4978 | 470 | 248.7809 | 61530 | 75538.717 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 900828 | 2009-03-24 | 890 | 975 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 3.5 | 0.13 | 5L | 35000 | SMLS | N/A | NATIONAL TUBE | 1959 | UNDER GROUND |  | 60 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1959 | NO | [57 empty] | LEAK WAS REPORTED BY A LOCAL ROAD CONTRACTOR TO A 911 OPERATOR, WHO CONTACTED FLORIDA GAS TRANSMISSION. PIPELINE HAD LOCALIZED CORROSION PITTING. PIPELINE REPAIR EXCEEDED $50,000 THRESHOLD, BECAUSE A STOPPLE AND BYPASS WAS REQUIRED TO MAKE THE PIPE REPLACEMENT, WHILE MAINTAINING CUSTOMER SERVICE. THE NRC CALLED BACK WITH A SECOND NRC REPORT #900833, DUE TO COMPUTER PROBLEMS ON THEIR END.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20090040 | 2009-04-24 15:07 | ORIGINAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1849 | 2009-04-07 | 2009 | CHANUTE | NEOSHO | KS | 66720 | METER# 14604 | D-26 | 37.66051 | -95.489058 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | VEHICLE BROKE 1" TAP FROM LINE. | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 110863 | 61337.1321 | 135080.4213 | 1465 | 775.4552 | 109398 | 134304.966 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 59 | 902099 | 2009-04-07 | 179 | 350 | NO | YES | NO | NO | NO | NO | DAVID SINCLAIR | 2708524424 | DAVID.L.SINCLAIR@SSCGP.COM | TRANSMISSION | OTHER | METER SETTING | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1985 | 1 | 0.18 | AP5L | 9528 | SEAMLESS |  |  |  | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | AT 18:59 ON 4/7/2009, GAS CONTROL WAS NOTIFIED THAT THERE WAS A VEHICLE ACCIDENT AT THIS LOCATION. UPON INVESTIGATION, THEY FOUND A VEHICLE DROVE ERATICALLY THROUGH A FIELD, ACROSS TWO ROADS, TRAVELING AT A HIGH RATE OF SPEED. THE VEHICLE STRUCK THE METER SETTING BREAKING OFF A 1" TAP. THIS CAUSED A RELEASE OF NATURAL GAS WHICH DID NOT IGNITE. THERE WAS NO LOSS OF SERVICE DUE TO THE ACCIDENT BECAUSE THE TOWN WAS HELD ON INTERNAL GRID.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090041 | 2009-04-28 10:43 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25314 | 712 | 2009-04-04 | 2009 | SENECA ROCKS | PENDLETON | WV | 26884 | SENECA COMPRESSOR STATION |  | 38.8813 | -79.3762 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | COMPRESSOR STATION BUILDING BLOW DOWN | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101335 | 61770.5633 | 53638.7423 | 101335 | 53638.7423 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 40 | 901801 | 2009-04-04 | 731 | 1000 | NO | YES | NO | NO | NO | NO | MARK NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | OTHER | LOST ELECTRICAL POWER | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2008 | [8 empty] | OTHER | COMPRESSOR STATION |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | COMPRESSOR STATION BUILDING BLOW DOWN | [10 empty] | DURING THE NIGHT, THE COMMERCIAL POWER TO THE STATION WAS BRIEFLY INTERRUPTED. THE POWER LOSS CAUSED THE AIR COMPRESSORS TO TURN OFF. DUE TO A SLOW LEAK SLOW LEAK, THE PRESSURE FELL ON THE AIR SYSTEM, AT WHICH POINT THE VENT VALVES OPENED, BLOWING DOWN ONE COMPRESSOR BUILDING AND THE ASSOCIATED FUEL GAS SYSTEM. CONTROLS TO AIR COMPRESSOR HAVE BEEN MODIFIED TO ALLOW UNITS TO STAY ON DURING BRIEF INTERRUPTIONS IN ELECTRIC POWER. COLUMBIA'S MONITORING CENTER IS ALSO NOW ABLE TO MONITOR STATION AIR PRESSURE WHICH IS USED TO ACTIVATE THE STATION ESD SYSTEM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090042 | 2009-04-28 18:58 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1500 | 2009-04-03 | 2009 | SALINAS | MONTEREY | CA |  | 62.3 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | DIG-IN | PUNCTURE | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1510000 | 834869.2639 | 1846802.6438 | 10000 | 5293.2099 | 1200000 | 1473207.5472 | 300000 | 368301.8868 | NO | NO | NO | NO | 0 |  | 2 | 0 | 901900 | 2009-04-03 | 300 | 313 | NO | NO | NO | NO | NO | NO | LAURENCE DENISTON | 9259744313 | LCD1@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 8 | [7 empty] | UNDER GROUND |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | ON 4/3/09 AT APPROXIMATELY 1500 HOURS A FARMER RIPPING AN AGRICULTURE FIELD DUG INTO LINE 187 NEAR MILE POST 62.3 IN SALINAS. USA WAS REQUIRED, BUT WAS NOT NOTIFIED. THE LINE WAS AN 8" STEEL DISTRIBUTION FEEDER MAIN OPERATING AT 300 PSI. THERE WERE NO INJURIES OR FATALITIES AND NO SIGNIFICANT NEWS MEDIA PRESENT. AT APPROXIMATELY 2100 HOURS ON 4/3/09 IT WAS DETERMINED THAT DUE TO THE NUMBER OF CUSTOMERS OUT OF SERVICE AND THAT THE LNG TRAILER WAS MOBILIZED TO ASSIST IN PROVIDING NATURAL GAS SUPPLY DURING THE OUTAGE A REPORT SHOULD BE FILED WITH THE CPUC (CPUC # 090403-1276). AT APPROXIMATELY 1800 HOURS ON 4/5/09 IT WAS DETERMINED THAT THE INCIDENT WAS DOT REPORTABLE DUE TO DAMAGES EXCEEDING $50,000. A DOT REPORT WAS FILED AND A DUPLICATE CPUC REPORT (# 090405-1282) WAS FILED AT APPROXIMATELY 1901 HOURS ON 4/5/09 INCLUDING THE DOT REPORT NUMBER. UPDATED BY PHMSA ON 12/16/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090043 | 2009-05-04 10:59 | SUPPLEMENTAL FINAL | 31336 |  | CHEVRON U.S.A. INC | 100 NORTHPARK BLVD | COVINGTON | ST. TAMMANY | LA | 70433 | 1224 | 2009-04-24 | 2009 |  |  | GM | [5 empty] | OFFSHORE |  | WEST DELTA | 33 | GM | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 903685 | 2009-04-24 | 20 | 960 | NO | YES | NO | NO | NO | NO | ERIN DUNAWAY | 9857736554 | ERIN.DUNAWAY@CHEVRON.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 26 | 0.58 | X52 | 52000 | SMLS | N/A |  |  | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | INTERNAL CORROSION | OTHER | EROSION/CORROSION | YES | 1966 | NO | [57 empty] | SEE REPORT #20090006 FOR DETAILS. PIPELINE WAS OUT OF SERVICE AT TIME OF LEAK REPORTED IN #20090043. CLAMPS HAVE BEEN INSTALLED OVER PINHOLE LEAKS REPORTED IN #20090006. PIPELINE OWNED BY TARGA RESOURCES, INC. UPDATE: AS OF 6/1/09, OPERATOR OF THIS LINE IS TARGA RESOURCES, INC. ON BEHALF OF VENICE GATHERING SYSTEMS, LLC. PER THE MMS PIPELINE PERMITS DATABASE, APPLICATION TO DECOMMISSION LINE AND RELINQUISH RIGHT-OF-WAY WAS SUBMITTED ON 9/2/09 AND APPROVED BY MMS ON 9/30/09.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090044 | 2009-05-04 | SUPPLEMENTAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056-5306 | 1418 | 2009-04-04 | 2009 | GLENARM | SANGAMON | IL | 62536 | VS 0 | 1+06 | 39°38' 02.35 N | 89° 37' 46 W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85135 | 51887.0054 | 45168.4951 | 84985 | 44984.3441 | 150 | 184.1509 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 50 | 901925 | 2009-04-06 | 860 | 900 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | OTHER | BUNA-N | NO | NO | NO | COMPRESSOR |  | 1965 |  |  | N/A |  | N/A | N/A | N/A |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | AN O-RING FAILURE ON A VALVE LIMIT SWITCH CAUSED A BLOWDOWN VALVE TO OPEN VENTING GAS REPORTABLE ONLY BECAUSE OF THE VOLUME OF NATURAL GAS RELEASED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090045 | 2009-05-07 12:32 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | -7-7002 | 1215 | 2009-04-08 | 2009 |  |  |  |  | 4495 |  | 28.313539 | -01.413973 | OFFSHORE |  | EUGENE ISLAND | 302 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450000 | 251484.6844 | 517535.2318 | 50000 | 26466.0494 | 400000 | 491069.1824 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 902157 | 2009-04-08 | 850 | 1260 | NO | YES | NO | NO | NO | NO | GLENNA S RICHMOND | 9852236440 | GLENNA.RICHMOND@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1972 | 30 | 0.75 | API 5L | 60000 |  |  |  |  | UNDER WATER |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1972 | NO | [57 empty] | BUBBLES WERE REPORTED AT THE WATER'S SURFACE BY TENNESSEE GAS PIPELINE HELICOPTER DURING ROUTINE AERIAL PATROL. THIS WAS DETERMINED TO BE A LEAK ON THE COMPANY'S 30" 523M-2300 PIPELINE. DIVERS INSTALLED A CLAMP TO REPAIR THE LEAK WHICH WAS APPARENTLY CAUSED BY INTERNAL CORROSION IN A WELD AT THE 6 O'CLOCK POSITION ON THE PIPELINE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090046 | 2009-05-07 | ORIGINAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1035 | 2009-04-07 | 2009 | MATAGORDA |  | TX |  |  |  | N28 28.99 | W95 59.74 | OFFSHORE |  | BRAZOS | 445°L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 30388.3648 | 67522.0126 | 0 | 0 | 55000 | 67522.0126 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 902045 | 2009-04-07 | 350 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER VP-MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.32 | APISL | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 3 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON APRIL 7, 2009, AT APPROX. 10:35AM, PANTHER BECAME AWARE OF A POTENTIAL NATURAL GAS LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 445-L. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMANT OF PIPELINE THAT SAME AFTERNOON. THE FOLLOWING DAY A BOAT WENT TO THE LEAK AREA TO GATHER MORE INFO AND EXACT COORDINATES TO COORDINATE REPAIRS AND NO SHEEN WAS REPORTED. UPON INVESTIGATION, A PINHOLE LEAK PROBLEM WAS DISCOVERED ON THE PANTHER PIPELINE. PANTHER REPAIRED THE LEAK WITH A CLAMP ON 4/15/09 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 4/15/09.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090047 | 2009-05-08 17:13 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 850 | 2008-07-21 | 2008 | EUREKA | HUMBOLDT | CA | 95503 |  |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70500 | 39338.2463 | 87117.1553 | 500 | 186.8192 | 70000 | 86930.3361 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 55 | 879750 | 2008-08-06 | 163 | 167 | NO | NO | NO | NO | NO | NO | LAURENCE DENISTON | 9259744313 | LCD1@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 4 | 0.19 | API-5L GR.B | 35000 |  |  |  | 1971 | UNDER GROUND |  | 48 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | OTHER | CULVERT INSTALLATION | YES | 7 | 1 | 2008 | ONE-CALL SYSTEM | YES | PAINT | YES | ACCURATE | YES | [36 empty] | A LARGE EXCAVATOR, DIGGING TO INSTALL A CULVERT, WAS MANEUVERING AROUND SOME GROUND SUBSIDENCE AND STRUCK A 4-INCH GAS TRANSMISSION LINE WITH ITS TRACK. THE GAS LINE WAS PROPERLY MARKED AND PG&E HAD STOOD BY DURING CONSTRUCTION ON PRIOR DAYS. NO STANDBY WAS CALLED FOR BY THE EXCAVATOR ON THE DAY OF THE INCIDENT. REPAIRS TO THE LINE WERE MADE AND THE LINE WAS PUT BACK IN SERVICE ON 7/22/08 AT 0340. PG&E INITIALLY ESTIMATED THE COST OF THE INCIDENT TO BE APPROXIMATELY $35,000. ON 8/6/08, ACTUAL COSTS IN PG&E ACCOUNTING SYSTEM WERE FOUND TO EXCEED $50,000.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090048 | 2009-05-13 08:56 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1047 | 2009-04-27 | 2009 | GIBSON | TERREBONNE | LA | 70356 | 101.74 |  | N29,36,003 | W60,52,550 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179000 | 98900.3145 | 219753.4591 | 0 | 0 | 179000 | 219753.4591 | 0 | 0 | NO | NO | NO | YES | 2 | THREAT TO THE PUBLIC | 21 | 13 | 903884 | 2009-04-27 | 822 | 1070 | YES | NO | NO | NO | NO | NO | JOHNNY LOPEZ | 7132152995 | JOHNNY.LOPEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | OTHER | MANIFOLD | 1967 | 30 | 0.5 | API 5LX-60 | 2000 | DSA |  | BETHLEHEM STEEL | 1967 | ABOVE GROUND |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1967 | NO | [57 empty] | ON APRIL 7, 2009 A PINHOLE LEAK WAS DISCOVERED ON A DEAD LEG SECTION OF LINE C IN THE STATION 62 YARD. INITIALLY THE LINE WAS ISOLATED AND REPAIRED BY INSTALLATION OF A SPLIT SLEEVE. THE CAUSE OF THE LEAK WAS INTERNAL CORROSION. A UT SCAN SURVEY WAS THEN COMPLETED FOR ALL DEAD LEG SECTIONS IN THE STATION YARD TO LOOK FOR SIMILAR AREAS TO PREVENT RECURRENCE. ALL SECTIONS REQUIRING REMEDIATION WERE REPAIRED OR REMOVED. A 150 FOOT SECTION OF THE LINE THAT LEAKED WAS REMOVED IN SEPTEMBER 2009 AND BLINDED AT THE IN-SERVICE CONNECTING ENDS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090049 | 2009-05-14 08:43 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 1645 | 2009-05-06 | 2009 | ARKANSAW | PEPIN | WI | 54721 | 49.15 |  | 44.6070064 | -92.0209659 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | 3RD PARTY CONTRACTOR DAMAGE TO PIPELINE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316630 | 179927.9875 | 327699.5848 | 87375 | 46249.4213 | 229255 | 281450.1635 | 0 | 0 | NO | NO | NO | YES | 25 | PRECAUTIONARY | 2 |  | 904811 | 2009-05-06 | 706 | 895 | NO | YES | NO | NO | NO | NO | BYRON H. WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 8 | 0.16 | API | 42000 | ERW |  | INTERLAKE (ACME NEWPORT) |  | UNDER GROUND |  | 39 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | LANDOWNER |  | NO |  |  |  |  | YES |  | YES | [38 empty] | ON MAY 6, 2009, AT APPROXIMATELY 4 P.M., EARTH MOVING EQUIPMENT OPERATED BY A KEVIN BITES AND OWNED BY A COMPANY CALLED DOANE LTD, STRUCK NORTHERN'S BLACK RIVER FALLS 8-INCH DIAMETER BRANCHLINE (WIB18601) NEAR MILE POST 49.15 IN THE EAST 1/2 OF THE NE 1/4 OF SECTION 36, T25N, R14W PEPIN COUNTY, WISCONSIN. THIS 8-INCH LINE HAS AN MAOP OF 895 AND WAS OPERATING AT APPROXIMATELY 706 PSIG AT THE TIME OF THE INCIDENT. THERE WAS ESCAPING GAS TO ATMOSPHERE BUT IT DID NOT IGNITE AND THERE WAS NO FIRE, EXPLOSION OR INJURIES. EMEREGENCY RESPONDERS EVACUATED RESIDENCES WITHIN A 1/2 MILE RADIUS, WHICH AFFECTED 24 BUILDINGS. RESPONDERS ALSO BLOCKED ROADS NEAR THE INTERSECTION OF SILVER BIRCH ROAD AND ROUND HILL ROAD. FOLLWING REPAIRS, THE PIPELINE WAS RETURNED TO NORMAL SERVICE AT APPROXIMATELY 7:20 P.M., MAY 7, 2009. REPRESENTATIES FROM THREE UTILITIES, ST. CROIX VALLEY NATURAL GAS, MIDWEST NATURAL GAS, AND WE ENGERGIES ASSISTED WITH GAS LOAD REDUCTIONS AND FACILITY MANAGEMENT DURING THE PIPELINE REPAIRS. FIVE NORTHERN NATURAL GAS CO. BOTTLE TRUCKS WERE UTILIZED IN MAINTAINING SERVICE. APPROXIMATELY 70 NORTHERN EMPLOYEES AND 20 CONTRACTOR EMPLOYEES WORKED NON-STOP PERFORMING EMERGENCY MANAGEMENT AND PIPELINE REPAIRS, WHICH CONSISTED OF REPLACING 83 FEET OF 8-INCH DIAMETER PIPE WITH NEW TESTED/COATED PIPE AND THE INSTALLATION OF A REPAIR SLEEVE. INITIAL INVESTIGATION INDICATES THAT NORTHERN'S PIPELINE WAS DENTED IN ONE LOCATION AND SEVERED IN ANOTHER BY EQUIPMENT OPERATED BY THE CONTRACTORS EMPLOYEE. IT APPEARS THAT THERE WAS NO ONE-CALL LINE LOCATE REQUEST MADE PRIOR TO COMMENCING EXCAVATION ACTIVITIES. THE PIPELINE WAS MARKED AT BOTH SIDES OF THE PROPERTY WITH PIPELINE MARKERS AND AN ADDITIONAL MARKER WAS VISIBLE APPROXIMATELY 121 FT WEST OF THE LINE HIT LOCATION, IN A TREE ROW. AN IN-DEPTH INVESTIGATION OF THE INCIDENT IS IN-PROGESS AND ADDITIONAL SUPPLEMENTAL/FINAL REPORTS WILL BE FILED AS THE ROOT CAUSE & TOTAL COST OF REPAIRS INFORMATION IS COMPLETE. THERE WAS NO LOSS OF SERVICE TO CUSTOMERS. SUPPLEMENTAL/FINAL REPORT: AN INVESTIGATION INTO THE ROOT CAUSE OF THE INCIDENT DETERMINED THAT THERE WAS NO "ONE CALL" MADE TO DIGGERS HOTLINE INCORPORATED (WISCONSIN) PRIOR TO MOVING SOIL AND EXCAVATION ACTIVITIES AT THE SITE, WHICH RESULTED IN REMOVAL OF SOIL FROM OVER THE PIPELINE TO THE EXTENT THAT THE PIPELINE WAS STRUCK AND SEVERED. SUPPLEMENTAL UPDATE OF FINAL REPORT: CORRECTED ESTIMATED COSTS FROM $287120 TO $316630 (GAS LOSS $87375; OPERATOR DAMAGE $229,255). NO OTHER MODIFICATION OR CORRECTIONS MADE. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090050 | 2009-05-14 18:22 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1200 | 2009-05-14 | 2009 | DUBACH | LINCOLN | LA | 71235 | RUSTON COMPRESSOR ST | 0+0 LINE F-EAST | +32.624800 | -92.611830 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48912 | 27089.4603 | 59254.6118 | 1136 | 601.3086 | 47776 | 58653.3031 | 0 | 0 | NO | YES | NO | NO | 0 |  |  | 32 | 902983 | 2009-04-14 | 1950 | 2500 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT , DOT COMPLIANCE MANAGER | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | OTHER | 1" 90 DEGREE WELDED PIPE FITTING | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1981 | [8 empty] | UNDER GROUND |  | 60 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDETERMINED | YES | 1981 | NO | [57 empty] | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE WE EXPERIENCED AN IGNITION OF THE LEAKING GAS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090051 | 2009-05-15 09:12 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 752 | 2009-04-23 | 2009 | GREENSBURG | GREEN | KY | 42713 | 869-1+19.80 (800-1 LINE) | 1045+69.70 | 37.163677 | -85.535165 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FAILURE AT FULL ENCIRCLEMENT TAP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115360 | 65185.0571 | 123914.1463 | 25360 | 13423.5802 | 90000 | 110490.566 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 903548 | 2009-04-23 | 720 | 936 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | FULL ENCIRCLEMENT TAP | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 30 | 0.63 | API 5L OR EQUIV | 52000 |  |  | NATIONAL TUBE | 1959 | UNDER GROUND |  |  | OTHER | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [64 empty] | INVESTIGATION COMPLETE | A TENNESSEE GAS PIPELINE EMPLOYEE FOUND, THROUGH ROUTINE OPERATIONS & MAINTENANCE WORK, INDICATIONS OF A GAS LEAK EVIDENCED BY WATER BUBBLING ABOVE A PIPELINE AT THE SURFACE OF WET GROUND. THE PIPELINE IS TGP'S 30" 800-1 LINE. EXCAVATION REVEALED WHAT APPEARED TO BE A CRACK IN A FILLET WELD WHERE A 12" PIPE TAPPED THROUGH A FULL ENCIRCLEMENT SLEEVE INTO THE 30" CARRIER PIPE. REPAIRS WERE COMPLETED AROUND APRIL 27, 2009 BY INSTALLING A WELD TEE. THE RESULTS FROM INVESTIGATION CONFIRM THAT THE BRANCH-TO-CARRIER PIPE FILLET WELD UNDER THE FULL ENCIRCLEMENT SADDLE CONTAINED A CRACK EXTENDING THROUGH THE WELD CAP AND STOPPING JUST BEFORE THE ROOT BEAD LEAVING A SMALL LIGAMENT OF METAL PREVENTING THROUGH-WALL PENETRATION. BASED ON THE LAB RESULTS, THE CRACK APPEARED TO HAVE PROPAGATED RAPIDLY MANY YEARS AGO AND THEN REMAINED STABLE FOR AN EXTENDED PERIOD OF TIME THEREAFTER. MINOR STRESS APPEARS TO HAVE CAUSED A DUCTILE FAILURE IN THE REMAINING METAL LIGAMENT BETWEEN THE OLD EXISTING CRACK AND THE INADEQUATELY FUSED ROOT BEAD WHICH RESULTED IN THE GAS LEAK.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090052 | 2009-05-15 16:21 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1842 | 2009-05-11 | 2009 | VERNAL | UINTAH | UT |  | M.P. 334.7 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69000 | 39321.6806 | 70044.0426 | 21000 | 11115.7407 | 45000 | 55245.283 | 3000 | 3683.0189 | NO | NO | NO | NO | 0 |  | 0 | 0 | 905318 | 2009-05-11 | 733 | 809 | NO | NO | NO | NO | YES | NO | BOYD SCHOW | 8015846741 | BOYD.SCHOW@WILLIAMS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 26 | 0.28 | X-52 |  | DSAW |  | CONSOLIDATED WEST | 1955 | UNDER GROUND |  | 44 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | PIPE DAMAGED DURING ORIGINAL CONSTRUCTION - LAYING ON ROCK CAUSING DENT AND CRACK |  | ON MAY 11, 2009 3:00 PM, AIR PATROL SPOTTED WHAT APPEARED TO BE DEAD VEGETATION ON THE RIGHT OF WAY. TWO VERNAL DISTRICT EMPLOYEES WERE DISPATCHED TO THE SITE TO SEE IF THEY COULD DETERMINE THE CAUSE. AT 6:42 PM, THESE EMPLOYEES INFORMED GAS CONTROL THAT GAS HAD BEEN DETECTED AT THIS SITE (M.P. 334.7) NORTH OF THE VERNAL COMPRESSOR STATION. GAS CONTROL MADE THE REQUIRED NOTIFICATIONS IN ACCORDANCE WITH NORTHWEST PIPELINE GP¿S EMERGENCY NOTIFICATION PROCEDURE. THIS SEGMENT WAS ISOLATED WITH REDUCED PRESSURE EARLY EVENING MAY 11 (LESS THAN 100 PSIG). EARLY MORNING MAY 12, CREWS REDUCED THE PRESSURES FURTHER TO 10 PSIG AND BEGAN EXCAVATION OF THE SUSPECTED LEAK AREA. LATE EVENING (10:30 PM) THE DAMAGED SECTION OF PIPE (APPROXIMATELY 19 FEET) WAS IDENTIFIED AND REMOVED. ON THE MORNING OF MAY 13, ACTIVITIES RESUMED INCLUDING PUP INSTALLATION FOLLOWED BY PURGING, PACKING, AND RETURN TO SERVICE AT 4:35 PM. INITIAL FINDINGS INDICATE THE PIPE WAS SITTING ON A ROCKY OUTCROP. THERE WAS A DENT ON THE BOTTOM OF THE PIPE AND THE LEAK WAS LOCATED IN THE DENT. THE INITIAL PIPE INSPECTION APPEARS FREE OF CORROSION WITH GOOD COATING. THE INTERNAL INSPECTION OF THE PIPELINE LOOKED CLEAN, ALSO FREE OF INTERNAL CORROSION. ON GOING ACTIVITIES INCLUDE ADDITIONAL ILI DATA REVIEW WITHIN THE SEGMENT AND WILL BE INCLUDED IN THE UPCOMING ROOT CAUSE ANALYSIS.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090053 | 2009-05-26 14:21 | ORIGINAL | 31245 |  | OREMET-WAH-CHANG | 1801 BROOKS DRIVE | DISTRICT HEIGHTS | PRINCE GEORGES | MD | 20747 |  | 2009-05-26 | 2009 |  | PRINCE GEORGES | MD | 20702 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 | [7 empty] | NO | NO | NO | NO | NO | NO | RUTH DONALDSON | 3017739511 |  | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO |  |  | 1950 | [8 empty] | UNDER GROUND |  |  | NATURAL FORCES | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090054 | 2009-06-01 15:20 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1637 | 2009-05-07 | 2009 | CELESTINE | DUBOIS | IN | 47575 | 645.63 |  | 38.3643794 | -86.7847489 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461854 | 257797.6674 | 534983.4343 | 45854 | 24271.4846 | 416000 | 510711.9497 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 905613 | 2009-05-14 | 673 | 858 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2008 | 30 | 0.38 | API | 70000 | DSAW |  | BERG | 2004 | UNDER GROUND |  | 72 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 10 | 15 | 2008 | WATER |  | 4 | 1800 | [12 empty] | A SMALL LEAK WAS DISCOVERED, AND CONFIRMED ON ANR'S 30-INCH LINE 1-501, NEAR CELESTINE, IN. THE LINE WAS SUBSEQUENTLY ISOLATED AND BLOWN DOWN. LATER, AN ICE BALL WAS FOUND AT THE LOCATION OF THE LEAK, FOLLOWING EXCAVATION. REMOVAL OF THE ICE BALL REVEALED A POSSIBLE CRACK IN THE GIRTH WELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090055 | 2009-06-04 14:47 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 2055 | 2009-05-07 | 2009 | CLENDENIN | KANAWHA | WV | 25045 |  |  |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | FAILED HEAD-END HEAD GASKET | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726553 | 442883.3873 | 384579.7515 | 726553 | 384579.7515 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 904943 | 2009-05-07 |  |  | NO | NO | NO | NO | YES | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | OTHER | HEAD-END HEAD GASKET | OTHER | GASKET | NO | NO | NO | COMPRESSOR | [10 empty] | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | A GASKET FAILURE CAUSED A LEAK IN UNIT NO. 3 AT CLENDENIN CS. THIS LEAK TRIGGERED THE RED STROBE LIGHT AT THE TOP OF THE UNIT¿S BUILDING. THE STATION OPERATOR SAW THE LIGHT AND MANUALLY ACTIVATED THE ESD SYSTEM. AFTER THE ESD SYSTEM ACTIVATED, THE OPERATOR OBSERVED THAT THE VENT VALVES CONTINUED TO VENT GAS AT A HIGH RATE. THE STATION WAS THEN MANUALLY ISOLATED FROM THE PIPELINE SYSTEM AND SECURED WITHIN 1HR AND 30 MINUTES. A ROOT CAUSE ANALYSIS FOLLOWED THIS EVENT AND IT IDENTIFIED THAT A FAILED GASKET ON HEAD-END HEAD GASKET AT UNIT NO. 3 CAUSED A LEAK, LEADING TO THE MANUAL ACTIVATION OF THE ESD SYSTEM. WATER IN THE AIR SYSTEM REDUCED THE AMOUNT OF AVAILABLE SUPPLY AIR PRESSURE TO THE VALVE OPERATORS FOR FOUR VALVES IN THE ESD SYSTEM, INCLUDING THE STATION ISOLATION VALVES. TO PREVENT A RE-OCCURRENCE OF THIS INCIDENT, THE WORK MANAGEMENT SYSTEM WAS MODIFIED TO INCLUDE INSPECTIONS OF THE AIR SYSTEM FOR WATER INTRUSION. AFTER REPAIRS WERE MADE, THE ESD SYSTEM WAS TESTED TO ENSURE THAT THE SYSTEM WOULD FUNCTION AS DESIGNED. THE TEST WAS SUCCESSFUL.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090056 | 2009-06-05 08:08 | ORIGINAL | 2714 |  | DOMINION TRANSMISSION, INC | 445 W. MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 1155 | 2009-05-07 | 2009 | COXS MILLS | GILMER | WV | 26342 |  |  | 39.024045 | -80.897674 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40000 | 22157.6811 | 48408.5663 | 1000 | 529.321 | 39000 | 47879.2453 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 45 | 904877 | 2009-05-07 | 435 | 822 | NO | NO | NO | NO | YES | NO | SHAWN MILLER | 3046273404 | SHAWN.A.MILLER@DOM.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1950 | 8 | 0.25 | UNKNOWN | 42000 | UNKNOWN |  | UNKNOWN |  | UNDER GROUND |  | 2 | EXCAVATION DAMAGE | OPERATOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [65 empty] | WHILE WORKING A WELL ROAD NEAR WELL #2186 IN RACKET NEWBERNE STORAGE FIELD, A DOZER OPERATOR (EMPLOYED BY KEVIN HERN BACKHOE SERVICE, AND CONTRACTED BY DTI) PUNCTURED PIPELINE TL286 (8¿). AT THE TIME OF THE INCIDENT (11:55 AM ON MAY 7, 2009), THE PIPELINE PRESSURE WAS APPROXIMATELY 435 PSIG. NO FIRE OR EXPLOSION OCCURRED. THE BACKHOE OPERATOR TRAVELLED BY FOOT TO THE LOCATION OF HIS TRUCK DRIVER, WHO THEN NOTIFIED DTI OF THE INCIDENT. OPERATIONS COORDINATED THE ISOLATION AND REPAIR OF THE PIPELINE. THE ROAD WORK WAS IN SUPPORT OF A TOP JOINT REPLACEMENT PROJECT ON WELL #2186. OPERATIONS ISOLATED AND BLEW DOWN THE RUPTURED SECTION BY 1:40 PM.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090058 | 2009-06-05 | ORIGINAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 530 | 2009-04-29 | 2009 | TEAGUE | FREESTONE | TX | 75860 |  |  | 31.632367 | -96.323209 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83474 | 50883.071 | 44184.5401 | 83474 | 44184.5401 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 45 | 904121 | 2009-04-29 | 650 | 800 | NO | NO | YES | NO | NO | NO | MARCUS CHAPMAN DIRECTOR OF COMPLIANCE | 2142062875 | MARCUS.CHAPMAN@ATMOSENERGY.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 8 | 0.25 | API 5H | 46 | SEAMLESS |  |  |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | WASHOUT | [52 empty] | EROSION RESULTING FROM HEAVY RAINS AND RUSHING WATER FROM THE TEAGUE CITY LAKE DAM CAUSED A SECTION OF PIPE TO SEPERATE.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20090059 | 2009-06-08 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 540 | 2009-05-04 | 2009 | PALM CITY | MARTIN | FL | 34997 | MP 810.3 | 1320+82 | 27° 04' 53 | -80° 15' 03 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 7 | 106 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 606360 | 343044.9702 | 646223.4868 | 140600 | 74422.5309 | 325760 | 399926.7421 | 140000 | 171874.2138 | NO | NO | NO | YES | 50 |  | 2 | 20 | 904503 | 2009-05-04 | 853 | 866 | YES | NO | NO | NO | NO | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 18 | 0.25 | 5L | 52000 | ERW | N/A | YOUNGSTOWN SHEET & TUBE | 1959 | UNDER GROUND |  | 30 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | SCC CRACK | STRESS CORROSION CRACKING |  | YES | 1959 | NO | [57 empty] | LEAK WAS REPORTED BY A LOCAL ROAD CONTRACTOR TO A 911 OPERATOR, WHO CONTACTED FLORIDA GAS TRANSMISSION. NTSB HAS TAKEN OVER THE INVESTIGATION. THE APPARENT CAUSE OF THE FAILURE WAS PROPAGATION OF A STRESS CORROSION CRACKING (SCC) FLAW. NTSB IS STILL IN POSSESION OF THE FAILED PIPE SEGMENT. FGT IS WAITING ON NTSB TO DETERMINE IF THEY WILL ISSUE A FINAL REPORT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090060 | 2009-06-08 | ORIGINAL | 18104 |  | CPS ENERGY | 145 NAVARRO | SAN ANTONIO | BEXAR | TX | 78296 | 1013 | 2009-05-06 | 2009 | SAN ANTONIO | BEXAR | TX | 78258 |  |  | 29.620 | -98.516 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 3.2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1519750 | 840641.3944 | 1854058.5794 | 16750 | 8866.1265 | 135000 | 165735.8491 | 1368000 | 1679456.6038 | YES | YES | NO | YES | 60 | THREAT TO THE PUBLIC | 1 | 46 | 904766 | 2009-05-06 | 539 | 931 | NO | YES | NO | NO | NO | NO | MICHAEL RAY FUENTES, PE OPERATIONS ENGINEER | 2102191309 | MRFUENTES@CPSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2009 | 24 | 0.38 | API-5L | 52000 | ERW |  | CPW AMERICA | 2007 | UNDER GROUND |  | 88 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | STORM DRAIN | YES | 5 | 2 | 2009 | ONE-CALL SYSTEM | YES | PAINT | NO | ACCURATE | YES | [36 empty] | H.L. CHAPMAN PIPELINE CONSTRUCTION WAS TRENCHING WITH A LARGE ROCK SAW TO INSTALL A 3'X3' STORM DRAIN BOX CULVERT WHEN THEY PUNCTURED A 24" TRANSMISSION NATURAL GAS PIPELINE THAT WAS OPERATING AT 539 PSIG. THE HIT RESULTED IN A RELEASE OF GAS THAT QUICKLY IGNITED. THE STREETS WERE IMMEDIATELY BLOCKED AND NEARBY BUSINESSES WERE EVACUATED. THERE WERE NO INJURIES REPORTED AND THE MAIN WAS ISOLATED WITHIN AN HOUR. THE FIRE WAS PUT OUT 45 MINUTES LATER. THE MAIN HAD BEEN LOCATED BY CPS ENERGY THE PREVIOUS DAY AND THE MARKS WERE CLEARLY SEEN ON THE DAY OF THE INCIDENT. THE EXCAVATION WAS TAKING PLACE WELL WITHIN THE TOLERANCE ZONE OF THE LOCATE MARKS AS MANDATED BY THE RAILROAD COMMISSION OF TEXAS. NO MECAHNIZED EQUIPMENT SHOULD HAVE BEEN USED WITHIN THIS TOLERANCE ZONE. THE WORK BEING DONE WAS PART OF THE STATE AND COUNTY'S ROAD IMPROVEMENT PROJECT ON BLANCO ROAD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090061 | 2009-06-08 | SUPPLEMENTAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056 | 1525 | 2009-05-05 | 2009 | ROCKVILLE | PARKE | IN | 47872 | VS 1 | 489+66 | 39° 47' 19.87 | -87° 10' 35.14 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2092739 | 1158810.0241 | 2538122.4116 | 44500 | 23554.784 | 1748239 | 2146265.7409 | 300000 | 368301.8868 | NO | NO | YES | YES | 52 | PRECAUTIONARY | 0 | 50 | 904705 | 2009-05-05 | 784 | 800 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1940 | 24 | 0.31 | 5L | 35000 | SMLS | N/A | NATIONAL TUBE | 1940 | UNDER GROUND |  | 144 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1955 | NO | [57 empty] | TENSILE OVERLOAD IN AN AREA OF WALL THINNING DUE TO LOCALIZED CORROSION PITTING AT APPROXIMATELY THE 6:00 O'CLOCK POSITION ON THE PIPE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090062 | 2009-06-09 | SUPPLEMENTAL FINAL | 12498 |  | MIDWESTERN GAS TRANSMISSION COMPANY | 3140 NEIL ARMSTRONG BLVD. SUITE 208 | EAGAN | DAKOTA | MN | 55121 | 1942 | 2008-06-24 | 2008 | WINSLOW | PIKE | IN | 47598 | 0.0 | 0+00 | 38.44173 | -87.17622 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | VENT VALVE FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98908 | 42558.4532 | 36955.8214 | 98908 | 36955.8214 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 10 | 18 | 908043 | 2009-06-09 | 844 | 936 | NO | NO | YES | NO | NO | NO | MARK MICKELBERG | 6519940332 | MARK.MICKELBERG@ONEOK.COM | TRANSMISSION |  |  |  |  | NO | NO | NO | COMPRESSOR |  | 1959 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | OTHER | 110 V PANEL BREAKER | [10 empty] | UNIT CONTROL PANEL LOSS OF POWER THE ELECTRIC BREAKER FOR THE 110 VOLT CONTROL VOLTAGE PANEL TRIPPED WHICH CONTROLS THE 480 VOLT POWER FOR THE UNIT CONTROL VALVES, THUS A LOSS OF POWER WAS EXPERIENCE AT THE ENGINE UNIT CONTROL PANEL, WHICH RESULTED IN THE OPENING OF THE UNIT VENT VALVE AND LOSS OF GAS ESTIMATED AT $98,908.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090063 | 2009-06-15 10:36 | SUPPLEMENTAL FINAL | 19570 | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1605 | 2009-05-15 | 2009 | HOUMA | TERREBONNE | LA | 70360 | 1.52 |  | 28^58'29 | 90^48'78 | OFFSHORE |  | SS | 69 |  | YES | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148640 | 83189.3897 | 169464.0275 | 18640 | 9866.5432 | 130000 | 159597.4843 | 0 | 0 | NO | NO | NO | NO | 0 |  | 238 | 15 | 905730 | 2009-05-15 | 800 | 1250 | YES | NO | NO | NO | NO | NO | JOHNNY LOPEZ | 7132152995 | JOHNNY.LOPEZ@WILLIAMS.COM | GATHERING | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 10.75 | 0.59 | ASTM-A-106 GRADE B |  |  |  |  | 1984 | UNDER WATER |  | 30 | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | THE LEAK ON THE FLANGE WAS CAUSED BY CORRODED BOLTS AND A WORN OUT GASKET. BOTH THE GASKET AND THE BOLTS WERE REPLACED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090064 | 2009-06-16 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY - PO BOX 58900 | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1500 | 2009-06-01 | 2009 | COLTON | WHITMAN | WA | 99113 | 72.32 |  | 46.56508110 | 117.13580441 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320578 | 177181.4377 | 392866.5889 | 1000 | 529.321 | 319578 | 392337.2679 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 30 | 907208 | 2009-06-01 | 624 | 811 | NO | NO | NO | NO | NO | NO | BOYD SCHOW | 8015846741 |  | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 12.75 | 0.25 |  |  | ERW | 2 | (PIPE) KAISER (VALVE) WKM |  | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | LEAK WAS DISCOVERED ON THE LEWISTON LATERAL AT THE TAP FOR THE COLTON M/S, APPROXIMATE MILEPOST 72.3. THE PRELIMINARY ASSESSMENT IS THAT THE LEAK IS UNDERNEATH THE REINFORCING SLEEVE FOR THE TAP AND WILL REQUIRE A CUTOUT TO REPAIR. FOLLOW UP:(12/2/2009) STRESS ENGINEERING SERVICES INC. SUMMARY STATES "NO DEINITIVE SOURCE OF THE REPORTED LEAK FROM THE COLTON PIPELINE SECTION COULD BE IDENTIFIED DRING THE METALLURGICAL EVALUATION. THE ATTACHMENT WELD FOR THE 2-INCH TAP, HOWEVER, DID NOT CONFORM TO ASME B31.8 GUIDELINES FOR FULL ENCIRCLEMENT REINFORCEMENT SINCE IT WAS NOT A FULL PENETRATION WELD." THE PIPE AND COMPONENT WAS CHECKED FOR CRACKING AND NONE WAS FOUND. THE COMPONENT IN IT'S ENTIRETY WAS CUT OUT AND REPLACED WITH A NEW 2" TEE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090065 | 2009-06-22 | ORIGINAL FINAL | 15105 |  | PANHANDLE EASTERN PIPELINE CO | 5444 WESTHEIMER RD | HOUSTON | HARRIS | TX | 77056-5306 | 906 | 2009-05-20 | 2009 | FAYETTE | HOWARD | MO | 65274 | VS 5 | 2440+95 | 39°02' 44" N | 92° 34' 39" W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | PIPE/COUPLING SEPERATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722850 | 403256.9808 | 840040.2152 | 67850 | 35914.429 | 615000 | 755018.8679 | 40000 | 49106.9182 | NO | NO | YES | YES | 14 | PRECAUTIONARY | 1 | 34 | 906220 | 2009-05-20 | 567 | 800 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1940 |  |  | N/A |  | N/A | N/A | N/A |  | UNDER GROUND |  | 60 | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | A SREIES OF EVENTS LEADING TO THE PIPELINE FAILURE BEGAN WITH A TREE FALLING ACROSS THE CREEK BLOCKING FLOW. THE IMPINGED FLOW CREATED AN EROSIONAL CHANNEL THAT DIRECTED STREAM FLOW AT THE LEFT BANK ADJACENT TO THE LINE 200 PIPELINE. THE RESULTING LOSS OF TOE SUPPORT LED TO THE ROTATIONAL SLIDE THAT PULLED THE PIPELINE FROM THE MECHANICAL COUPLING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090066 | 2009-06-15 | SUPPLEMENTAL FINAL | 5304 |  | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER RD. | HOUSTON | HARRIS | TX | 77056 | 1255 | 2009-05-11 | 2009 | MADISON | MADISON | FL | 32340 | MP 17.83 | 941+65 | 30° 23' 48.9 | -83° 21' 26.8 | ONSHORE | 3 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279320 | 159238.0317 | 282820.4232 | 86050 | 45548.071 | 193270 | 237272.3522 | 0 | 0 | NO | NO | NO | YES | 99 | PRECAUTIONARY | 1 | 30 | 905277 | 2009-05-11 | 910 | 975 | NO | NO | NO | NO | YES | NO | MARVIN HOVIS PRINCIPAL ENGINEER | 7139897473 | MARVIN.HOVIS@SUG.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1959 | 3.5 | 0.13 | 5L | 35000 | ERW | N/A | REPUBLIC | 1959 | UNDER GROUND |  | 120 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | LF ERW |  | MATERIAL DEFECT |  | NO | NO | [19 empty] | THE RUPTURE INITIATED AT A THUMBNAIL SHAPED MANUFACTURING DEFECT, WHICH WAS DISTURBED BY AN UNKNOWN OUTSIDE FORCE. THE DEFECT AT THE INITIATION POINT WAS DETERMINED TO BE 0.35 INCHES IN LENGTH. PHMSA'S SYSTEM WOULD NOT ALLOW THE ENTRY OF 0.35, SO THE 0.35 WAS ROUNDED BY CONVENTIONAL ROUNDING RULES TO THE APPROPRIATE WHOLE DIGIT OF 0.0 AND THAT VALUE WAS ENTERED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090067 | 2009-06-23 20:29 | SUPPLEMENTAL FINAL | 32335 |  | REGENCY INTRASTATE GAS LP | 201 OAK STREET | DUBACH | LINCOLN | LA | 71235 | 1745 | 2009-05-25 | 2009 | BRYCELAND | BIENVILLE | LA | 71088 | EASTSIDE COMP STATION |  | 32.40702 N | -92.97530 W | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9227057 | 5099637.7328 | 11308913.0329 | 27057 | 14321.838 | 9200000 | 11294591.195 | 0 | 0 | NO | YES | NO | NO | 0 |  | 1 | 45 | 906619 | 2009-05-25 | 1017 | 1071 | YES | NO | NO | NO | NO | NO | ANGELA MORGAN | 9032436541 | ANGELA.MORGAN@REGENCYGAS.COM | TRANSMISSION | OTHER | WELDED FLANGE UNDER RELIEF VALVE ON COMPRESSOR | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2007 | [11 empty] | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [5 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 1 | 1 | 1950 | WATER |  | 0 | 0 | [12 empty] | A NATURAL GAS FIRE OCCURRED AT REGENCY¿S EASTSIDE COMPRESSOR STATION LOCATED NEAR BRYCELAND IN BIENVILLE PARISH LOUISIANA. EASTSIDE IS A BOOSTER COMPRESSION STATION SITUATED AT APPROXIMATELY THE MIDPOINT OF THE RIGS PIPELINE SYSTEM, WITH NO GAS PROCESSING OR TREATMENT TAKING PLACE ONSITE. THE STATION WAS UNATTENDED WHEN THE FIRE STARTED. THE FIRE BURNED FOR APPROXIMATELY 1 HOUR 45 MINUTES BEFORE BEING COMPLETELY EXTINGUISHED AND DAMAGED 2 OF THE 3 UNITS LOCATED AT THE FACILITY. THE FIRE IGNITED WHEN A WELD UNDER A RELIEF VALVE ON #1 COMPRESSOR BROKE. THE CUMULATIVE EFFECT OF CYCLIC STRESS AS A RESULT OF PRESSURE CONTAINMENT, AXIAL TORQUE AND VIBRATION CAUSED THE PSV CONNECTION SERVING COMPRESSOR THROWS 2, 4 & 6 TO FAIL IN A WELDED JOINT. COMPRESSOR PULSATION BOTTLE SUPPORT DESIGN, PIPING SUPPORT DESIGN, DISCHARGE RELIEF VALVE CONNECTION SIZE AND PIPING CONFIGURATION ALL CONTRIBUTED TO THE UNIT¿S PROPENSITY TO SHAKE. SECTION F5D, F, G - WE ARE UNABLE TO LOCATE THE DATE OF THE TEST, TIME HELD AND TEST PRESSURE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090068 | 2009-06-24 16:09 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 2040 | 2009-05-28 | 2009 | JENA | LA SALLE | LA |  | MP 76.9 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | ESD OF THE COMPRESSOR STATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 909460 | 2009-06-23 | 850 | 858 | YES | NO | NO | NO | NO | NO | LOUIS A. SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | NO FAILURE OCCURRED | STEEL |  | NO | NO | NO | COMPRESSOR |  |  | 30 | 0.3 | API | 60000 |  |  | AOS | 1966 | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | THE CAUSE OF THE UNPLANNED SHUTDOWN WAS A DEFECTIVE FIRE SENSOR. ALL EMERGENCY SHUTDOWN VALVES WERE FOUND TO BE OPERATING PROPERLY. |  | ON THE EVENING OF MAY 28, 2009, THE JENA COMPRESSOR STATION EXPERIENCED AN UNPLANNED EMERGENCY SHUTDOWN OR ESD. THE CAUSE OF THE ESD WAS A DEFECTIVE FIRE SENSOR. ALL ESD VALVES FUNCTIONED PROPERLY, ISOLATING THE STATION FROM THE PIPELINE AND VENTING ALL GAS FROM THE STATION. THE GAS STREAM APPARENTLY CONTAINED SOME TYPE OF CONTAMINANT, LEAVING A RESIDUE ON NEARBY RESIDENCES FOLLOWING THE GAS VENTING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090069 | 2009-06-26 09:22 | SUPPLEMENTAL FINAL | 31451 |  | KINDER MORGAN TEXAS PIPELINE CO | 500 DALLAS ST | HOUSTON | HARRIS | TX | 77002 | 1440 | 2009-06-15 | 2009 | CHOATE | KARNES | TX | 78119 | 144.18 | 7612+86 | 28 45 37.2 | -97 45 01.7 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | CRACK - 1.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114426 | 68545.7599 | 75313.7851 | 93311 | 49391.4707 | 21115 | 25922.3145 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 15 | 908646 | 2009-06-15 | 1033 | 1200 | NO | YES | NO | NO | NO | NO | KRISTIN VAN DER LAAN | 3039147753 | KRISTIN_VANDERLAAN@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 2 | 0.22 | X42 | 42000 |  |  |  |  | UNDER GROUND |  | 54 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | A LEAK WAS FOUND ON A 2" SIDETAP ON INDEX 50 @ RECHAIN STATION 7612+86. THE APPARENT CAUSE WAS THAT THE MAINLINE OVER TIME SETTLED WHILE THE BRACE FOR THE 2" VALVE WAS HELD IN POSITION BY A BRACE. THIS EXERTED FORCE ON THE NIPPLE BETWEEN THE VALVE AND THE MAINLINE RESULTING IN A CRACK NEAR THE WELD ON THE 2" NIPPLE.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090070 | 2009-06-28 | ORIGINAL | 30792 |  | LAMAR OIL & GAS | 4305 BUSINESS HWY 35 SOUTH | ROCKPORT | ARANSAS | TX | 78382 | 915 | 2009-05-28 | 2009 | CORPUS CHRISTI |  | TX |  | N/A | N/A | 270847887 | -97.45277 | OFFSHORE |  | NUECES BAY | 690 | TX | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19800 | 11013.5227 | 23405.6538 | 1292 | 683.8827 | 18508 | 22721.7711 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 906870 | 2009-05-28 | 30 | 1000 | YES | NO | NO | NO | NO | NO | LARRY WASHINGTON PRODUCTION SUPERVISOR | 3617273350 | LWASHINGTON@LAMARCOS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 4.5 | 0.34 | A106B | 35000 | SEAMLESS |  |  |  | UNDER WATER |  | 38 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | WAS NOTIFIED OF TUG HITTING A LINE AND NO POLLUTION AT 9:15AM ON 5/28/09. DEPARTED TO SHORE BASE FACILITY TO DEPRESSURIZE LINE, HAD FIELD BOAT IN ROUTE TO LCOATE LINE TO ZERO AT SHORE BASE 9:50 AM 5/28/09. FIELD BOAT SHUT IN WELLS FEEDING THIS GATHERING LINE AT 10:05A M - 5/28/09. WHAT SMALL SHEEN THAT HAD APPEARED HAD DRIFTED AWAY AND WAS DISSIPATING RAPIDLY, MET TXGLO &amp; USCG ON LOCATION AT 11:15 AM - 5/28/09. NO SHEEN FOUND. NO GAS LEAK ON ARE AFFECTED 6/3/09 REPLACED 40 FT SECTION OF LINE X-RAY BOTH WELDS &amp; 6/4/09 HYDRO LINE TO 125PSI NORMAL OPERATING PSI IS 30PSI, WE PUT BACK ONLINE 6/5/09.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090071 | 2009-06-30 08:58 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124 | 1100 | 2009-06-23 | 2009 | BESSEMER | GOGEBIC | MI | 49911 | 121.26 | SE1/4,SEC3,T47N,R46W | 46.4941417 | -90.0177625 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 792 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 692449 | 400275.1352 | 633611.8005 | 310000 | 164089.5062 | 382449 | 469522.2943 | 0 | 0 | NO | NO | NO | YES | 10 | PRECAUTIONARY | 1 | 30 | 909472 | 2009-06-23 | 923 | 1090 | NO | YES | NO | NO | NO | NO | BYRON WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1965 | 16 | 0.2 | API | 60000 | ERW |  | YOUNGSTOWN | 1965 | UNDER GROUND |  | 45 | CORROSION | CORROSION, EXTERNAL | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | COATED | OTHER | LOCALIZED SCC | STRESS CORROSION CRACKING |  | YES | 1965 | NO | [57 empty] | ON JUNE 23, 2009, AT APPROXIMATELY 11:54 A.M. CDT, NORTHERN'S OPERATION COMMUNICATION CENTER, IN OMAHA, NE RECEIVED AN EMERGENCY CALL REPORTING THAT THERE WAS GAS BLOWING TO ATMOSPHERE AND A POSSIBLE RUPTURE OF THE PIPELINE APPROXIMATELY 1 1/4 MILES NORTH OF THE TOWN OF BESSMER, MICHIGAN. PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE AREA AND IT WAS DETERMINED THAT A PIPE RUPTURE HAD OCCURRED ON THE M432B (MIM10101) 16-INCH CARLTON-WAKEFIELD B LINE @ APPROXIMATE MILEPOST 121.26. LOCAL LAW ENFORCEMENT EVACUATED APPROXIMATELY 15 HOME SITES AND ESTABLISHED A 1/2 MILE SAFE ZONE. THE INCIDENT OCCURRED IN THE SE1/4 OF SECTION 3, T47N, R46W IN GOGEBIC COUNTY, MICHIGAN. LINE PRESSURE AT THE TIME OF THE INCIDENT WAS APPROXIMATELY 923 PSIG. THE EVENT WAS IMMEDIATELY REPORTED TO THE NRC (TICKET # 909472), PHMSA, MICHIGAN PUBLIC SAFETY, EPA AND LOCAL AND STATE AGENCIES. INITIAL INVESTIGATION INDICATED THAT APPROXIMATELY 66 FEET OF PIPE HAD BLOWN OUT OF THE GROUND. IMMEDIATE ACTIONS WERE TAKEN TO ISOLATE THE SEGMENT OF LINE AND ATTEMPT TO MAINTAIN AS MUCH SERVICE TO CUSTOMERS AS POSSIBLE. NORTHERN'S BOTTLE TRUCKS WERE BROUGHT IN AND PLACED IN SERVICE FOR THE TOWN OF BESSEMER AND RAMSAY. GAS SERVICE TO APPROXIMATELY 380 HOMES IN RAMSAY WAS LOST AND HAD TO BE RESTORED BY XCEL ENERGY. SERVICE TO INTERRUPTIBLE BUSINESSES IN BESSEMER WAS INTERRUPTED. THE PIPE IN THE FAILED SEGMENT WAS MANUFACTURED BY YOUNGSTOWN AND INSTALLED IN 1965. IT IS 16-INCH X 0.203 AND 0.250 INCH WALL THICKNESS, GRADE X-60 ELECTRIC RESISTANCE WELDED (ERW) PIPE. REPAIRS WERE MADE BY INSTALLING APPROPRIATE STOPPLE FITTINGS TO ENABLE REPLACEMENT OF APPROXIMATELY 219 FEET OF NEW 16-INCH TESTED, X-60, 0.312 WALL THICKNESS PIPE. THE NEW PIPE WAS PRESSURE TESTED TO A MINIMUM TEST PRESSURE OF 1620 PSIG. A RETURN TO SERVICE PLAN WAS DEVELOPED AND SUBMITTED TO THE CENTRAL REGION OFFICE OF PHMSA FOR REVIEW. PHMSA DID NOT IDENTIFY ANY CONCERNS WITH THE PLAN THEREFORE NORTHERN WAS AUTHORIZED TO RE-START THE CARLTON TO MARQUETTE LINE AT A REDUCED PRESSURE AS REQUIRED BY A CORRECTIVE ACTION ORDER ISSUED BY THE ASSOCIATE ADMINISTRATOR FOR PIPELINE SAFETY. THE CORRECTIVE ACTION ORDER REQUIRES THAT THE PRESSURE AT THE FAILURE SITE AND DOWNSTREAM OF THE FAILURE SITE IS NOT TO EXCEED 80% OF THE OPERATING PRESSURE IMMEDIATELY PRIOR TO THE FAILURE. SPECIFICALLY, THE PRESSURE AT THE FAILURE SITE IS NOT TO EXCEED 739 PSIG. THIS PRESSURE RESTRICTION WILL REMAIN IN EFFECT UNTIL WRITTEN APPROVAL TO INCREASE THE PRESSURE OR RETURN THE PIPELINE TO ITS PRE-FAILURE OPERATING PRESSURE IS OBTAINED FROM THE REGIONAL DIRECTOR, PHMSA. PIECES OF THE FAILED PIPE HAVE BEEN SENT TO BRYAN LAB IN HOUSTON, TX FOR FAILURE ANALYSIS. AN ADDITIONAL SECTION OF PIPE WERE SENT TO KEIFNER & ASSOCIATES LABORATORY IN OHIO. KEIFNER AND BRYAN LABS WILL ASSIST NORTHERN WITH IDENTIFYING THE CAUSE OF THE FAILURE AND THE INSPECTION TECHNIQUES NORTHERN WILL USE TO IDENTIFY OTHER RISKS TO THE PIPELINE SYSTEM. ADDITIONAL SUPPLEMENTAL REPORTS WILL BE FILED AS THE ROOT CAUSE AND FINAL, ACCURATE COST OF GAS LOSS/REPAIRS ARE DETERMINED. SUPPLEMENTAL/FINAL REPORT: THIS REPORT IS BEING SUBMITTED TO UPDATE THE COTS INCURRED IN THE REPAIR PROCESS OF THIS INCIDENT. IN ADDITION, THE ROOT CAUSE HAS BEEN IDENTIFIED AS STRESS CORROSION CRACKING (SCC). A CORRECTIVE ACTION ORDER (CAO) WAS ISSUED BY PHMSA, RE; CPF NO.3-2009-1010H. ADDITIONAL ACTIONS AND COST ARE BEING INCURRED TO COMPLY WITH THE CAO, AND MUST BE COMPLETED PRIOR TO RESTORATION OF THE LINE PRESSURE BACK TO IT'S CAPABILITY PRIOR TO THE RUPTURE. THESE ACTIONS AND COST ARE BEING ADDRESSED VIA QUARTERLY REPORTS TO THE DIRECTOR, CENTRAL REGION OF OPS. AS FAR AS COST AND REPAIR ACTIONS TAKEN TO ADDRESS THE RUPTURE EVENT, PER THIS 7100 REPORT, THERE ARE CONSIDERED COMPLETE. SUPPLEMENTAL/FINAL REPORT: DO TO THE IDENTIFICATION OF ADDITONAL COST, FROM EMPLOYEE EXPENSE AND OUTSIDE SERVICES, THIS SUPPLEMENTAL REPORT IS BEING SUBMITTED TO CORRECT THE PREVIOUS TOTAL COST OF $674,379 TO $692, 449. 09/18/2012 ADDED INCIDENT COORDINATES AS PER REQUEST OF JIM BUNN, PHMSA.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090072 | 2009-07-07 | ORIGINAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1450 | 2009-04-21 | 2009 |  | MATAGORDA | TX |  |  |  | N 28 28.99.404 | W 95 59.583 | OFFSHORE |  | BRAZOS | 445°L | TX | YES | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 30388.3648 | 67522.0126 | 0 | 0 | 55000 | 67522.0126 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 903371 | 2009-04-21 | 350 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER VP-MANAGER | 8325523600 | JSIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | API5L | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON APRIL 21, 2009 AT APPROX. 2:50 OM, PANTHER BECAME AWARE OF A POTENTIAL NATURAL GAS LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 445-L. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE THAT SAME AFTERNOON. THE FOLLOWING DAY A BOAT WENT TO THE LEAK AREA TO GATHER MORE INFO AND EXACT COORDINATES TO COORDINATE REPAIRS AND NO SHEEN WAS REPORTED. UPON INVESTIGATION, A PINHOLE LEAK PROBLEM WAS DISCOVERED ON THE PANTHER PIPELINE. PANTHER REPAIRED THE LEAK WITH A CLAMP ON 5/2/09 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL ON 5/3/09.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20090073 | 2009-07-08 | SUPPLEMENTAL FINAL | 4060 |  | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | CUYAHOGA | OH | 44101 | 730 | 2009-06-08 | 2009 | NEW PHILADELPHIA | TUSCARAWAS | OH | 44663 | NEW PHILLY STATION |  | N40'30.587 | W081'26.188 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1000 | 552.5157 | 1227.673 | 0 | 0 | 1000 | 1227.673 | 0 | 0 | NO | YES | NO | NO | 0 |  | 0 | 30 | 907918 | 2009-06-08 | 5 | 437 | NO | YES | NO | NO | NO | NO | ROBERT MAJIKAS - MANAGER GAS OPERATIONS | 2167365693 | ROBERT.P.MAJIKAS@DOM.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 8 | 0.32 | API-5L | 16 | ERW |  |  |  | OPEN DITCH |  | 36 | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | INADEQUATE SAFETY PRACTICES |  | 0 | 0 | Y | 1 |  |  | PIPELINE INVOLVED WAS LINE # 256, APPROXIMATELY 5 MILES ON INTRASTATE TRANSMISSION, 8" STEEL PIPE INSTALLED FROM 1953-1980 WITH A 437# MAOP, OPERATING AT 150#. LINE WAS BEING REPLACED AS PART OF DOMINION'S INFRASTRUCTURE REPLACEMENT PROGRAM WITH 12" STEEL. ON SATURDAY JUNE 6, 2009 THE 8" LINE WAS REMOVED FROM SERVICE BY VALVING OUT 7 PRODUCTION FEEDS ALONG THE 5 MILES, VALVING OUT THE MAIN FEED ON THE FURTHERMOST EASTERN POINT OF THE LINE AND OPENING A 3" VENT AT THAT LOCATION, AND REMOVING APPROXIMATELY 25' OF PIPE AT THE FURTHERMOST WESTERN POINT OF THE LINE. AT THE FURTHERMOST WESTERN POINT A FOAM BODY/URETHANE COATED PIG AND A 8" DRESSER CAP WAS INSTALLED DUE TO MINOR DRIFT OCCURRING AND TO ALLOW FOR WELDING ON THE 12" LINE AT THAT LOCATION. ON MONDAY, JUNE 8, 2009 AT APPROXIMATELY 7:30AM CONTRACTORS, WHILE PREPARING TO PURGE THE 8" LINE OF GAS/FLUIDS REMAINING IN THE LINE, WERE REMOVING THE DRESSER CAP, RELEASING APPROXIMATELY 5# OF PRESSURE INTO AN OPEN DITCH WHERE ADDITIONAL WORK WAS BEING PERFORMED. ADDITIONAL WORK CONSISTED OF PRE-HEATING WAX WITH AN OPEN TORCH TO COAT THE 12" LINE AND PREPARING TO ATTACH TEST WIRES TO THE 12" WITH A CAD WELD. A FLASH FIRE OCCURRED INJURING TWO CONTRACTOR PERSONNEL IN THE DITCH. INDIVIDUAL REMOVING THE DRESSER CAP RECEIVED BURNS TO BOTH HANDS AND WAS TREATED AND RELESSED AT A LOCAL HOSPITAL. INDIVIDUAL PREPARING TO ATTACH TEST WIRES APPROXIMATELY 20' FEET FROM THE END CAP RECEIVED 2ND AND 3RD DEGREE BURNS TO HIS BODY AND WAS LIFE-FLIGHTED TO A BURN CENTER FOR TREATMENT. UPDATED BY PHMSA ON 12/14/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090074 | 2009-07-07 | ORIGINAL FINAL | 19235 |  | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1500 | 2009-06-08 | 2009 |  |  | LA |  | MP 27.19 | 1435+59 | 29.4722 | -89.0562 | OFFSHORE |  | BRETON SOUND | 42 | LA | NO | NO | INTERSTATE | OTHER | 1-INCH BODY BLEED ON 10-INCH BALL VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130000 | 71884.0962 | 158899.1323 | 1000 | 529.321 | 129000 | 158369.8113 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 907954 | 2009-06-08 | 971 | 1440 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@SPECTRAENERGY.COM | TRANSMISSION | OTHER | 1-INCH BODY BLEED ON 10-INCH BALL VALVE | STEEL |  | NO | NO | NO | OTHER | VALVE | 2004 |  |  | N/A |  | N/A | BALL | CAMERON | 2004 | UNDER WATER |  | 0 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | 1-INCH BODY BLEED ON 10-INCH BALL VALVE FAILED TO MAINTAIN SEAL. |  | <P>A LEAK OCCURRED IN A 1-INCH BODY BLEED OF A 10-INCH BALL VALVE IN BRETON SOUND BLOCK 42 UNDER 20 FEET OF WATER ON THE TEXAS EASTERN LINE 40-B. REPLACEMENT OF THE 1-INCH BODY BLEED ELIMINATED THE LEAK. </P>
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090075 | 2009-07-13 15:54 | SUPPLEMENTAL FINAL | 31531 |  | ONEOK WESTEX TRANSMISSION, INC. | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103 | 545 | 2009-06-16 | 2009 | GOLDSMITH | ANDREWS | TX | 79741 |  | 1195+29 | 32.22872 | -102.24731 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252421 | 149978.3211 | 181220.4818 | 184248 | 97526.3333 | 68173 | 83694.1484 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 30 | 908725 | 2009-06-16 | 585 | 658 | NO | YES | NO | NO | NO | NO | PATTI FORD | 9185887131 | PATTI.FORD@ONEOK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1966 | 20 | 0.25 | X-42 | 1050 |  |  |  |  | UNDER GROUND |  | 32 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | GENERAL CORROSION |  | OTHER | ELECTROLYTE / COATING ISSUES | YES | 1966 | NO | [57 empty] | THE WESTEX PIPELINE 0441-000 RUPTURED AT APPROXIMATELY 0545 ON JUNE 16, 2009 AT LINE PRESSURE OF 585 PSIG WITH NO IGNITION OR EXPLOSION. REPAIR OF THE LINE WAS HAMPERED BY WATER FLOODING THE IMMEDIATE AREA FROM AN 18INCH FIBERGLASS WATER LINE LOCATED 36 INCHES BELOW THE RUPTURED 20INCH NATURAL GAS LINE. A 4INCH FIBERGLASS WELL FLOW LINE WAS ALSO DAMAGED. THE RUPTURED PIPE SECTION WAS SENT TO AN INDEPENDENT THIRD PARTY LAB FOR FAILURE ANALYSIS. THE CAUSE OF FAILURE WAS SHALLOW PIT CORROSION ON THE OUTSIDE DIAMETER OF THE PIPE WHICH REDUCED THE WALL THICKNESS TO THE POINT OF FAILURE. DUE TO THE RUPTURE DISRUPTING THE ENVIRONMENT AROUND THE FAILURE SITE, IT WAS NOT CLEAR WHAT INITIALLY CAUSED THE GENERAL CORROSION. THERE WAS ELECTROLYE AND / OR LOCALIZED COATING ISSUES SINCE THERE WAS GENERAL CORROSION PRESENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090076 | 2009-07-15 16:29 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1915 | 2009-06-19 | 2009 | DILKON | NAVAJO | AZ | 86047 | 188.1 | LINE 1201 | 35.34141N | -110.56786W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92298 | 54835.5937 | 66314.0677 | 67298 | 35622.2438 | 25000 | 30691.8239 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 909161 | 2009-06-19 | 707 | 845 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1953 | 30 | 0.34 | API | [5 empty] | UNDER GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | LEAK DEVELOPED AT LOCATION OF OLD PRIOR DAMAGE OF UNKNOWN SOURCE. |  | EL PASO NATURAL GAS COMANY'S 30" PIPELINE NO. 1201 BEGAN LEAKING AT A POINT OF DAMAGE SUSTAINED AT SOME TIME OVER ITS LIFE BUT OF UNKNOWN ORIGIN. THE DAMAGE WAS IN THE FORM OF A GOUGE. THE COST OF GAS LOSS DUE TO BLOW DOWN AND THE COST OF REPAIRS COMBINED TO QUALIFY THIS AS AN INCIDENT UNDER 49 CFR PART 191. PIPE WAS REPAIRED BY A FULL ENCIRCLEMENT WELDED SLEEVE AND PLACED BACK INTO SERVICE. UPDATED BY PHMSA ON 12/14/2015 PER OPERATOR'S MARK UP(PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090077 | 2009-07-21 15:05 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1915 | 2009-06-26 | 2009 | DENVER CITY | GAINES | TX | 79323 | 204+4179 | LINE NO. 1102 |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88968 | 51864.3717 | 76074.2363 | 47468 | 25125.8086 | 41500 | 50948.4277 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 0 | 909905 | 2009-06-26 | 498 | 624 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 30 | 0.25 | API 5L | 52000 | DSAW |  | CONSOLIDATED | 1948 | UNDER GROUND |  |  | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | NO | [19 empty] | EVIDENCE OF A LEAK WAS REPORTED NEAR EL PASO NATURAL GAS COMPANY'S 30" 1102 PIPELINE BY A LANDOWNER IN GAINES COUNTY, TEXAS. COMPANY PERSONNEL INVESTIGATED BY EXCAVATING THE PIPELINE AND FOUND ABOUT A 5-INCH LONG CRACK IN A CIRCUMFERENTIAL GIRTH WELD. THE PIPE WAS ISOLATED AND VENTED TO A SAFE PRESSURE TO ALLOW INSTALLATION OF A FULL ENCIRCLEMENT SLEEVE, RESULTING IN REPAIR AND THE PIPELINE BEING PLACED BACK INTO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090078 | 2009-07-21 16:36 | SUPPLEMENTAL FINAL | 31703 |  | CHESAPEAKE MIDSTREAM PARTNERS, L.P. | PO BOX 18312 | OKLAHOMA CITY | OKLAHOMA | OK | 73154-0312 | 314 | 2009-07-13 | 2009 | SEARCY | WHITE | AR | 72143 | 450 NORTH OF GENTRY VALVE | 05 + 14 | 35.31460 | - 91.78937 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 20479.0939 | 29001.5141 | 20000 | 10586.4198 | 15000 | 18415.0943 | 0 | 0 | NO | NO | NO | YES | 3 | PRECAUTIONARY | 0 | 21 | 911402 | 2009-07-13 | 1184 | 1300 | NO | YES | NO | NO | NO | NO | DONALD E. MCCOY | 4059354467 | DON.MCCOY@CHK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2006 | 10 | 0.25 | API-5L | 52000 | ERW |  | NIPPON | 2005 | UNDER GROUND |  | 48 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | EXCAVATION OF THE FAILED SECTION OF PIPE REVEALED CHARRED TIMBERS ON TOP OF AND AROUND THE PIPE. SINCE NO IGNITION OR FIRE OCCURRED AT THIS INCIDENT, THE CHARRED TIMBERS ARE POSSIBLY THE RESIDUAL FROM AN OLD BURN PILE. THE EXCAVATION ALSO REVEALED GOUGES ON THE TOP OF THE PIPE WALL THAT RAN IN THE LONGITUDINAL DIRECTION OF THE PIPE FOR APPROXIMATELY 77 INCHES AS WELL AS A QUARTER SIZED DENT NEAR THE BEGINNING OF ONE OF THE GOUGES AND DIRECTLY BESIDE THE FAILURE. IT APPEARS THAT THE GOUGES AND DENT COULD HAVE BEEN MADE BY THE TEETH OF A TRACK HOE BUCKET AND THAT THE DAMAGE COULD HAVE OCCURRED WHILE USING A TRACK HOE TO BURY THE CHARRED TIMBERS. SINCE THE 70 INCH LONGITUDINAL SPLIT IN THE PIPE WAS NOT ALONG THE SEAM OF THE PIPE AND WAS ON A DENT AND LONGITUDINAL GOUGE, THE FAILURE WAS PROBABLY THE RESULT OF THE DAMAGE (DENT AND GOUGES) IN THE PIPE WALL.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090079 | 2009-07-23 10:05 | ORIGINAL FINAL | 31711 |  | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HWY. 56 | OWENSBORO | DAVIESS | KY | 42301 | 1645 | 2009-07-09 | 2009 | POND CREEK | GRANT | OK | 43766 |  | 120/815815 | 36.687536 | -97.841605 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | GASKET LEAK ON MAIN LINE VALVE. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57442 | 33279.7285 | 51643.5362 | 27030 | 14307.5463 | 29912 | 36722.1535 | 500 | 613.8365 | NO | NO | NO | NO | 0 |  | 0 | 0 | 911140 | 2009-07-09 | 798 | 900 | NO | YES | NO | NO | NO | NO | BRAD CARTER | 2708524438 | BRAD.CARTER@SSCGP.COM | TRANSMISSION | OTHER | GASKET | STEEL |  | NO | NO | NO | PIPELINE |  | 1971 | 26 | 0.25 | APIX | 1250 | DOUBLE SUBMERGED ARC WELD | GATE VALVE (SLAB) | M&J | 1970 | UNDER GROUND |  | 30 | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | DURING A YEARLY VALVE INSPECTION, ONE OF THE VALVES DEMONSTRATED A PROBLEM IN THE WAY THAT IT OPERATED. WHEN THE VALVE WAS EXCAVATED A PROBLEM WAS FOUND WITH THE GASKET. WHEN THE FLANGE WHERE THE GASKET WAS LOCATED WAS TIGHTENED, THE GASKET STARTED LEAKING. IN ORDER TO PROPERLY REPAIR THE GASKET LEAK, 14 MILES OF 26" PIPE HAD TO BE BLOWN DOWN. THE GAS LOSS AND COST OF REPAIR RESULTED IN SOUTHERN STAR REPORTING THIS AS AN INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090080 | 2009-07-27 10:50 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACCORKLE AVE SE | CHARLESTON | KANAWHA | WV | 25314 | 1220 | 2009-06-26 | 2009 | RANSOM | PIKE | KY |  | LINE KA VALVE SEGT 7070 | 1495+80 | 37.57472 | -82.16048 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396563 | 236499.421 | 273959.8663 | 304846 | 161361.3858 | 91717 | 112598.4805 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 909853 | 2009-06-26 | 240 | 374 | NO | YES | NO | NO | NO | NO | MARY S. FRIEND | 3043572475 | MFRIEND@NISOURCE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1975 | 20 | 0.25 |  | 42000 | DSAW |  | KAISER STEEL | 1975 | UNDER GROUND |  |  | NATURAL FORCES | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [10 empty] | SUBSIDENCE | [54 empty] | PIPE SPLIT CIRCUMFERENTIALLY ON UNDERSIDE OF PIPE NEAR CHANGE IN SLOPE IN MINE AREA. EVALUATIONS SUGGEST THAT THE PIPELINE FAILED DUE TO BUCKLES.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090081 | 2009-07-28 15:25 | SUPPLEMENTAL | 11272 |  | LAVACA PIPELINE CO | 103 FANIN ROAD | POINT COMFORT | CALHOUN | TX | 77978 |  | 2009-07-22 | 2009 | [6 empty] | 28-37.98 | 96-32.59 | OFFSHORE |  | LAVACA BAY | 26 | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 4434.3888 | 9646.7957 | 250 | 132.3302 | 7750 | 9514.4654 | 0 | 0 | NO | NO | NO | NO | 0 |  | 11 | 0 | 912338 | 2009-07-22 | 450 | 600 | NO | YES | NO | NO | NO | NO | ROBERT C SERRATA | 3619878914 | ROBERTS@FTPC.FPCUSA.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 10 | 0.37 | WT GRADE B | 2042 | SML | N/A | N/A | 1952 | UNDER WATER |  | 168 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | WERE NOT ABLE TO SEE | OTHER | N/A | YES | 1952 | NO | [57 empty] | THE DIVERS WERE NOT ABLE TO SEE THE PIPE TO DETERMINE WHAT KIND OF CORROSION CAUSED THE LEAK.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090082 | 2009-07-30 10:58 | SUPPLEMENTAL FINAL | 32436 |  | MIDCONTINENT EXPRESS PIPELINE LLC | 500 DALLAS ST. SUITE 1000 | HOUSTON | HOUSTON | TX | 77002 | 2358 | 2009-07-02 | 2009 | DELHI | MADISON | LA | 71232 |  |  | 32.46606 | -91.4757 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275500 | 167907.4307 | 146177.1081 | 275000 | 145563.2716 | 500 | 613.8365 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 15 | 910-536 | 2009-07-03 | 1275 | 1332 | NO | YES | NO | NO | NO | NO | KRISTIN VAN DER LAAN | 3039147753 | KRISTIN_VANDERLAAN@KINDERMORGAN.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2009 | 1 | 0.02 | SCHEDULE 80 | 35000 |  |  |  |  | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | FITTING | [9 empty] | MATERIAL DEFECT |  | NO | YES | 3 | 20 | 2009 | WATER |  | 8 | 1859 | [12 empty] | A NPS 2X1 SCHEDULE 80 SWAGED NIPPLE IN THE POWER GAS ASSEMBLY FOR MAINLINE VALVE 36-01 FRACTURED DURING LINE PACKING OF THE MIDCONTINENT EXPRESS PIPELINE ON JULY 2, 2009. THE SWAGED NIPPLE FRACTURED DUE TO VIBRATION-INDUCED FATIGUE AT THE TOE OF A FILLET WELD CONNECTION TO A NPS 1 SOCKET WELD TEE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090083 | 2009-08-03 14:33 | ORIGINAL FINAL | 18484 |  | SOUTHERN CALIFORNIA GAS CO | 555 W FIFTH STREET | LOS ANGELES | LOS ANGELES | CA | 90013 | 1133 | 2009-08-03 | 2009 | WESTMINSTER | ORANGE | CA |  | 43+776 |  | 33.771399 | -118.007350 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63000 | 34922.5949 | 75946.6923 | 2000 | 1058.642 | 61000 | 74888.0503 | 0 | 0 | YES | NO | NO | NO | 0 |  | 6 | 30 | 911623 | 2009-07-15 | 180 | 200 | NO | NO | NO | YES | NO | NO | W. JEFF KOSKIE | 2132443283 | WKOSKIE@SEMPRAUTILITIES.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 16 | 0.25 | GRADE A | 21 |  |  |  |  | UNDER PAVEMENT |  | 18 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ROAD WORK |  | YES | 5 | 8 | 2009 | ONE-CALL SYSTEM | YES | PAINT |  | ACCURATE | YES | [36 empty] | ON JULY 14, 2009 A 16 INCH STEEL NATURAL GAS SUPPLY LINE WAS DAMAGED WHEN A WHEN BY MECHANIZED GRADING EQUIPMENT. THE FACILITIES HAD BEEN PROPERLY LOCATED AND MARKED IN RESPONSE TO A USA REQUEST. HOWEVER, THE REQUEST HAD EXPIRED, AND SOCALGAS WAS UNAWARE THAT EXCAVATING ACTIVITY WAS TAKING PLACE ON THE DAY OF THE INCIDENT. REPAIRS WERE COMPLETED WITH NO GAS IGNITION AND NO INJURIES. ONE CUSTOMER OUT OF SERVICE WAS RESTORED. THIS INCIDENT BECAME REPORTABLE TO PHMSA ON JULY 15, 2009 WHEN CONSIDERABLE PIPE GOUGING WAS DISCOVERED, ABOVE AND BEYOND THE INITIAL DAMAGE, NECESSITATING REMOVAL AND REPLACEMENT OF PIPELINE SECTION. THIS INCREASED REPAIR ACTIVITY TRIGGERED REPORTING DUE TO POTENTIAL OF EXCEEDING $50,000 IN TOTAL COSTS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090084 | 2009-08-05 11:30 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 459 | 2009-07-12 | 2009 | CHESTER SPRINGS | CHESTER | PA | 19425 | 2006+77 |  | -75.6693 | 40.1252 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | MALFUNCTION OF A COMPONENT. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115050 | 70130.787 | 60898.3796 | 115050 | 60898.3796 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 43 | 911330 | 2009-07-12 | 757 | 1200 | NO | YES | NO | NO | NO | NO | MARK A NEWMAN | 3047228475 | MNEWMAN@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1983 | [5 empty] | PNEUMATIC,TWO PISTON, SPRING RETURN | SHRADER BELOWS | 1983 | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | SEVERAL STUD BOLTS USED TO AFFIX A POWER CYLINDER TO COMPRESSOR UNIT# 3 (INGERSOLL-RAND KVS) BROKE CAUSING A NATURAL GAS LEAK IN THE FUEL GAS SUPPLY HEADER. THE ELEVATED GAS LEVELS IN THE COMPRESSOR BUILDING AUTOMATICALLY ACTIVATED THE STATION EMERGENCY SHUTDOWN (ESD) SYSTEM. AN EMERGENCY VALVE FAILED TO CLOSE FOR APPROXIMATELY 103 MINUTES WHICH RESULTED IN APPROXIMATELY 18,923 MCF OF GAS WAS LOST AT AN APPROXIMATE VALUE OF $115,050. THE FAILURE OF THE POWER CYCLINDER STUD BOLTS IS INHERENT WITH THE INGERSOLL-RAND KVS ENGINES. THE EVENT ELEVATED TO A REPORTABLE EVENT WHEN THE PNEUAMTIC FIRE VALVES FAILED TO CLOSE. PLANNED QUATERLY MAINTENANCE HAS BEEN SCHEDULED TO MAKE SURE THESE VALVES CLOSE WHEN NECESSARY.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090085 | 2009-08-06 11:38 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1147 | 2009-08-04 | 2009 | GIBSON | TERREBONNE | LA | 70356 | 101.74 |  | N29^36'003 | W90^52'55 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 58233.8038 | 86263.0415 | 52272 | 27668.6667 | 47728 | 58594.3748 | 0 | 0 | NO | NO | NO | NO | 0 |  | 14 | 43 | 913784 | 2009-08-05 | 653 | 2000 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1967 | 30 | 0.5 | API-5LX | 60000 | DOUBLE SEAM SUBMERGED ARC WELD |  | BETH | 1967 | ABOVE GROUND |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | OTHER | N/A | OTHER | N/A | YES | 1967 | YES | 0 | 1 | [55 empty] | THE ULTRASONIC EXAMINATION FOUND THAT THE SIGNIFICANT CORROSION IN THE TERREBONNE VALVE YARD WAS CONFINED TO THE ISOLATED SECTION OF THE MANIFOLD, WHICH WAS A LONG DEAD LEG CONNECTED TO THE INCOMING 30” LINE C. TO EFFECT THE REPAIR, APPROXIMATELY 155 FEET OF PIPE FORMING THIS DEAD LEG WAS REMOVED PERMANENTLY, INCLUDING THE BADLY CORRODED SECTION OF PIPE. THERE WERE THREE OPEN ENDS LEFT BY THE CUT-OUT. AT TWO LOCATIONS, THE OPEN ENDS WERE FITTED WITH BLIND FLANGES, AND THE REMAINING OPEN END WAS REMOVED BY NEW CONSTRUCTION PIPING MODIFICATION. THIS WORK WAS COMPLETED BY A CONSTRUCTION CREW ON-SITE TO PERFORM OTHER PLANNED MODIFICATIONS TO THE LINE C SCRAPER TRAP. THE WORK ON THE REPAIR (CUT-OUT) WAS COMPLETED BY SEPTEMBER 15, 2009.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090086 | 2009-08-14 15:58 | SUPPLEMENTAL FINAL | 15348 |  | PEOPLES GAS SYSTEM INC | 702 N. FRANKLIN STREET | TAMPA | HILLSBOROUGH | FL | 33602 | 752 | 2009-08-11 | 2009 | JACKSONVILLE | DUVAL | FL | [5 empty] | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 0.5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 110680.8622 | 243359.2248 | 3115 | 1648.8349 | 196885 | 241710.3899 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 8 |  |  | 475 | 500 | YES | NO | NO | NO | NO | NO | TODD WEIDLEY | 8132284577 | TWEIDLEY@TECOENERGY.COM | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1987 | 18 | 0.31 | X42 | 42000 | ERW |  |  | 1986 | UNDER WATER |  |  | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | RAILROAD |  | YES | 7 | 13 | 2009 | ONE-CALL SYSTEM | YES | PAINT | NO | INACCURATE | YES | [36 empty] | CONTRACTOR PERFORMING WORK FOR CSX AT RAILROAD RIVER CROSSING. IN PREPARING TO PERFORM WORK A BARGE SPUD GLANCED OFF CONCRETE COATED MAIN CREATING A SMALL HOLE AND LEAK. PIPELINE HAD BEEN INCORRECTLY MARKED BY DIVERS HIRED BY THE OPERATOR TO LOCATE THE FACILITY.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090087 | 2009-08-19 16:39 | SUPPLEMENTAL FINAL | 32178 |  | VINTAGE PRODUCTION CALIFORNIA LLC | 9600 MING AVE , SUITE 300 | BAKERSFIELD | KERN | CA | 93311 | 253 | 2009-07-19 | 2009 | SANTA PAULA | VENTURA | CA | [5 empty] | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20900 | 11832.8395 | 22166.6049 | 5000 | 2646.6049 | 15900 | 19520 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 25 |  |  | 210 | 500 | NO | YES | NO | NO | NO | NO | WILL HILL | 6618698001 | WILL_HILL@OXY.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 8 | 0.25 | [6 empty] | UNDER PAVEMENT |  | 4 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | BARE | OTHER | EXTERNAL UT ONLY | OTHER | C02 AND WET GAS - TOP LINE CORROSION | YES | 1972 | NO | [57 empty] | VINTAGE PRODUCTION CALIFORNIA LLC ACQUIRED THE SOUTH MOUNTAIN PIPELINE SYSTEMS NOVEMBER 2006. RECORDS FOUND INDICATED THAT THE PIPELINE HAS BEEN USED BY PREVIOUS OPERATORS FOR TRANSPORTATION OF MIXTURE OF TWO STREAM OF GAS , ONE WET GAS AND THE OTHER HIGH CO2 CONTENT GAS AND CORROSION INHIBITOR OIL SOLUBLE WAS USED. VPC IMPLEMENTED ENHANCED EXTERNAL CORROSION PROTECTION BY IMPRESS CURRENT AND CHANGED CHEMICAL CORROSION INHIBITOR FROM OIL SOLUBLE TO WATER SOLUBLE TYPE . ULTRASONIC THICKNESS INSPECTION ON THE PIPELINE WALL SHOWED PITTING TOP OF THE PIPELINE TYPICALLY KNOW AS TOP OF THE LINE CORROSION. IT IS LIKELY THAT THE DEEP CORROSION PITTING WAS GENERATED ON DURING PREVIOUS CHEMICAL INHIBITOR TYPE
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090088 | 2009-08-25 16:30 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 144 | 2009-07-30 | 2009 | POCASSET | GRADY | OK | 73079 |  | ADWEST 254+26 | +35.185863 | -97.999560 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELEASE DUE TO LIGHTNING STRIKE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2503 | 1423.0545 | 2581.924 | 703 | 372.1127 | 1800 | 2209.8113 | 0 | 0 | NO | YES | NO | YES | 2 | THREAT TO THE PUBLIC | 2 | 0 | 913200 | 2009-07-30 | 100 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT , DOT COMPLIANCE MANAGER | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | DOMESTIC TAP | 1974 | [8 empty] | ABOVE GROUND |  |  | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE THERE WAS AN IGNITION OF LEAKING GAS AND EMERGENCY RESPONDER PERSONNEL EVACUATED 2 PERSONS FROM THEIR HOME.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090089 | 2009-08-25 | ORIGINAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 436 | 2009-07-20 | 2009 | DENTON | DENTON | TX | 76205 |  |  | 31.19778 | -97.06639 | ONSHORE | 2 |  |  |  | NO | NO | INTRASTATE | OTHER | COMPRESSOR VALVE BOLT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500108 | 276323.695 | 613893.6447 | 108 | 57.1667 | 500000 | 613836.478 | 0 | 0 | NO | NO | YES | NO | 0 |  | 0 | 45 | 912145 | 2009-07-20 | 350 | 500 | YES | NO | NO | NO | NO | NO | MARCUS CHAPMAN DIRECTOR OF COMPLIANCE | 2142062875 | MARCUS.CHAPMAN@ATMOSENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR | [13 empty] | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | CYLINDER BOLT BACKED OUT RELEASING GAS INTO BUILDING |  | A 1-INCH THREADED CRANK END COMPRESSOR CYLINDER SUCTION VALVE BOLT SEPARATED FROM THE COMPRESSOR CYLINDER ALLOWING GAS FROM THE COMPRESSOR TO ESCAPE INTO THE COMPRESSOR BUILDING. THE GAS THAT ACCUMULATED IN THE COMPRESSOR BUILDING WAS IGNITED AND CAUSED AN EXPLOSION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090090 | 2009-08-27 15:12 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 130 | 2009-08-09 | 2009 |  |  | LA |  |  |  | X=2064690 | Y=-152156 | OFFSHORE |  | SHIP SHOAL | 300 |  | YES | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1858000 | 1029426.8227 | 2246098.7538 | 50000 | 26466.0494 | 1808000 | 2219632.7044 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 914309 | 2009-08-09 | 700 | 1300 | YES | YES | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1992 | 8.63 | 0.41 | API | 42000 | SEAMLESS |  | U.S. STEEL | 1992 | UNDER WATER |  | 0 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A RUPTURE OCCURRED IN THE 8-IN. RISER PIPE ON ANR LINE 692 AT THE SHIP SHOAL 300 PLATFORM, APPROXIMATELY 10 FT. OFF OF THE NATURAL BOTTOM. THE 8-IN PIPELINE APPEARS TO HAVE BEEN DAMAGED BY AN EXTERNAL FORCE CAUSING APPROXIMATELY 250 LINEAR FEET OF THE PIPELINE TO BE DRAGGED OUT OF ITS ORIGINAL POSITION. REPAIRS HAVE BEEN COMPLETED.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090091 | 2009-08-28 16:41 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 800 | 2009-08-09 | 2009 |  |  | LA | [5 empty] | OFFSHORE |  | EUGENE ISLAND | 307B |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170000 | 96780.2819 | 173786.8041 | 50000 | 26466.0494 | 120000 | 147320.7547 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 914910 | 2009-08-14 | 590 | 1440 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1984 | 6.63 | 0.3 | API | 42000 |  |  | UNKNOWN | 1984 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1984 | NO | [57 empty] | A SMALL SHEEN WAS DISCOVERED EMANATING FROM THE 6-INCH ANR LINE 674, APPROXIMATELY 0.4 MILES NORTHEAST OF THE EI BLK. 307B PLATFORM. THE LEAK WAS FIRST IDENTIFIED ON AUGUST 8 OR 9, BY THE PRODUCER AND WAS CONFIRMED BY DIVERS ON AUGUST 10. THE REPAIR WAS COMPLETED ON AUGUST 11 BY INSTALLING A REPAIR CLAMP.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090092 | 2009-08-31 10:41 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | PO BOX 20008 | OWENSBORO | DAVIESS | KY | 42301 | 1000 | 2009-08-04 | 2009 | GRAND CHENIER | CAMERON | LA |  | MP 30 |  | 29.83333 | 93.0 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199250 | 112271.0037 | 217901.8737 | 38250 | 20246.5278 | 161000 | 197655.3459 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 913752 | 2009-08-04 | 725 | 1052 | NO | NO | NO | NO | YES | NO | JACK L. ADAMS | 7134798099 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 20 | 0.28 | API5L | 60000 | ERW |  | AMERICAN STEEL |  | UNDER GROUND |  | 48 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1981 | NO | [57 empty] | LEAK INDICATION IS LOCATED IN MARSH WATER. PIPELINE WAS ISOLATED AND ALLOWED TO BLOWDOWN TO ZERO. SCHEDULING REPAIR ACTIVITY AT THIS TIME. UPDATE: PLIDCO SPLIT SLEEVE INSTALLED AND PIPELINE RETURNED TO SERVICE 12/07/2009
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090093 | 2009-08-31 13:33 | SUPPLEMENTAL FINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 1345 | 2009-08-14 | 2009 |  | GOM, BLOCK NPI 933 |  |  |  |  | 26^58'30 | 96^55'19 | OFFSHORE |  | PADRE ISLAND | NPI933 | TX | NO | NO | INTRASTATE | OTHER | PIPE PLUG | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200502 | 110809.1477 | 245800.3103 | 502 | 265.7191 | 200000 | 245534.5912 | 0 | 0 | NO | NO | NO | NO | 0 |  | 23 | 45 | 914934 | 2009-08-14 | 600 | 1440 | YES | NO | NO | NO | NO | NO | EDGAR RODRIGUEZ | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | GATHERING | OTHER | VALVE | STEEL |  | NO | NO | NO | OTHER | VALVE | 1981 | 8 |  |  |  |  | BALL | GROVE | 1981 | UNDER WATER |  | 36 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | PLUG THREADS DAMAGED | [8 empty] | THE CAUSE OF THE LEAK ON THE VALVE WAS CAUSED BY AN IMPROPERLY INSTALLED 1/2" PLUG DURING FABRICATION.THE PLUG WAS REMOVED AND A NEW PLUG WAS INSTALLED PROPERLY.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090094 | 2009-08-31 | SUPPLEMENTAL | 31994 |  | PANTHER PIPELINE, LTD. | 14405 WALTERS RD., SUITE 960 | HOUSTON | HARRIS | TX | 77014 | 1030 | 2009-07-14 | 2009 |  | MATAGORDA | TX |  |  |  | N 28 .30.41 | W 95 58.09 | OFFSHORE |  | BRAZOS | 446 L | TX | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 35913.522 | 79798.7421 | 0 | 0 | 65000 | 79798.7421 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 0 | 911533 | 2009-07-14 | 350 | 960 | NO | YES | NO | NO | NO | NO | JEFF SHIPPER VP- MANAGER | 8325523600 | JSHIPPER@PANTHERCOMPANIES.COM | GATHERING | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 12 | 0.31 | APISL | 52 | ERW |  | N/A | 1958 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1958 | NO | [57 empty] | ON JULY 14, 2009, AT APPROX. 10:30 AM, PANTHER BECAME AWARE OF A POTENTIAL NATURAL GAS LEAK ON ITS OFFSHORE MATAGORDA GATHERING SYSTEM IN BRAZOS BLOCK 446-L. ALL GAS SUPPLY WAS SHUT OFF INTO THE SEGMENT OF PIPELINE THAT SAME DAY. THE FOLLOWING DAY A CHOPPER LANDED NEARBY TO GATHER EXACT COORDINATES TO COORDINATE REPAIRS. NO SHEEN WAS REPORTED. UPON INVESTIGATION, A PINHOLE LEAK PROBLEM WAS DISCOVERED ON THE PANTHER PIPELINE. PANTHER REPAIRED THE LEAK WITH A CLAMP ON 7/19/09 AND SERVICE WAS REINSTATED TO THE OFFSHORE LATERAL THE FOLLOWING DAY.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090095 | 2009-09-01 16:40 | ORIGINAL FINAL | 22175 |  | TARGA MIDSTREAM SERVICES, L.P. | 1565 TIDEWATER ROAD | VENICE | PLAQUEMINES | LA | 70091 | 1410 | 2009-07-12 | 2009 | [6 empty] | 29.11.33 | 89.27.20 | OFFSHORE |  |  |  | LA | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 152.3412 | 332.7216 | 7 | 3.7052 | 268 | 329.0164 | 0 | 0 | NO | NO | NO | NO | 0 |  | 38 |  | 911545 | 2009-07-12 | 780 | 1182 | NO | NO | NO | YES | NO | NO | EVERETT H. HANNA | 5045344031 | HHANNA@TARGARESOURCES.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 22 | 0.63 | 52000 |  | SEAMLESS API 5LX |  | UNKNOWN |  | UNDER WATER |  | 168 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1970 | NO
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090096 | 2009-09-04 09:02 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1940 | 2009-09-04 | 2009 | SHERMAN | GRAYSON | TX |  | 173 |  | N 33 41.201 | W 96 26.037 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | N/A | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 121913.5802 | 105864.1975 | 200000 | 105864.1975 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 16 | 30 |  |  | 946 | 1200 | NO | YES | NO | NO | NO | NO | MATTHEW STRATMANN | 7133818209 | MSTRATMANN@EPCO.COM | TRANSMISSION | OTHER | VALVE ATTACHMENT | STEEL |  | NO | NO | NO | PIPELINE |  | 2007 | 36 | 0.38 | API-5L | 1354 |  |  |  |  | ABOVE GROUND |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | OTHER | BODY BLEED TYPE STREET ELLE | [8 empty] | A CONCRETE SUPPORT STUCTURE WAS BUILT FOR THE VALVE. THE SUPPORT STRUCTURE WAS INSTALLED TO CLOSE TO THE STREET ELLE BODY BLEED ON THE VALVE. THE PIPE HARMONICS CAUSED THE BLEED VALVE TO RUB AGAINST THE SUPPORT STRUCTURE AND EVENTUALLY CAUSED A LEAK AT THE RUB SPOT.
2022-01-31 10:32 | NO | NO | GG (Gas Gathering) | 20090097 | 2009-09-08 10:02 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 2200 | 2009-08-04 | 2009 | [6 empty] | 28.4115 | 93.7393 | OFFSHORE |  | HIGH ISLAND | 264B |  | YES | NO | INTERSTATE | OTHER | PLATFORM EXPLOSION AND FIRE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7061 | 4304.159 | 3737.5355 | 7061 | 3737.5355 | 0 | 0 | 0 | 0 | NO | NO | YES | YES | 39 | COMPANY POLICY | 38 | 50 | 913841 | 2009-08-04 | 0 |  | NO | NO | NO | NO | NO | NO | JOEL E. KOHLER | 7133814830 | JKOHLER@EPROD.COM | GATHERING | OTHER | PLATFORM | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1978 | [8 empty] | INSIDE/UNDER BUILDING |  |  | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | INCORRECT OPERATION | [57 empty] | FAILURE TO FOLLOW PROCEDURES |  | 0 | 0 | Y | 14 |  |  | AN EXPLOSION AND FIRE OCCURRED ON HIGH ISLAND BLOCK 264 PLATFORM B (HI 264B) IN AND AROUND THE COMPRESSOR BUILDING. ACCORDING TO THE RECENTLY RECEIVED BAKERRISK REPORT, THE CAUSE OF THE INCIDENT IS AS FOLLOWS: A) THE MOST PROBABLE SCENARIO SUGGESTS THE INITIAL FIRE RESULTED FROM A GAS RELEASE WHILE ATTEMPTING TO START THE NO. 2 TURBINE/COMPRESSOR SET. B) THE NO. 2 COMPRESSOR OUTBOARD CASE DRAIN WAS LEFT OPEN DURING STARTUP AND EVENTUAL LOADING OF THE COMPRESSOR. REPLACEMENT COST FOR THE COMPRESSOR PLATFORM AND EQUIPMENT IS ESTIMATED TO BE IN THE RANGE OF $35 - $70 MILLION, HOWEVER ENTERPRISE HAS ELECTED TO NOT REPAIR OR REPLACE AT THIS TIME.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090098 | 2009-09-08 17:44 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 730 | 2009-08-05 | 2009 | [6 empty] | 28.28.65 | 93.59.9 | OFFSHORE |  | HIGH ISLAND | 468 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364565 | 201517.1813 | 446473.6704 | 1565 | 828.3873 | 363000 | 445645.283 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 | 0 | 913867 | 2009-08-05 | 828 | 1440 | NO | YES | NO | NO | NO | NO | NATHAN L. GRAY JR. | 9858041376 | NGRAY@EPROD.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1980 | 12.75 | 0.44 | API 5 LX | 35000 |  |  |  |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | GENERAL CORROSION |  | GALVANIC |  | YES | 1980 | NO | [57 empty] | DURING NORMAL OPERATIONS MOVING FROM PLATFORM TO PLATFORM A SHEEN AND GAS BUBBLES WERE NOTED FROM THE AIR. AFTER FURTHER INVESTIGATION OF COORDINATES AND MAPS A DECISION WAS MADE TO SHUT IN PIPELINE AT DEPARTING PLATFORM AND MONITOR PRESSURES. A DIVE VESSEL AND DIVERS WERE SECURED AND SENT TO SIGHT TO INVESTIGATE. UPON INVESTIGATION A PIN HOLE LEAK WAS FOUND. A CLAMP WAS INSTALLED AND PIPELINE WAS RETURNED TO SERVICE. ATTEMPTS HAVE BEEN MADE FOR THE PAST 2 WEEKS TO ACCESS THE PHMSA ON LINE DATA ENTRY SITE WITH FAILURE AND ERRORS OCCURRING. THIS IS THE FIRST OPPORTUNITY THAT THE SITE HAS BEEN ACCESSED WHICH IS THE REASON FOR THE LATE FILING
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090100 | 2009-09-12 13:19 | SUPPLEMENTAL FINAL | 31451 |  | KINDER MORGAN TEXAS PIPELINE CO | 500 DALLAS ST | HOUSTON | HARRIS | TX | 77002 | 1100 | 2009-09-12 | 2009 | RAY POINT | LIVE OAK | TX | 78071 | 120.61 | 6368+32 | 28 31 42.70 | -98 01 35.60 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | CRACK 1.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107028 | 64004.1133 | 71790.3423 | 85351 | 45178.0756 | 21677 | 26612.2667 | 0 | 0 | NO | NO | NO | NO | 0 |  | 3 |  | 20090100 | 2009-09-12 | 812 | 1200 | NO | NO | NO | NO | NO | NO | LARRY KEPPLER | 8325964128 | LARRY_KEPPLER@KINDERMORGAN.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 2 | 0.22 | X42 | 42000 |  |  |  |  | UNDER GROUND |  | 60 | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | A LEAK WAS FOUND ON A 2" SIDETAP ON INDEX 50 @ RECHAIN STATION 6368+32. THE APPARENT CAUSE WAS THAT THE MAINLINE OVER TIME SETTLED WHILE THE BRACE FOR THE 2" VALVE WAS HELD IN POSITION BY A BRACE. THIS EXERTED FORCE ON THE NIPPLE BETWEEN THE VALVE AND THE MAINLINE RESULTING IN A CRACK NEAR THE WELD ON THE 2" NIPPLE
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090101 | 2009-09-14 16:02 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 900 | 2009-08-19 | 2009 |  |  | LA |  |  |  | 28* 19' 24 | 91* 35' 33 | OFFSHORE |  | EUGENE ISLAND | 307A | LA | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 223858.8982 | 456151.584 | 50000 | 26466.0494 | 350000 | 429685.5346 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 |  | 915377 | 2009-08-19 | 950 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 16 | 0.38 | API 5L | 52000 |  |  | KS | 1978 | UNDER WATER |  | 24 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1978 | YES | 6 | 0 | [55 empty] | A LEAK WAS SUSPECTED AFTER BUBBLES WERE SPOTTED IN THE EI 307A AREA. THE PRODUCER (DYNAMIC) SHUT IN AND THE BUBBLES STOPPED. THE LEAK WAS IN THE AREA OF THE ANR 16-IN LINE 607 LINE, FROM EI BLK. 307A TO EI BLK. 305. A DIVING BOAT WAS MOBILIZED TO INSPECT THE AREA AND ASSESS THE PIPELINE CONDITION FOR A REPAIR METHOD. THE LEAK WAS REPAIRED ON AUGUST 25 WITH THE INSTALLATION OF A FULL-ENCIRCLEMENT REPAIR SLEEVE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090102 | 2009-09-16 13:21 | SUPPLEMENTAL FINAL | 13845 |  | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | SALT LAKE | UT | 84108 | 1421 | 2009-09-02 | 2009 | SODA SPRINGS | CARIBOU | ID | 83276 | 538.52 |  | N42.49.37 | W111.33.50 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132430 | 76778.721 | 118403.6824 | 63259 | 33484.3164 | 68171 | 83691.6931 | 1000 | 1227.673 | NO | NO | NO | NO | 0 |  | 1 | 40 | 916743 | 2009-09-02 | 805 | 850 | NO | YES | NO | NO | NO | NO | LAURI DUNCOMBE | 8015846509 | LAURI.M.DUNCOMBE@WILLIAMS.COM | TRANSMISSION | PIPE SEAM |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1956 | 22 | 0.25 | API 5L | 52000 | DSAW | NA | CONSOLIDATED WEST | 1955 | UNDER GROUND |  | 30 | MATERIAL AND/OR WELD FAILURES | PIPE SEAM WELD | MATERIAL/WELD/EQUIP FAILURE | PIPE SEAM | [40 empty] | DSAW |  | MATERIAL DEFECT |  | NO | YES | 5 | 26 | 1956 | WATER |  | 7 | 994 | [12 empty] | FINDINGS AND CONCLUSIONS FROM STORK MATERIALS TECHNOLOGY REPORT DATED FEBRUARY 19, 2010; 1.THE LEAK OCCURRED AT A SHORT CRACK IN THE LONGITUDINAL DOUBLE SUBMERGED ARC WELD (DSAW). METALLOGRAPHIC EXAMINATION OF THE CRACK SHOWED THAT IT WAS INTERGRANULAR AND APPEARED TO CONTAIN COPPER. 2. ENERGY-DISPERSIVE X-RAY SPECTROSCOPY (EDS) ANALYSIS SHOWED A SIGNIFICANT PRESENCE OF COPPER IN THE INTERGRANULAR CRACKS. 3. THE LEAK IN THE PIPE WAS CAUSED BY COPPER CONTAMINATION ORIGINATING IN THE INTERNAL WELD PASS OF THE DSAW PIPE. THE CRACKING PRODUCED A SMALL DEFECT THAT APPARENTLY EITHER DID NOT PENETRATE TO THE OUTSIDE SURFACE ON THE WELD OR WAS NOT DETECTED FOR MANY YEARS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090104 | 2009-09-22 16:23 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 1400 | 2009-08-30 | 2009 | WILLCOX | COCHISE | AZ | 85643 | 412+4461 | LINE NO. 1100 | 32.08853 | -109.75644 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | IMPACT DAMAGE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504105 | 283866.3078 | 553506.8395 | 93605 | 49547.091 | 410500 | 503959.7484 | 0 | 0 | NO | NO | NO | NO | 0 |  | 4 | 0 | 916432 | 2009-08-30 | 630 | 837 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1947 | 1 | 0.13 | [6 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | DRIVER OF A PICKUP TRUCK ON KANSAS SETTLEMENT ROAD LOST CONTROL OF HIS VEHICLE AND CRASHED THROUGH THE FENCING INTO EL PASO'S COCHISE #2 METER STATION. THE IMPACT RESULTED IN THE TAP PIPING BEING SEVERED WITH A GAS RELEASE. HOWEVER, THERE WAS NO IGNITION AND NO SIGNIFICANT INJURIES. EL PASO VENTED THE GAS PRESSURE TO ATMOSPHERIC PRESSURE WITH PLANS TO REBUILD THE STATION. THE STATION WAS TEMPORARILY PLACED BACK INTO SERVICE BY 11 PM MOUNTAIN STANDARD TIME THE DAY OF THE INCIDENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090105 | 2009-09-23 | SUPPLEMENTAL FINAL | 32380 |  | STECKMAN RIDGE, LP | 5400 WESTHEIMER COURT | HOUSTON | HARRIS | TX | 77056 | 1400 | 2009-08-23 | 2009 | CLEARVILLE | BEDFORD | PA | 15535 | MP 0.00 | 0+00 | 39.1969 | -78.3331 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | CRACK IN 1-INCH DIAMETER NIPPLE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102000 | 56413.656 | 124524.2895 | 1000 | 529.321 | 1000 | 1227.673 | 100000 | 122767.2956 | NO | NO | NO | NO | 0 |  |  |  | 916122 | 2009-08-27 | 2161 | 2650 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF | 7136275573 | DETESCHENDORF@SPECTRAENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 2009 | 1 |  | A106 SCHEDULE 80 | 35000 | SEAMLESS | NA | PHOENIX-CAPITOL-CAMCO | 2009 | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | THREADS STRIPPED, BROKEN PIPE COUPLING | MATERIAL/WELD/EQUIP FAILURE | THREADS STRIPPED, BROKEN PIPE COUPLING | [55 empty] | NIPPLES | [9 empty] | A THREADED 1-INCH DIAMETER NIPPLE LOCATED IN THE GAS COMPRESSOR PIPING BETWEEN THE FIRST AND SECOND STAGE COMPRESSOR CYLINDERS EXPERIENCED A CRACK IN THE PIPE THREADS ON AUGUST 23, 2009 RESULTING IN A NATURAL GAS LEAK WHICH TRIGGERED AN EMERGENCY SHUTDOWN OF THE STECKMAN RIDGE COMPRESSOR STATION PIPING. COMPRESSOR LUBRICATION OIL WAS DISPERSED ALONG WITH NATURAL GAS DURING THE SHUT DOWN. DAMAGES TO THE PIPELINE FACILITIES WERE MINIMAL, HOWEVER, THE COST TO CLEAN UP NEIGHBORING PROPERTY EXCEEDED $50,000 WHICH CAUSED THIS EVENT TO BE DEFINED AS A DOT REPORTABLE INCIDENT.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090106 | 2009-10-02 13:02 | SUPPLEMENTAL FINAL | 31618 |  | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 1015 | 2009-09-04 | 2009 |  | MATAGORDA | TX |  |  |  | N28 14.88 | W96 19.26 | OFFSHORE |  | MATAGORDA ISLE | 564 | TX | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155000 | 85925.198 | 186797.5483 | 5000 | 2646.6049 | 150000 | 184150.9434 | 0 | 0 | NO | NO | NO | NO | 0 |  | 36 |  | 916908 | 2009-09-04 | 800 | 1250 | NO | YES | NO | NO | NO | NO | MATTHEW STRATMANN | 7133818209 | MSTRATMANN@EPCO.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 12.75 | 0.38 | 42000 | [5 empty] | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | OTHER | STILL BEING DETERMINED | YES | 1989 | NO | [57 empty] | THE LEAK OCCURRED ON AN LATERAL THAT DOES NOT ACTIVELY HAVE FLOW. THE UNUSED SECTION DEVELOPED TWO PINHOLE LEAKS. A DIVE TEAM WAS DEPLOYED AND TWO CLAMPS WERE INSTALLED TO STOP THE LEAKS. IT WAS DETERMINED THAT INTERNAL CORROSION WAS THE CAUSE DUE TO STAGNATION ON THIS PORTION OF THE LINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090107 | 2009-10-04 | SUPPLEMENTAL FINAL | 13063 |  | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | ERIE | NY | 14221-5887 | 1155 | 2009-09-29 | 2009 | DERBY | ERIE | NY | 14047 | DERBY COMPRESSOR STATION | N/A | 42.68550 | 78.96580 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 39075.4659 | 81048.6431 | 7000 | 3705.2469 | 63000 | 77343.3962 | 0 | 0 | NO | NO | NO | NO | 0 |  |  | 50 | 919183 | 2009-09-29 | 680 | 750 | NO | NO | NO | NO | YES | NO | BRIAN A. KEMPSKI | 7168272131 | KEMPSKIB@NATFUEL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1950 | 4 | 0.24 | UNKNOWN | 24000 | ERW | N/A | UNKNOWN | 1950 | INSIDE/UNDER BUILDING |  | 36 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | GENERAL CORROSION |  | GALVANIC |  | YES | 1973 | NO | [57 empty] | ON SEPTEMBER 29, 2009 AT APPROXIMATELY 11:55 AM NATIONAL FUEL SUPPLY CORPORATION ("NFGSC") PERSONNEL RECEIVED AN EMERGENCY WARNING NOTIFICATION FROM ITS SCADA SYSTEM THAT AN INCIDENT HAD OCCURED AT DERBY COMPRESSOR STATION LOCATED AT 7393 VERSAILLES PLANK ROAD, DERBY, NEW YORK. ON ARRIVAL, NFGSC PERSONNEL OBSERVED DAMAGE TO THE INGERSOLL-RAND MODEL #4XVG 75HP COMPRESSOR, THE COMPRESSOR STATION BUILDING, AND THE FOUR-INCH BURIED DISCHARGE PIPING. THERE WAS NO FIRE NOR WERE THERE ANY INJURIES OR FATALITIES. NFGSC PERSONNEL ISOLATED THE DAMAGED FACILITY BY CLOSING THREE VALVES. THE FACILITY WAS SHUT-IN AND MADE SAFE AT APPROXIMATELY 12:45 PM THE SAME DAY. FURTHER INVESTIGATION INTO THE INCIDENT REVEALED A RUPTURE IN THE BURIED FOUR-INCH DISCHARGE PIPING. PART G: NARRITIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE EVENT - CONTINUED: INVESTIGATION UPDATE: THE FAILED SECTION WAS DELIVERED TO BATTELLE, COLUMBUS OHIO FOR A COMPLETE METALLURGICAL AND FAILURE ANALYSIS TO DETERMINE THE ROOT CAUSE OF THE FAILURE. BATTELLE CONCLUDED: "A STRONG GRADATION IN WALL THICKNESS WAS FOUND FROM REMOTE TO THE ENDS OF THE CASING TOWARD THE MIDLENGTH OF THE CASING WHERE THE RUPTURE OCCURRED. THIS GRADATION AND THE SLIGHTLY DIFFERING CORROSION PRODUCTS FOUND WITHIN THE AREA OF THE CASING SUGGEST THAT THE SLIGHTLY MORE STAGNANT CONDITIONS AND POTENTIALLY COOLER TEMPERATURE (AND INCREASED POTENTIAL FOR CONDENSATION DUE TO ITS PROXIMITY TO THE INGROUND CONDITIONS) OPENS THIS AREA TO SOMEWHAT FASTER CORROSION. THE CAUSE OF THE FOCALIZED CORROSION THUS APPEARS TO TRACE TO THE TYPE OF FOUNDATION PENETRATION EMPLOYED.”
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090108 | 2009-10-05 14:06 | SUPPLEMENTAL FINAL | 13750 |  | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | DOUGLAS | NE | 68124-1000 | 1540 | 2009-09-30 | 2009 | NEWKIRK | SIOUX | IA | 51238 | 1.0 |  | 43.06488 | -95.98441 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | LINE WAS SEVERED BY TILING EXCAVATOR | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8965 | 5038.8817 | 9958.5601 | 1500 | 793.9815 | 7465 | 9164.5786 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 919313 | 2009-09-30 | 670 | 800 | NO | NO | NO | NO | YES | NO | BYRON WOOD | 4023987396 | BYRON.WOOD@NNGCO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 2 | 0.15 |  | 35000 |  |  |  |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | LANDOWNER |  | NO |  |  |  |  | NO | [40 empty] | ON SEPTEMBER 30, 2009, AT APPROXIMATELY 2:30 P.M. A TILING CONTRACTOR TILING IN SECTION 12 OF HOLLAND TOWNSHIP, T-95N, R44W, IN SIOUX COUNTY, IOWA STRUCK THE 2-INCH NEWKIRK BRANCH LINE (IAB48601)SEVERING THE 2-INCH GAS LINE. THERE WAS BLOWING GAS, NO FIRE, NO EXPLOSION, NO INJURIES. THE SEVERING OF THE LINE RESULTED IN THE LOSS OF GAS SERVICE TO THE COMMUNITY OF NEWKIRK, IOWA IN WHICH THERE WERE APPROXIMATELY 17 METER SETTINGS THAT WERE SERVICED BY MIDAMERICAN ENERGY COMPANY. AN INVESTIGATION AND INTERVIEW WITH THE TILER DETERMINED THAT THERE WAS NO 1-CALL REQUEST MADE BY THE TILER. THE FAILURE TO MAKE A ONE-CALL LOCATE REQUEST WAS THE ROOT CAUSE FOR THE PIPELINE BEING STUCK. THE IOWA ATTORNEY GENERALS OFFICE HAS BEEN NOTIFIED OF THE ONE CALL VIOLATION. REPAIRS WERE MADE BY INSTALLING APPROXIMATELY 12 FEET OF NEW TESTED, COATED TWO-INCH PIPE. A FOLLOW UP REPORT WILL BE SUBMITTED ONCE ALL COST HAVE BEEN DETERMINED. EVEN THOUGH THIS INCIDENT MAY NOT REACH THE $50K REPORTING THRESHOLD NORTHERN CONSIDERS THE LOSS OF SERVICE TO THE COMMUNITY OF NEWKIRK, IA AS A SIGNIFICANT EVENT. SUPPLEMENTAL/FINAL REPORT: A FINAL TOTAL COST OF REPAIRS OF $8,965, WHICH INCLUDES GAS LOSS HAS BEEN CALCULATED. AS PREVIOUSLY INDICATED THE ROOT CAUSE WAS THE FAILURE OF THE CONTRACTOR/LANDOWNER TO MAKE A ONE-CALL LINE LOCATE REQUEST PRIOR TO COMMENCING WORK ACTIVITIES. THIS INCIDENT IS CONSIDERED CLOSED WITH NO FURTHER ACTIONS PENDING.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090109 | 2009-10-05 17:01 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1700 | 2009-09-21 | 2009 |  |  | LA |  |  |  | 28*19' 24.9 | 91*35'35.7 | OFFSHORE |  | EUGENE ISLAND | 307 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 139555.2353 | 289459.4398 | 25000 | 13233.0247 | 225000 | 276226.4151 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 |  | 918428 | 2009-09-21 | 1200 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | OTHER | UNKNOWN | STEEL |  | NO | NO | NO | PIPELINE |  | 1978 | 16 | 0.38 | API | 52000 | UNKNOWN |  |  | 1978 | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1978 | NO | [57 empty] | A CALL WAS RECEIVED FROM THE OPERATOR AT EI BLOCK 307, INDICATING THAT A LEAK HAD OCCURRED ON THE 16-IN. ANR LINE 607, FROM EI 307 TO EI 305. A SHEEN WAS SPOTTED ALONG WITH A 60' BUBBLE CIRCLE. WORK BEGAN TO ISOLATE THE SEGMENT, DEPRESSURIZE AND LOCATE THE LEAK. FOLLOWING A DIVER INSPECTION, A PINHOLE LEAK ON THE PIPE BOTTOM QUADRANT WAS DISCOVERED. THE PIPELINE WAS REPAIRED ON AUGUST 30, 2009 BY INSTALLING A REPAIR CLAMP. THE LINE WAS SUBSEQUENTLY RETURNED TO SERVICE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090110 | 2009-10-06 14:20 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 1855 | 2009-09-14 | 2009 | STERLINGTON | OUACHITA | LA |  | EIS 1, MP 0.000 |  | 32.67667 | 92.02 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | UNINTENDED VALVE OPERATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11130 | 6784.4907 | 5891.3426 | 11130 | 5891.3426 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 30 | 917817 | 2009-09-14 | 530 | 624 | NO | NO | NO | NO | NO | NO | GLENN FLOYD | 9016853471 | GLENN.FLOYD@BWPMLP.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  |  | 4 | [7 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | A 4" ESD - BLOW OFF VALVE, EIS 1-36, ENCOUNTERED AN UNINTENDED ACTIVATION DUE TO A PILOT AIR VALVE FAILURE AND RELEASED GAS FOR APPROXIMATELY 30 MINUTES BEFORE BEING CLOSED. A NEW PILOT VALVE HAS BEEN INSTALLED TO CORRECT THE PROBLEM AND AVOID REOCCURRENCE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090111 | 2009-10-08 10:52 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 845 | 2009-09-10 | 2009 | COLUMBIA | MARION | MS |  | COLUMBIA 4 | 22+30 | 31.26503 | 89.84846 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PUNCTURE | 6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99409 | 54925.0355 | 122041.7409 | 0 | 0 | 47911 | 58819.039 | 51498 | 63222.7019 | NO | NO | NO | YES | 15 | PRECAUTIONARY | 5 | 0 | 917531 | 2009-09-10 | 300 | 415 | NO | NO | NO | NO | YES | NO | GLENN FLOYD | 9016853471 | GLENN.FLOYD@BWPMLP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1933 | 4 | 0.24 | X-42 | 24000 | UNKNOWN | VALVE NOT INVOLVED. | UNKNOWN |  | OPEN DITCH |  | 0 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | A SECOND PARTY WAS CUTTING ROW FOR GULF SOUTH PIPELINE COMPANY, LP. A LEAD MAN, ON A FOUR WHEELER, WAS GOING AHEAD OF THE TRACTOR WITH THE BUSH HOG, IDENTIFYING ABOVE GROUND TAPS AND OTHER AREAS TO ALERT THE TRACTOR DRIVER, TO PREVENT DAMAGE TO THE PIPELINE. THE LEAD PERSON GOT TOO FAR AHEAD OF THE TRACTOR OPERATOR AND THE TRACTOR OPERATOR TURNED AT A LATERAL LINE, WHICH CONNECTED WITH THE MAIN LINE, INSTEAD OF CONTINUING DOWN THE MAIN LINE. THE TRACTOR DRIVER DROVE THROUGH A DITCH WHERE THE PIPE WAS MARKED EXPOSED (MARKED AT BOTH ENDS OF THE EXPOSURE). THE PIPE WAS DAMAGED WHEN THE BUSH HOG CAME IN CONTACT WITH THE PIPE, CAUSING TWO PUNCTURES MEASURING 4" X 1" AND 6" X 1.5". THE TRACTOR OPERATOR WAS SUPPOSE TO PROCEED MOWING THE MAIN LINE, RATHER THAN THE LATERAL LINE. THIS INCIDENT INVOLVED TWO NRC REPORTS. 917531 MADE ON 09-10-2009 AND 917420 MADE ON 09-10-2009.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090112 | 2009-10-16 12:58 | SUPPLEMENTAL FINAL | 117 |  | AIR PRODUCTS & CHEMICALS INC | 14700 INTRACOASTAL DRIVE | NEW ORLEANS | ORLEANS | LA | 70129 | 1643 | 2009-09-20 | 2009 | NEW ORLEANS | ORLEANS | LA | 70129 |  |  | 30 00 09 | 89 54 24 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | STRESS CRACK - 2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 652000 | 360354.3559 | 799046.0634 | 2000 | 1058.642 | 650000 | 797987.4214 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 7 | 918317 | 2009-09-20 | 280 | 350 | NO | YES | NO | NO | NO | NO | JODY R. ARNER - PIPELINE MAINTENANCE ENGINEER | 6104811707 | ARNERJR@AIRPRODUCTS.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1995 | 8.63 | 0.25 | API5L | 42000 | ERW |  | LTV STEEL | 1994 | UNDER WATER |  | 144 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | THE SUBJECT AIR PRODUCTS 8” REFINERY OFF GAS (ROG) PIPELINE (IMP LINE#525) REPAIR WAS COMPELETED ON 4 DEC, 2009 WITH PRODUCT BEING INTRODUCED INTO THE PIPELINE IN THE AM ON 11 DEC, 2009. IT IS AIR PRODUCTS OPINION, THAT THE DAMAGE CAUSED TO THE SUBJECT 8" ROG PIPELINE, WAS FORM A "SPUD ANCHOR" EQUIPPED BARRAGE AND FAILURE OF THE BARRAGE OPERATOR TO HEED THE "NO ACHORAGE / DREDGING" WARNING SIGNS POSTED AT THE INCIDENT LOCATION. KJS 15 JAN. 2010 UPDATED BY PHMSA ON 12/3/2015 PER OPERATOR'S MARK UP (PART C, QUESTION 5 - YEAR THE PIPE OR COMPONENT WHICH FAILED WAS INSTALLED).
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090113 | 2009-10-30 | ORIGINAL FINAL | 31130 |  | DCP MIDSTREAM | 370 17TH STREET, SUITE 2500 | DENVER | DENVER | CO | 80202 | 1715 | 2009-10-01 | 2009 | OFFSHORE GULF OF MEXICO |  | AL |  | MP 17.65 | 931+92 | 29.4032 | -88.0417 | OFFSHORE |  | MAIN PASS | 225 |  | YES | NO | INTERSTATE | OTHER | 2-INCH DIAMETER BY PASS SEPARATED FROM MAINLINE BY | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1440000 | 809315.1642 | 1600244.5842 | 240000 | 127037.037 | 1200000 | 1473207.5472 | 0 | 0 | NO | NO | NO | NO | 0 |  | 63 |  | 919461 | 2009-10-01 | 937 | 1760 | NO | NO | YES | NO | NO | NO | DWAYNE TESCHENDORF PRINCIPAL ENGINEER | 7136275573 | DETESCHENDORF@SPECTRAENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1998 | 2 | 0.22 | A106 | 35000 | SMLS |  |  |  | UNDER WATER |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | 2-INCH BY-PASS PIPE SEPARATED FROM 16-INCH MAINLINE WHEN BUOY WAS RETRIEVED WITH BOAT WINCH BECAUSE BUOY CABLE WAS TANGLED IN PIPE |  | A RUN-A-WAY BUOY WAS BEING RETRIEVED BY ITS OWNER IN THE GULF OF MEXICO IN MAIN PASS BLOCK 225. THE 1-INCH CABLE ATTACHED TO THE BUOY WAS ENTANGLED ON THE 2-INCH BY PASS FOR 16-INCH LINE 71-C. WHEN THE BUOY WAS WINCHED ONTO THE BUOY OWNER'S BOAT THE 2-INCH BY PASS WAS SEPARATED FROM THE MAINLINE AND NATURAL GAS WAS RELEASED.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090114 | 2009-11-03 10:42 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 530 | 2009-10-23 | 2009 | GLENVILLE | MCLEAN | KY | 42376 | 488.61 |  | 37.584722 | 87.185556 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 30478.3951 | 26466.0494 | 50000 | 26466.0494 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 35 | 921406 | 2009-10-23 | 810 | 810 | YES | NO | NO | NO | NO | NO | GLENN FLOYD | 9016853471 | GLENN.FLOYD@BWPMLP.COM | TRANSMISSION | OTHER | NO FAILURE | STEEL |  | NO | NO | NO | PIPELINE |  |  | 26 |  |  |  |  | BALL | BECKER |  | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | PRESSURE REGULATOR | [11 empty] | MLS #1-26". BLOCK VALVE LOCATION ON MLS (MP 488.61) RELIEF VALVE VENTED PREMATURELY (MLS 48-14) AT 810 PSIS. VENT SETTING IS AT 820PSIS. APPROXIMATELY 22,209 MCF VENTED. UPSTREAM CONTROL POINT (SLAUGHTERS COMPRESSOR STATION) WAS LOWERED VIA PRESSURE SET POINT AND HORSEPOWER REDUCTION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090115 | 2009-11-04 | ORIGINAL FINAL | 12408 |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | WAYNE | MI | 48806 | 830 | 2009-10-07 | 2009 | ASHLEY | GRATIOT | MI | 48806 | 53.02 / MAIN LINE VALVE/ | 2799+46 | 43.15757 | -84.56181 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | OTHER | LEAK THROUGH VALVE BODY SEAL | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50500 | 29071.6137 | 47681.2689 | 20500 | 10851.0802 | 29800 | 36584.6541 | 200 | 245.5346 | NO | NO | NO | NO | 0 |  |  |  | 920419 | 2009-10-13 | 675 | 970 | NO | YES | NO | NO | NO | NO | JOHN D LUEDERS PE SUPERVISOR CODES & STANDARDS | 6166322646 | LUEDERS@DTEENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | VALVE | 1951 | [5 empty] | GATE | WKM | 1951 | UNDER GROUND |  | 68 | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | AT APPROXIMATELY 08:30 ON OCTOBER 7, 2009 A MICHCON FIELD TECHNICIAN CONDUCTING A ROUTINE ANNUAL INSPECTION DISCOVERED BUBBLES PERCOLATING IN A WATER PUDDLE NEAR AN ABOVE-GRADE OPERATING EXTENSION FOR VALVE BD AT MAIN LINE VALVE 5 ON MICHCON'S 24" AUSTIN-DETROIT "B" PIPELINE. FURTHER INVESTIGATION ON OCTOBER 7, 2009 REVEALED THAT THAT LEAK WAS ESSENTIALLY ELIMINATED BY CLOSING THE VALVE AND VENTING THE VALVE BODY CAVITY. AFTER FORMULATING A RESPONSE PLAN, MICHCON REDUCED THE OPERATING PRESSURE OF THE 24" PIPELINE FROM APPROXIMATELY 675 PSIG TO 180 PSIG BY BLOCKING IN THE PIPELINE SEGMENT FROM THE EAST AND UTILIZING SUCTION FROM A COMPRESSOR STATION SEVERAL MILES TO THE WEST. THE PRESSURE WAS STABILIZED AT 16:00 ON OCTOBER 9, 2009. MICHCON MADE AN EXCAVATION AT THE VALVE SITE, INTENDING TO REPAIR WHAT WAS BELIEVED TO BE A LEAKING VALVE BODY BLEED FITTING. ONCE THE BURIED VALVE WAS EXPOSED, NATURAL GAS WAS FOUND TO BE LEAKING NOT FROM A BODY BLEED BUT FROM THE UPPER BONNET AND BEARING HOUSING, INDICATING A POSSIBLE BODY SEAL FAILURE. MICHCON TECHNICIANS ATTEMPTED TO STOP THE LEAK BY TIGHTENING THE SEAL PACKING, BUT THIS EFFORT WAS INEFFECTIVE. AT 08:45 ON OCOTBER 13, 2009 MICHCON MADE THE DECISION TO HALT EFFORTS TO REPAIR THE VALVE AND PROCEEDED TO PLAN FOR A SHUT-DOWN OF THE PIPELINE SEGMENT TO FACILITATE COMPLETE REPLACEMENT OF THE VALVE. NATURAL GAS WAS BLOWN TO THE ATMOSPHERE COMMENCING AT 14:30 ON OCTOBER 13, 2009 UNTIL THE 13.9 MILES OF 24" PIPELINE BETWEEN MAIN VALVE 5 AND MAIN LINE VALVE 6 WAS AT NOMINAL ATMOSPHERIC PRESSURE. ON OCTOBER 15, 2009 MICHCON REPLACED THE LEAKING 12" GATE VALVE WITH A NEW BALL VALVE. THE 24" PIPELINE SEGMENT WAS RETURNED TO SERVICE AT LINE PRESSURE AT 13:00 ON OCTOBER 13, 2009. THE EVENT WAS REPORTED TELEPHONICALLY TO THE NATIONAL RESPONSE CENTER AND TO THE MICHIGAN PUBLIC SERVICE COMMISSION SOLELY ON THE BASIS OF THE COST OF REPAIR, NOT ON ACCOUNT OF ANY INJURY, FATALITY, OR PUBLIC ATTENTION.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090116 | 2009-11-05 13:48 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 2330 | 2009-10-22 | 2009 | SALINAS | MONTEREY | CA | 93901 | 6.79 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PUNCTURE | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85000 | 46963.8365 | 104352.2013 | 0 | 0 | 85000 | 104352.2013 | 0 | 0 | NO | NO | NO | NO | 0 |  | 7 | 0 | 921487 |  | 406 | 408 | YES | NO | NO | NO | NO | NO | LAURENCE DENISTON | 9259744313 | LCD1@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 12 | [7 empty] | UNDER GROUND |  | 6 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GENERAL PUBLIC | OTHER | FARMING | NO |  |  |  |  | YES |  | YES | ACCURATE | YES | [36 empty] | ON 10/22/09 AT APPROXIMATELY 2330 HOURS A FARMER RIPPING A FIELD STRUCK AND PUNCTURED LINE 301B, A 12-INCH STEEL GAS TRANSMISSION PIPELINE CAUSING GAS TO BE RELEASED. THE INCIDENT RESULTED IN THE LOSS OF SERVICE FOR 2 CUSTOMERS. SALINAS FIRE DEPARTMENT WAS ON SCENE. PG&E CREWS WERE ON SCENE AT 0050 HOURS ON 10/23/09, GAS FLOW WAS STOPPED AT 0945 HOURS AND HAD SERVICE RESTORED BY 0010 HOURS ON 10/24/09. NO MEDIA WAS PRESENT. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT BECAME REPORTABLE WHEN DAMAGE ESTIMATES TO THE PIPELINE WERE REVISED AT 1900 HOURS ON 10/23/09 TO EXCEED $50,000.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20090117 | 2009-11-09 14:00 | SUPPLEMENTAL FINAL | 13120 |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 500 DALLAS STREET, SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1315 | 2009-10-28 | 2009 | SAINT ELMO | FAYETTE | IL | 62458 |  |  | 39.102070 | -88.861411 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | TANK FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 663800 | 366759.9371 | 814929.3082 | 0 | 0 | 663800 | 814929.3082 | 0 | 0 | NO | NO | YES | NO | 0 |  | 3 | 15 | 921917 | 2009-10-28 | 0 | 0.5 | NO | NO | NO | NO | NO | NO | BRUCE HANCOCK | 3039147959 | BRUCE_HANCOCK@KINDERMORGAN.COM | TRANSMISSION | OTHER | WASTE WATER TANK | STEEL |  | NO | NO | NO | OTHER | PROCESS FACILITY | 1999 | [8 empty] | ABOVE GROUND |  |  | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [29 empty] | MAN-MADE | [35 empty] | A FIRE STARTED IN RELATION TO A PRODUCED WATER PROCESS TANK AT A GAS STORAGE FIELD LOCATION. THE FIRE ORIGINATED IN CONJUNCTION WITH A WELDING OPERATION ON THE EXTERIOR OF THE TANK. INCIDENT INVESTIGATION COMPLETE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090118 | 2009-11-11 08:43 | SUPPLEMENTAL FINAL | 32163 |  | ROCKIES EXPRESS PIPELINE LLC (KM) | 500 DALLAS ST.; SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1745 | 2009-11-10 | 2009 | BLOOMINGBURG | FAYETTE | OH | 43106 | MP488.9/MLV27 | 25776+41 | 39.605278 | -83.446667 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133645 | 80552.8673 | 81914.7349 | 117645 | 62271.9676 | 16000 | 19642.7673 | 0 | 0 | NO | NO | NO | YES | 8 | THREAT TO THE PUBLIC | 0 | 10 | 923145 | 2009-11-10 | 512 | 1332 | NO | YES | NO | NO | NO | NO | LARRY KEPPLER | 8325964128 | LARRY_KEPPLER@KINDERMORGAN.COM | TRANSMISSION | OTHER | SOCKET WELD | STEEL |  | NO | NO | NO | OTHER | BLOCK VALVE BYPASS ASSEMBLY | 2009 | 1 | 0.02 | SCHED 80 A105 | 35000 |  |  |  |  | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | [38 empty] | FITTING |  |  |  | MATERIAL DEFECT |  | NO | YES | 9 | 13 | 2009 | WATER |  | 8 | 2035 | [12 empty] | A SOCKET WELD JOINING A NPS 1 SOCKET WELD TEE AND A NPS 2 X 1 SWAGED NIPPLE IN THE POWER GAS ASSEMBLY FOR MAINLINE VALVE 27 FRACTURED DURING LINE PACKING OF THE ROCKIES EXPRESS EAST PIPELINE IN FAYETTE COUNTY, OHIO. THE NPS 1 SOCKET WELD FRACTURED IN THE FILLET WELD DUE TO FATIGUE INITIATING AT THE FILLET WELD ROOT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090119 | 2009-11-11 10:16 | SUPPLEMENTAL FINAL | 19160 |  | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA | HOUSTON | HARRIS | TX | 77002 | 850 | 2009-10-16 | 2009 | GOLDEN MEADOW | LAFOURCHE | LA | 70357 | 4 + 217 | LINE 524C-100 | 29 13 07 | -90 13 07 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881000 | 488534.9697 | 1059930.9632 | 31000 | 16408.9506 | 850000 | 1043522.0126 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 15 | 920776 | 2009-10-16 | 790 | 1138 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1961 | 16 | 0.38 |  | 42000 | UNKNOWN |  | NATIONAL TUBE | 1961 | UNDER WATER |  | 48 | OTHER OUTSIDE FORCE DAMAGE | CAR, TRUCK OR OTHER VEHICLE NOT RELATED TO EXCAVATION ACTIVITY | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [65 empty] | TENNESSEE GAS PIPELINE'S 16" 524C-100 PIPELINE WAS STRUCK BY A DIVE SUPPORT VESSEL IN BAYOU LAFOURCHE, LOUISIANA WHEN THE VESSEL NAVIGATED OUT OF THE CHANNEL AND INTO A WATER DEPTH THAT DID NOT SUPPORT THE VESSEL'S DRAFT. THE VESSEL DUG INTO THE PIPE CAUSING IT TO TEAR OPEN RELEASING NATURAL GAS. THERE WAS NO IGNITION AND THE PIPELINE WAS BLOWN DOWN AND SECURED. REPAIRS BEGAN 3/29/2010 FOR COMPLETION WITHIN 30 DAYS WITH A REPLACEMENT SPOOL AND SMART FLANGES.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090120 | 2009-11-12 09:25 | ORIGINAL | 19570 |  | WILLIAMS GAS PIPELINE - TRANSCO | 2800 POST OAK BLVD | HOUSTON | HARRIS | TX | 77056 | 2100 | 2009-10-16 | 2009 | PLAINS | LUZERNE | PA | 1780 | 77.82 | 2542+91 |  |  | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO | NO | NO | NO | 0 |  | 11 | 30 | 920860 | 2009-10-16 | 960 | 2400 | YES | NO | NO | NO | NO | NO | EDGAR | 7132152846 | EDGAR.X.RODRIGUEZ@WILLIAMS.COM | TRANSMISSION |  |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1958 | 23.38 | 0.38 | API-5L | 52000 | LONG SEAM |  | BETHLEHEM STEEL CORP | 1958 | OTHER | ROAD CASING | 79 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | OTHER | .. | OTHER | .. | YES | 1958 | NO | [57 empty] | SECTION OF PIPE WAS REMOVED AND TRANSPORTED TO EFFORT CONSTRUCTION YARD, SAND BLASTED AND INSPECTED WITH NO FINDINGS. ENTIRE SECTION OF PIPE WAS REASSEMBLED AND WILL BE HYDRO TESTED 11/11/09
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090121 | 2009-11-16 09:05 | SUPPLEMENTAL FINAL | 32163 |  | ROCKIES EXPRESS PIPELINE LLC (KM) | 500 DALLAS ST.; SUITE 1000 | HOUSTON | HARRIS | TX | 77002 | 1020 | 2009-11-14 | 2009 | PHILO | MUSKINGUM | OH | 43771 | 575.3 | 30336+72 | 39.8397879 | -81.9349548 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447052 | 271223.2209 | 252367.1777 | 424523 | 224708.9336 | 22529 | 27658.244 | 0 | 0 | NO | NO | NO | YES | 50 |  | 2 | 30 | 923529 | 2009-11-14 | 1197 | 1480 | NO | YES | NO | NO | NO | NO | LARRY KEPPLER | 8325964128 | LARRY_KEPPLER@KINDERMORGAN.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 2009 | 42 | 0.56 | API 5L-X-70 PSL2 | 70000 | HELICAL |  | WELSPUN GUJARAT STAHL ROHREN LTD. | 2007 | UNDER GROUND |  | 68 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | FABRICATION | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 10 | 2 | 2009 | WATER |  | 8 | 2035 | [12 empty] | ROCKIES EXPRESS EAST GIRTH WELD IFTT292 FRACTURED BETWEEN NPS 42 X 0.555" WT API 5L GRADE X70 LINEPIPE AND THE SEGMENTED END OF AN INDUCTION BEND PRIMARILY AS THE RESULT OF LONGITUDINAL STRESSES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090122 | 2009-11-16 16:59 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1300 | 2009-11-04 | 2009 |  |  | LA |  |  |  | 28* 58' 29.17 | 91* 54' 29.55 | OFFSHORE |  | SOUTH MARSH ISLAND | 9 |  | YES | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210000 | 119451.4326 | 215910.2027 | 60000 | 31759.2593 | 150000 | 184150.9434 | 0 | 0 | NO | NO | NO | NO | 0 |  |  |  | 922572 | 2009-11-04 | 861 | 1300 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1968 | 12.75 | 0.38 | API | 46000 | ERW |  | AMERICAN | 1968 | UNDER WATER |  | 36 | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1968 | NO | [57 empty] | A 10-15 FT. BUBBLE CIRCLE WITH NO SHEEN WAS OBSERVED BY APACHE CORP. FLYING OVER THE SOUTH MARSH ISLAND BLOCK 9 AREA. THE LEAK WAS CONFIRMED TO ORIGINATE FROM THE 12-INCH ANR LINE 747. EXAMINATION OF THE DAMAGED PIPE SECTION REVEALED THAT THE LEAK WAS DUE TO INTERNAL CORROSION. THE PIPELINE WAS SUBSEQUENTLY ISOLATED AND REPAIRED WITH A REPAIR CLAMP. REPAIRS WERE COMPLETED ON JANUARY 28, 2010.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090123 | 2009-11-17 12:41 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1200 | 2009-11-11 | 2009 | SAN FRANCISCO | SAN FRANCISCO | CA | 94101 | 39 |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | STRUCK BY CROSS BORING | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 27625.7862 | 61383.6478 | 0 | 0 | 50000 | 61383.6478 | 0 | 0 | NO | NO | NO | NO | 0 |  | 5 | 20 | 923326 | 2009-11-12 | 145 | 275 | YES | NO | NO | NO | NO | NO | LAURENCE DENISTON | 9259744313 | LCD1@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1951 | 20 | [7 empty] | UNDER GROUND |  | 82 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | OTHER | FIBER OPTIC CABLE INSTALLATION | YES | 10 | 23 | 2009 | ONE-CALL SYSTEM | YES | PAINT |  | ACCURATE | YES | [36 empty] | ON 11/11/09 AT APPROXIMATELY 1200 HOURS A 3RD PARTY CONTRACTOR STRUCK AND PUNCTURED LINE 101, A 20-INCH STEEL GAS TRANSMISSION PIPELINE CAUSING GAS TO BE RELEASED. THE CONTRACTOR WAS CONDUCTING HORIZONTAL BORING OPERATIONS TO INSTALL FIBER OPTIC CABLES. THE AREA WAS PROPERLY DELINEATED AND CORRECTLY MARKED AND LOCATED UNDER USA TICKET 0331801. THE CONTRACTOR DID NOT USE APPROPRIATE EXCAVATION PRACTICES WHILE BORING. THE INCIDENT RESULTED IN LOSS OF SERVICE FOR SIX CUSTOMERS. SAN FRANCISCO FIRE DEPARTMENT AND HIGHWAY PATROL WERE ON SCENE. PG&E CREWS WERE ON SCENE AT 1240 HOURS ON 11/11/09. MAJOR MEDIA WAS PRESENT. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT BECAME REPORTABLE WHEN THE DAMAGES TO THE PIPELINE EXCEEDED $50,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090124 | 2009-11-24 13:44 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 1500 | 2009-10-28 | 2009 | GOODMAN | MARINETTE | WI | 54125 | MP13.74/MLV #2 | 725+71 | 45.655203 | -88.384053 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245300 | 139525.7594 | 252263.5383 | 70000 | 37052.4691 | 175300 | 215211.0692 | 0 | 0 | NO | NO | NO | YES | 7 | THREAT TO THE PUBLIC | 3 | 30 | 921949 | 2009-10-28 | 732 | 975 | YES | NO | NO | NO | NO | NO | ROBERT J. CADORIN | 2482057669 | ROBERT_CADORIN@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 30 | 0.34 | API 5LX | 60000 | DSAW | N/A | SOCIETES VALLOUREC | 1970 | UNDER GROUND |  | 54 | NATURAL FORCES | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [65 empty] | PRELIMINARY RESULTS RECEIVED ON OCTOBER 26, 2009, FROM AN MFL TOOL RUN ON SEPTEMBER 29, 2009, ON ANR PIPELINE COMPANY’S 237 LINE INDICATED AN ANOMALY AT APPROXIMATE MP 13.74 IN VALVE SECTION 2 WITH A POSSIBLE 86% PIPE WALL LOSS. PLANNING TO EXCAVATE AND INSPECT THIS ANOMALY, FIELD PERSONNEL WERE DISPATCHED ON OCTOBER 28, 2009, TO CONDUCT A LEAK SURVEY AT THE SITE. THE SURVEY INDICATED THAT THERE WAS LEAKING GAS. AFTER SHUTTING IN THE VALVE SECTION, PIPELINE PRESSURE WAS LOWERED FROM 732 PSIG TO APPROXIMATELY 200 PSIG. THE FOLLOWING DAY, PRESSURE WAS LOWERED TO ATMOSPHERIC AND THE SITE WAS EXCAVATED. THE ANOMALY WAS INSPECTED AND WAS DETERMINED TO BE A PIN-HOLE-SIZED LEAK WITHIN AN APPROXIMATE ONE-INCH DIAMETER PIT. ON EXAMINATION, THE PIT APPEARED TO HAVE CHARACTERISTICS CONSISTENT WITH THE THOSE CAUSED AS A RESULT OF A LIGHTNING STRIKE. THE PIPE SEGMENT CONTAINING THE ANOMALY WAS REMOVED AND REPLACED. FURTHER METALURGICAL ANALYSIS CONCLUDED THAT CAUSE OF THE LEAK WAS A LIGHTNING STRIKE THAT CREATED A METAL LOSS AREA ON THE OUTSIDE SURFACE APPROXIMATELY 1-INCH IN DIAMETR WITH A THROUGH-WALL PINHOLE LEAK AT THE DEEPEST PORTION OF THE MELTED AREA.
2022-01-31 10:32 | YES | YES | GT (Gas Transmission) | 20090125 | 2009-12-02 11:10 | SUPPLEMENTAL FINAL | 4280 |  | EL PASO NATURAL GAS CO | 2 NORTH NEVADA | COLORADO SPRINGS | EL PASO | CO | 80903 | 345 | 2009-11-05 | 2009 | BUSHLAND | POTTER | TX | 79012 | LINE 1102 | 42+4250 | 35.207275 | -102.072609 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 8 | 35 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 436156 | 265866.6975 | 230866.5247 | 436156 | 230866.5247 | 0 | 0 | 0 | 0 | NO | YES | NO | YES | 150 | PRECAUTIONARY | 14 | 0 | 922663 | 2009-11-05 | 762 | 780 | NO | YES | NO | NO | NO | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | OTHER | TAP CONNECTION | STEEL |  | NO | NO | NO | PIPELINE |  | 1991 | 24 | 0.25 | API 5L OR EQUIV | 52000 |  |  | A.O. SMITH | 1948 | UNDER GROUND |  | 58 | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | PIPELINE MATERIAL FEATURE INFLUENCED BY OTHER FACTORS. |  | ON NOVEMBER 5, 2009, EL PASO NATURAL GAS COMPANY'S 24" 1102 LINE RUPTURED AT APPROXIMATE MILEPOST 42+4250 IN POTTER COUNTY, TEXAS, NEAR BUSHLAND. THE NATUAL GAS PIPELINE RUPTURE RESULTED IN A FIRE. A HOME NEAR THE RUPTURE SITE WAS DESTROYED BY FIRE AND THREE INDIVIDUALS RESIDING IN THE HOME WERE INJURED AND HOSPITALIZED. OTHER NEARBY STRUCTURES SUFFERED PROPERTY DAMAGE. FINDINGS IN THE METALLURGICAL ANALYSIS REPORT OF THE RUPTURED 24" LINE INCLUDE THE FOLLOWING: -THE ORIGIN OF THE RUPTURE WAS NEAR THE SADDLE AREA OF THE ABANDONED BRANCH CONNECTION TAP. FRACTURE ORIGINATED IN THE CARRIER PIPE AT THE APPROXIMATE 7:30 POSITION ON THE UNDERSIDE OF THE TAP. -BENDING STRESSES ON THE ABANDONED BRANCH CONNECTION TAP PLACED TENSILE STRESSES ACROSS THE THICKNESS OF THE CARRIER PIPE. -THERE WAS NO INDICATION OF PROGRESSIVE CRACK GROWTH, SUCH AS ENVIRONMENTAL CRACKING OR FATIGUE IN THE FRACTURE. -THERE WAS NO EVIDENCE OF A LEAK PRESENT IN THE PIPE PRIOR TO THE OVERLOAD EVENT THAT CAUSED THE RUPTURE. -CORROSION DAMAGE WAS NOT INVOLVED IN THE RUPTURE OF THE PIPE. -NO DEFECTS WERE OBSERVED IN THE SADDLE TO CARRIER PIPE WELD THAT CONTRIBUTED TO THE RUPTURE OF THE PIPE. THE FINITE ELEMENT ANALYSIS OF THE PIPELINE RUPTURE WAS INCONCLUSIVE IN DETERMINING THE CAUSE OF FAILURE. HOWEVER, THE ANALYSIS WORK ALLOWS FOR THE FOLLOWING CONCLUSIONS TO BE REACHED: „X PRESENCE OF LAMINATIONS IN THE CARRIER PIPE MID-WALL WAS NOT A CONTRIBUTING FACTOR. „X WEIGHT OF THE ABANDONED STUB AND SOIL ON TOP OF IT WERE INSUFFICIENT TO CAUSE THE FAILURE. „X LACK OF SUPPORT UNDER THE ABANDONED STUB WAS NOT A CONTRIBUTING FACTOR. „X THE SADDLE BEING OF A ¡§DIFFERENT SIZE¡¨ (6-INCH X 20-INCH) WAS NOT A CONTRIBUTING FACTOR. „X SOIL EXPANSION UNDERNEATH THE BRANCH PIPE WAS NOT A CAUSATIVE FACTOR. „X ABNORMAL GAS OR AMBIENT TEMPERATURE CONDITIONS WERE NOT CONTRIBUTING FACTORS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090126 | 2009-12-01 | SUPPLEMENTAL FINAL | 19730 |  | TRUNKLINE GAS CO | 5444 WESTHEIMER ROAD | HOUSTON | HARRIS | TX | 77056 | 901 | 2009-10-28 | 2009 | EUDORA | CHICOT | AR | 71640 | MP 212.2/VS 69 | 406+03 | 33.096111 DEG N | -91.248611 DEG W | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408287 | 230121.8904 | 445708.563 | 79522 | 42092.6636 | 323765 | 397477.5346 | 5000 | 6138.3648 | NO | NO | NO | NO | 0 |  | 5 | 44 | 921896 | 2009-10-28 | 825 | 900 | NO | NO | NO | NO | YES | NO | NATHAN HLAVATY - DIRECTOR REGULATORY COMPLIANCE | 2817142231 | NATHAN.HLAVATY@ENERGYTRANSFER.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1960 | 30 | 0.5 | 5L | 52000 | DSAW |  | KAISER | 1959 | UNDER GROUND |  | 62 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | GALVANIC |  | YES | 1960 | NO | [57 empty] | TRUNKLINE GAS COMPANY RECEIVED A REPORT OF BUBBLES IN THE WATER IN A&nbsp;DITCH NEXT TO HIGHWAY 65. THE REPORT OF BUBBLES IN THE VICINITY OF TRUNKLINE'S PIPELINE MARKER WAS MADE TO THE AREA DIRECTOR BY A ROW SPRAYING CONTRACTOR. THE PIPE HAS BEEN SUBMITTED TO TRUNKLINE'S GAS COMPANY'S METALURIGT FOR DETERMINATION OF CAUSE. TWO METALURGIST AND A CORROSION SPECIALIST EXAMINED THE PIPE REMOVED FROM HWY 65 ON NOV.19, 2009. VISUAL INSPECTION REVEALED THREE MINOR METAL LOSS INDICATIONS BUT NO INDICATIONS OF THE LEAK SITE. APPLUS RTD WAS CONTRACTED TO FURTHER EXAMINE THE PIPE AND ALSO COULD NOT FIND THE LEAK SITE. THE MEASURED DEPTH OF THE METAL LOSS INDICATIONS WERE 0.50", 0.46", 0.45". FIELD PERSONNEL WERE INSTRUCTED TO CUT THE REMOVED 200' SECTION AT GIRTH WELDS TO FACILITATE TRANSPORTATION FROM THE LEAK SITE. EXTERNAL CORROSION WAS FOUND AND REPORTED AS THE PROBABLE CAUSE OF THE INCIDENT REPORT, TGC WAS NOT ABLE TO DETERMINE THE CAUSE OF THE LEAK. STRUCTURE TO ELECTOLYTE POTENTIALS RECORDED AT THE EXCAVATION SITE INDICATE LEVELS OF CP (-1.136 V) POTENTIAL IMPROVED AFTER INSTALLATION OF THE NEW 200' PIPE SEGMENT TO (-1.628 V) TGC CONTINUES TO UTILIZE MFL INSPECTIONS, CIS, RECTIFIER INSPECTIONS, AND TEST POINT READS TO MANAGE THE THREAT OF EXTERNAL CORROSION. ALSO TGC UTILIZES WEEKLY AERIAL PATROLS TO MONITOR LEAKS ON THE PIPELINE SYSTEM.
2022-01-31 10:32 | YES | NO | GG (Gas Gathering) | 20090127 | 2009-12-02 13:34 | SUPPLEMENTAL | 31336 |  | CHEVRON U.S.A. INC | 100 NORTHPARK BLVD | COVINGTON | ST. TAMMANY | LA | 70433 | 1420 | 2009-11-09 | 2009 |  | LAFOURCHE | LA |  |  |  | 29.0855 | -90.1643 | OFFSHORE |  | BM | 3 | LA | NO | NO | INTRASTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 552515.7233 | 1227672.956 | 0 | 0 | 1000000 | 1227672.956 | 0 | 0 | NO | NO | NO | NO | 0 |  | 6 | 0 | 923010 | 2009-11-09 | 1150 | 1173 | NO | YES | NO | NO | NO | NO | ERIN DUNAWAY | 9857736554 | ERIN.DUNAWAY@CHEVRON.COM | GATHERING | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  |  | 6 | 0.43 | A106 GRADE B SCH 80 | 35000 | SMLS | N/A | UNKNOWN |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | HURRICANE / ENVIRONMENTAL LOADING ON SEA FLOOR | [51 empty] | WE BELIEVE THAT HIGH WAVE ACTION AND CURRENTS ON THE SEA FLOOR CAUSED BY HURRICANE / TROPICAL STORM IDA CREATED EXCESSIVE LATERAL LOADING ON THIS PIPELINE. THIS LATERAL LOADING CAUSED THE PIPELINE MATERIAL TO YIELD, RESULTING IN A PARTED LINE. NOTE THAT THIS LINE IS A LA DNR REGULATED PIPELINE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090128 | 2009-12-03 11:37 | SUPPLEMENTAL FINAL | 19270 |  | TEXAS GAS TRANSMISSION LLC | 3800 FREDERICA STREET | OWENSBORO | DAVIESS | KY | 42301 | 1145 | 2009-11-04 | 2009 | GRAND CHENIER | CAMERON | LA | 70643 | APPROX. MP 30 |  | 29.83333 | 93.0 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 27625.7862 | 61383.6478 | 0 | 0 | 50000 | 61383.6478 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 |  | 922589 | 2009-11-04 | 500 | 1052 | NO | NO | NO | NO | YES | NO | JACK L. ADAMS | 7134788099 | JACK.ADAMS@BWPMLP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1981 | 20 | 0.28 | X60 | 60000 | ERW | N/A | AMERICAN STEEL |  | UNDER WATER |  |  | CORROSION | CORROSION, INTERNAL | CORROSION | INTERNAL | COATED | LOCALIZED PITTING |  | MICROBIOLOGICAL |  | YES | 1981 | NO | [57 empty] | BUBBLING OVER TOP OF PIPELINE RGC 20" IN A MARSHY AREA. LINE WAS ISOLATED FROM FGC 2 TO RGC 2A WITH 500 PSIG ON LINE. PRESSURE LOWERED TO 400 PSIG. THE WEEK OF NOVEMBER 30TH THE PIPELINE WAS TAKEN OUT OF SERVICE TO REPAIR LEAK. A FULL ENCIRCLEMENT CLAMP WAS INSTALLED AND THE LINE WAS RETURNED TO SERVICE ON 12/7/2009
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090129 | 2009-12-10 17:41 | SUPPLEMENTAL FINAL | 405 |  | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | HARRIS | TX | 77002 | 930 | 2009-11-18 | 2009 |  | FOND DU LAC | WI |  | 177.8/MLV 11 |  | 43.6548421 | -88.195338252 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220000 | 124976.5898 | 228186.9322 | 60000 | 31759.2593 | 160000 | 196427.673 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 |  | 923934 | 2009-11-18 | 775 | 975 | YES | NO | NO | NO | NO | NO | LOUIS SALINAS | 8323205305 | LOUIS_SALINAS@TRANSCANADA.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1974 | 30 | 0.38 | API | 65000 | DSAW |  | SCC | 1974 | UNDER GROUND |  | 36 | MATERIAL AND/OR WELD FAILURES | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [36 empty] | PIPE | [5 empty] | CONSTRUCTION DEFECT | POOR WORKMANSHIP | NO | YES | 12 | 4 | 1974 | WATER |  | 24 | 1689 | [12 empty] | DURING THE FOLLOW-UP TO THE ILI PIG RUN ON THE ANR 30-INCH 237/253 UPPER WISCONSIN LINE, AN ANOMALY WAS IDENTIFIED FOR FURTHER INVESTIGATION AT MP 178. INVESTIGATION FOUND A PIN HOLE LEAK AND A 15-FT. SEGMENT OF PIPE WAS REMOVED AND REPLACED. THE REPAIRS WERE MADE AND THE LINE WAS RETURNED TO SERVICE.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090130 | 2009-12-11 16:22 | SUPPLEMENTAL FINAL | 15007 |  | PACIFIC GAS & ELECTRIC CO | 375 NORTH WIGET LANE | WALNUT CREEK | CONTRA COSTA | CA | 94598 | 1000 | 2009-12-09 | 2009 | ELK GROVE | SACRAMENTO | CA | 95624 | 62.82 |  |  |  | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | LEAK |  | PINHOLE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150000 | 82877.3585 | 184150.9434 | 0 | 0 | 150000 | 184150.9434 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 925711 | 2009-12-09 | 398 | 410 | YES | NO | NO | NO | NO | NO | LAURENCE DENISTON | 9259744313 | LCD1@PGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1930 | 16 | [7 empty] | OTHER | IN EXCAVATION FOR SANDBLASTING | 32 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | COATED | LOCALIZED PITTING |  | OTHER | UNDER INVESTIGATION | YES | 1980 | NO | [57 empty] | ON 12/9/09 AT 1000 HOURS MEARS, A PG&E CONTRACTOR, WAS SANDBLASTING TRANSMISSION LINE 108 WHICH CAUSED A PIN-HOLE LEAK IN THE 16-INCH STEEL PIPELINE RELEASING GAS TO ATMOSPHERE. THE SANDBLASTING WAS PART OF AN EXTERNAL CORROSION DIRECT ASSESSMENT (ECDA). THE OPERATING PRESSURE WAS REDUCED TO 306 PSIG (80% OF OPERATING PRESSURE). REPAIRS ARE SCHEDULED TO BEGIN ON 12/11/09 (EMEREGENCY PLUGGING EQUIPMENT REQUIRED) AND TEMPORARY LNG IS IN PLACE TO PROVIDE SUPPLEMENTAL GAS, IF NEEDED, PRIOR TO AND DURING THE REPAIRS, RESULTING IN NO LOSS OF SERVICE TO CUSTOMERS. NO POLICE OR FIRE DEPARTMENTS ON SCENE AND NO MEDIA PRESENT. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT BECAME REPORTABLE WHEN THE DAMAGES TO THE PIPELINE EXCEEDED $50,000.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090131 | 2009-12-14 07:30 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 811 | 2009-11-14 | 2009 | CAMERON | MARSHALL | WV | 26033 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | DEHYDRATION UNITS FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600000 | 3094088.0503 | 6874968.5535 | 0 | 0 | 5600000 | 6874968.5535 | 0 | 0 | NO | NO | NO | NO | 0 |  | 0 | 45 | 923523 | 2009-11-14 |  |  | NO | NO | NO | NO | YES | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | COMPONENT |  |  |  | NO | NO | NO | OTHER | DEHYDRATION UNITS | [9 empty] | ABOVE GROUND |  |  | OTHER | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [63 empty] | FAILURE OF A DEHYDRATION UNIT IN ADALINE COMPRESSOR STATION YARD. |  | ON NOVEMBER 14, 2009 AT 08:11 AM, A FIRE WAS REPORTED IN AN ETHYLENE GLYCOL DEHYDRATION UNIT IN THE ADALINE COMPRESSOR STATION IN MARSHALL COUNTY, WV. GAS WAS EVACUATED FROM THE STATION PIPING AND THE COMPRESSOR STATION SHUT DOWN BY A COMPANY EMPLOYEE WHO ACTIVATED THE EMERGENCY SHUT DOWN (ESD) SYSTEM. THE EMPLOYEE RESPONDED TO THE SITE WITHIN 15 MINUTES FROM THE TIME HE WAS CALLED. THE FIRE WAS EXTINGUISHED BY THE LOCAL FIRE DEPARTMENT IN LESS THAN AN HOUR. SPILL KITS WERE USED TO CONTAIN THE ETHYLENE GLYCOL. THERE ARE THREE DEHYDRATION UNITS AT THIS LOCATION. TWO UNITS WERE COMPLETELY DESTROYED, AND THE THIRD ONE WAS DAMAGED. NEW UNITS ARE IN THE PROCESS OF BEING INSTALLED. THE MAIN CAUSE THAT LED TO THE FAILURE OF THE DEHYDRATION UNIT AND INITIATED A FIRE WAS IDENTIFIED AS FOLLOWS: THE EXCESSIVE FLUIDS IN THE SYSTEM OVERLOADED THE REBOILER AND CAUSED THE RELIEF VALVES TO OPEN, VENTING THE VAPORS AND LIQUIDS. THE VAPORS IGNITED AND THE ENSUING FIRE DAMAGED FUEL LINES ON THE REBOILERS. THE QUALITY OF THE GAS TO THE COMPRESSOR STATION WAS OUTSIDE OF COMPANY STANDARDS. THERE WERE NO FLUID HANDLING FACILITIES IN PLACE CAPABLE OF REMOVING THE HYDROCARBON FLUIDS IN A SAFE AND EFFICIENT MANNER. IN THE ROOT CAUSE ANALYSIS (RCA) REPORT, A LIST OF RECOMMENDATIONS WERE PROVIDED TO AVOID SIMILAR INSTANCES FOR ANY FLUID (HYDROCARBON) TO BACK-UP AND CAUSE A SIMILAR EVENT THAT LEAD TO THE FIRE IN THE DEHYDRATION UNITS. A NEW DEHYDRATION SYSTEM WAS INSTALLED. A NEW PIPELINE HAS BEEN INSTALLED AND IS NOW IN SERVICE FROM THE POINT OF RECEIPT (FROM THE PRODUCER) TO THE EXTRACTION PLANT. TEMPORARY LAUNCHERS/RECEIVERS WERE INSTALLED ON THE PIPELINES TO ENSURE THAT THE PIPELINE SYSTEM IS PERIODICALLY CLEARED FROM EXCESS FLUIDS TO AVOID SIMILAR OCCURRENCE. A RCA REPORT WAS SUBMITTED TO THE WV PSC.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090132 | 2009-12-16 10:04 | SUPPLEMENTAL FINAL | 2616 |  | COLUMBIA GAS TRANSMISSION CORP | 1700 MACORKLE AVENUE SE | CHARLESTON | KANAWHA | WV | 25314 | 1640 | 2009-11-16 | 2009 | SANDYVILLE | JACKSON | WV | 25275 |  |  | 38.84527 | -81.69804 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | LEAK |  | CONNECTION FAILURE |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5167 | 2864.3765 | 6226.7614 | 167 | 88.3966 | 5000 | 6138.3648 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 923776 | 2009-11-14 | 1458 | 1700 | NO | NO | NO | NO | YES | NO | GEORGE HAMATY | 3043573728 | GHAMATY@NISOURCE.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | OTHER | PIG VALVE | 2004 |  |  | ANSI 900 |  |  | 4-IN PIG VALVE | TULSA VALVE | 2004 | ABOVE GROUND |  |  | MATERIAL AND/OR WELD FAILURES | COMPONENT | MATERIAL/WELD/EQUIP FAILURE | JOINT/FITTING/COMPONENT | [32 empty] | VALVE | [9 empty] | MATERIAL DEFECT |  | NO | NO | [19 empty] | ON NOVEMBER 16, 2009 AT 16:40, A CALL WAS REPORTED TO COLUMBIA GAS TRANSMISSION MONITORING CENTER VIA A PASSER-BY WHO REPORTED A GAS LEAK ON A WELL LINE IN RIPLEY STORAGE FIELD. THE FIRE DEPARTMENT WAS ON SITE SECURING THE NEARBY ROAD. THE VALVE WAS ISOLATED TO STOP THE RELEASE OF GAS. COMPANY PERSONNEL REPORTED TO THE SITE WITHIN 20 MINUTES. THE STORAGE LINE WAS ISOLATED AND THE LEAK WAS DETERMINED TO BE FROM A PIG VALVE. NO FIRE WAS INVOLVED IN THIS EVENT. FURTHER FIELD INVESTIGATION INDICATED THAT FOUR CAPSCREWS ASSOCIATED WITH THE TRUNNION PLATE OF THE 4” SHUT-OFF STYLE PIG VALVE HAD FAILED. THE MANUFACTURER OF THIS VALVE WAS NOTIFIED, THE FAILED VALVE WAS REMOVED FROM THE SITE AND THE STORAGE LINE WAS PLUGGED AND CAPPED AT BOTH ENDS. THE FAILED VALVE AND THE RECOVERED CAPSCREWS WERE SENT TO A LABORATORY FOR FURTHER ANALYSIS TO DETERMINE THE CAUSE OF THE FAILURE. LABORATORY ANALYSIS DISLPAYED THAT THE CAPSCREWS WERE NOT PROPERLY TEMPERED TO THE REQUIRED TEMPERATURE LEVEL, EVEN THOUGH THEY MET THE CHEMICAL COMPOSITION AND TENSILE PROPERTY REQUIREMENTS. THERE WERE NO INDICATIONS OF ELONGATION, FRETTING OR THREAD DEFORMATION INDICATIVE OF OVER TORQUING THE SCREWS DURING INSTALLATION. THE METALLURGICAL FAILURE ANALYSIS OF PIG VALVE BOLTS REPORT WAS SUBMITTED TO THE WVPSC.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090133 | 2009-12-18 11:10 | SUPPLEMENTAL FINAL | 31531 |  | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST 5TH STREET | TULSA | TULSA | OK | 74103-4298 | 1234 | 2009-12-03 | 2009 | COLORADO CITY | MITCHELL | TX | 79512 |  |  | 32.28772 | -101.00385 | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205654 | 121108.4918 | 160898.8654 | 131133 | 69411.4491 | 74521 | 91487.4164 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 10 | 925209 | 2009-12-03 | 878 | 960 | NO | YES | NO | NO | NO | NO | PATTI FORD | 9185887131 | PATTI.FORD@ONEOK.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 16 | 0.25 | X46 | 46000 | ERW | N/A | UNKNOWN |  | UNDER GROUND |  | 50 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | PROFESSIONAL EXCAVATOR | ELECTRIC |  | NO |  |  |  |  | YES |  | YES | ACCURATE | [37 empty] | THE ONEOK WESTEX TRANSMISSION MORGAN CREEK 16 INCH 4100-000 LINE RUPTURED AT 12:34 PM ON THURSDAY DECEMBER 3, 2009. GAS CONTROL NOTICED THE LINE PRESSURE REDUCTION AND COMPANY PERSONNEL WERE DISPATCHED TO INVESTIGATE. THE RUPTURE OCCURRED APPROXIMATELY 133 FEET TO THE EAST OF PAVED COUNTY ROAD 670, 4.5 MILES SOUTH OF WESTBROOK TX IN MITCHELL COUNTY WITH ONE CUSTOMER IMPACTED. THE RAILROAD COMMISSION OF TEXAS WAS NOTIFIED AT 3:28 PM (INCIDENT NUMBER 10-CA-040). THE RUPTURED LINE WAS ISOLATED AT 2:44 PM AND THE LINE BLOWN DOWN BY 4:45 PM. PHMSA WAS NOTIFIED AT 6:17 PM (NRC NUMBER 925209). THE PIPE WAS REPAIRED BY 9:00 AM ON FRIDAY DECEMBER 4, 2009. SEVERAL GOUGES (APPROXIMATELY 0.10 INCH DEEP) WERE OBSERVED ON THE OUTSIDE OF THE PIPE IN THE VICINITY OF THE RUPTURE INITIATION SITE. A GUY WIRE WAS OBSERVED HANGING LOOSE FROM AN ELECTRICAL POWER POLE LOCATED ABOUT 18 FEET FROM THE RUPTURE INITIATION SITE. A GUY WIRE ANCHOR WAS LOCATED ON THE GROUND SURFACE 83 FEET FROM THE ELECTRICAL POWER POLE. THE RUPTURED PIPE SECTION WAS SENT TO AN INDEPENDENT LAB FOR FAILURE ANALYSIS. THE RESULTS OF THE FAILURE ANALYSIS INDICATE THE PIPELINE RUPTURED DUE TO A REDUCTION IN WALL THICKNESS WHICH REDUCED THE HOOP STRESS CAPACITY OF THE PIPE. THE REDUCTION IN WALL THICKNESS WAS CAUSED BY GOUGES FOUND ON THE OD OF THE PIPE. THE FAILURE ORIGINATED AT THE GOUGES.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090134 | 2009-12-21 09:57 | SUPPLEMENTAL FINAL | 2620 |  | COLUMBIA GULF TRANSMISSION CO | 1700 MACCORKLE AVE, PO BOX 1273 | CHARLESTON | KANAWHA | WV | 25325-1273 | 503 | 2009-12-06 | 2009 | RAYNE | ACADIA | LA | 70578 |  |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | ESD VALVE OPENED AT COMPRESSOR STATION | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114700 | 69632.1774 | 64204.8771 | 109700 | 58066.5123 | 5000 | 6138.3648 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 0 | 925373 | 2009-12-06 | 840 |  | NO | NO | NO | NO | NO | NO | GREGORY LAGO | 3043572465 | GLAGO@NISOURCE.COM | TRANSMISSION | OTHER | CONTROLLER INSTRUMENTATION | OTHER | CONTROLLER MODULE | NO | NO | NO | COMPRESSOR | [10 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | FAILURE OF CONTROL INSTRUMENTATION CAUSED AN EIGHT INCH PLUG TYPE ESD VENT VALVE ON HORSEPOWER BLOCK NUMBER 3 TO OPEN (FAIL SAFE POSITION) CAUSING THE RELEASE OF NATURAL GAS AT THE RAYNE COMPRESSOR STATION. AFTER ASSESSMENT OF THE SITUATION, THE VALVE WAS MANUALLY CLOSED BY COMPANY PERSONNEL. THE LOUISIANA STATE POLICE RESPONDED, HOWEVER, THERE WAS NO FIRE, NO EXPOSION AND NO INJURIES ASSOCIATED WITH THE EVENT. THE EVENT WAS REPORTED DUE TO THE COST OF LOST NATURAL GAS ESTIMATED AT OVER $50,000. THE COMMUNICATION BLOCK HAS BEEN REPLACED. IN ADDITION, THE PROGRAM LOGIC ASSOCIATED WITH THE CONTROL SYSTEM HAS BEEN ADJUSTED TO ENSURE THAT THE HORSEPOWER BLOCK IS ISOLATED IN THE EVENT THAT THE ESD VENT VALVE OPENS.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090135 | 2009-12-21 | SUPPLEMENTAL FINAL | 31978 |  | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | DALLAS | TX | 75240 | 1550 | 2009-11-22 | 2009 | LONGLAKE (PALESTINE) | ANDERSON | TX | 75801 | S & S17 JCT MM9 |  |  |  | ONSHORE | 1 |  |  |  | NO | NO | INTRASTATE | RUPTURE |  |  |  | LONGITUDINAL-TEAR/CRACK | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92336 | 53417.7904 | 83972.4576 | 42079 | 22273.2978 | 48757 | 59857.6503 | 1500 | 1841.5094 | NO | NO | NO | NO | 0 |  | 1 | 45 | 924373 | 2009-11-22 | 414 | 500 | NO | NO | NO | NO | YES | NO | MICHAEL ARCHER COMPLIANCE ANALYST | 2142062879 | MICHAEL.ARCHER@ATMOSENERGY.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1941 | 12.75 | 0.28 |  | 38 | LAP |  |  |  | UNDER GROUND |  | 21 | OTHER OUTSIDE FORCE DAMAGE | RUPTURE OF PREVIOUSLY DAMAGED PIPE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [65 empty] | THIS SECTION OF PIPELINE WAS INSTALLED IN 1941. APPARENTLY A THIRD PARTY EXCAVATOR DAMAGED THE PIPELINE SOMEWHERE BETWEEN WHEN THE LINE WAS INSTALLED AND WHEN THE RUPTURE OCCURRED. THE FAILED SECTION OF PIPE WAS SENT TO A METALLURGICAL LAB TO DETERMINE THE CAUSE OF FAILURE. THE RESULTS OF THE LAB TESTING DETERMINED THE PIPELINE FAILED DUE TO SIGNIFICANT MECHANICAL GOUGING AND DENTING DAMAGE TO THE EXTERNAL PIPE SURFACE.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090136 | 2009-12-31 14:16 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1826 | 2009-12-05 | 2009 | BETHANY | CADDO | LA | 71007 | BETHANY TB ST. | LINE N 994+20/LINE NT-2 | +32.305706 | -94.042066 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | RELIEF VALUE FAILURE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22315 | 13468.4922 | 13452.2266 | 19966 | 10568.4228 | 2349 | 2883.8038 | 0 | 0 | NO | NO | NO | YES | 7 | PRECAUTIONARY | 19 | 28 | 925365 | 2009-12-05 | 230 | 250 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT , DOT COMPLIANCE MANAGER | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | REGULATOR/METERING |  | 1954 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | VALVE | [11 empty] | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE EMERGENCY RESPONDERS CLOSED A ROAD AND EVACUATED 7 PERSONS. AT APPROXIMATELY 18:26 HRS ON DECEMBER 05, 2009 THE CENTERPOINT ENERGY GAS TRANSMISSION (CEGT) CONTROLLER NOTICED A SIGNIFICANT DROP IN PRESSURE AT THE BETHANY TOWN BORDER STATION (LINES NT-2 & N) AND THEY DISPATCHED COMPANY PERSONNEL TO THE SITE. EMERGENCY RESPONDERS ARRIVED ON SITE FIRST AND CLOSED BETHANY STATE LINE ROAD DUE TO THE LOCATION OF THE ESCAPING GAS BEING WITHIN 150 FEET OF THE HIGHWAY. THE EMERGENCY RESPONDERS ALSO EVACUATED SEVEN PEOPLE FROM TWO RESIDENCES APPROXIMATELY A ¼ MILE FROM THE INCIDENT SITE TO ENSURE SAFETY. SUBSEQUENTLY, THE SITUATION WAS PROMPTLY BROUGHT UNDER CONTROL BY CEGT PERSONNEL WHO WERE ABLE TO CLOSE A VALVE TO SECURE THE GAS RELEASE AND THE SITE WAS MADE SAFE AT 19:28 HRS. THE ROAD AND WAS RE-OPENED AND THE EVACUATED RESIDENCES WERE ALLOWED TO RETURN HOME IN LESS THAN TWO HOURS. THE RELEASE STEMMED FROM A MALFUNCTIONING RELIEF VALVE (OVER-PROTECTION DEVICE) AT A TOWN BORDER STATION.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090137 | 2009-12-31 15:14 | ORIGINAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 615 | 2009-12-10 | 2009 | LANTY | CONWAY | AR | 72110 | ROUND MT. COMPRESS ST. | LINE J 3392+46 | +35.335000 | -92.673900 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FAILED RELAY ON BLOW DOWN VALVE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128315 | 78170.2077 | 68488.9794 | 127500 | 67488.4259 | 815 | 1000.5535 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 29 | 925771 | 2009-12-10 | 945 | 1000 | NO | YES | NO | NO | NO | NO | JOHNNY L CAVITT , DOT COMPLIANCE MANAGER | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | COMPONENT |  | STEEL |  | NO | NO | NO | COMPRESSOR |  | 1996 | [8 empty] | ABOVE GROUND |  |  | EQUIPMENT | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [53 empty] | INSTRUMENTATION | [11 empty] | AT APPROXIMATELY 06:15 HRS ON DECEMBER 10, 2009 THE CENTERPOINT ENERGY GAS TRANSMISSION (CEGT) CONTROLLER NOTICED A SIGNIFICANT DROP IN PRESSURE ON LINE J BETWEEN THE DUNN COMPRESS STATION DISCHARGE AND THE ROUND MOUNTAIN COMPRESSOR STATION SUCTION AND THEY DISPATCHED COMPANY PERSONNEL TO THE SITE. SUBSEQUENTLY, THE SITUATION WAS PROMPTLY BROUGHT UNDER CONTROL BY CEGT PERSONNEL WHO WERE ABLE TO CLOSE A VALVE TO SECURE THE GAS RELEASE AND THE SITE WAS MADE SAFE AT 07:44 HRS. THE 6” SUCTION HEADER BLOW DOWN VALVE, (J-30) WHICH IS AN ESD VALVE, OPERATED TO THE OPEN POSITION CAUSING GAS TO BE BLOWN DOWN FROM THE HEADER AND LINE J. THE VALVE OPERATED BECAUSE THE GAS RELAY THAT CONTROLS THE ESD FUNCTION OF THE VALVE FAILED AND ALLOWED THE VALVE TO OPERATE, WITHOUT ANY COMMAND FROM THE ESD SYSTEM.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090138 | 2010-01-12 11:48 | SUPPLEMENTAL FINAL | 31728 |  | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA, SUITE 2800 | HOUSTON | HARRIS | TX | 77046 | 1100 | 2009-12-22 | 2009 | WHARTON | WHARTON | TX |  | 106.94 / 5646+40 |  | 29.32903 | 96.00371 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | HARD SPOT | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79363 | 45834.7211 | 73129.1603 | 34800 | 18420.3704 | 44563 | 54708.7899 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 30 | 926880 | 2009-12-22 | 655 | 930 | YES | NO | NO | NO | NO | NO | GLENN FLOYD | 9016853471 | GLENN.FLOYD@BWPMLP.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1952 | 30 | 0.38 | X-52 | 1300 | ELECTRIC FLASH WELD | N/A | A.O. SMITH | 1952 | UNDER GROUND |  | 32 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | OTHER | HARDSPOT | [10 empty] | MATERIAL DEFECT |  | NO | YES | 4 | 1 | 1952 | WATER |  | 8 | 1180 | [12 empty] | FOUND RELEASE DURING AIR PATROL WITH COMPANY PERSONNEL. FIELD VERIFICATION PROVED THERE WAS A RELEASE. EXCAVATION DETERMINED RELEASE WAS UNDER A PREVIOUSLY INSTALLED HARD SPOT SHIELD. PERMANENT PRESSURE CONTAINING REINFORCEMENT WAS INSTALLED OVER SHIELD.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090139 | 2010-01-21 10:59 | SUPPLEMENTAL FINAL | 18516 |  | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, SUITE 501 | BIRMINGHAM | JEFFERSON | AL | 35209 | 2307 | 2009-12-31 | 2009 | HEFLIN | CLEBURNE | AL | 36264 | 399.631 | NORTH MAIN LOOP | 33.62998 | -85.4608 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | OTHER | CIRCUMFERENTIAL PARTIAL SEPARATION IN WRINKLE BEND | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265000 | 148698.7538 | 297399.2546 | 40000 | 21172.8395 | 225000 | 276226.4151 | 0 | 0 | NO | NO | NO | NO | 0 |  | 1 | 38 | 927518 | 2009-12-31 | 462 | 500 | NO | NO | NO | NO | YES | NO | KENNETH C. PETERS | 2053257554 | KEN.PETERS@ELPASO.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1948 | 24 | 0.25 |  | 52000 | SAW |  | REPUBLIC STEEL | 1948 | UNDER GROUND |  | 71 | MATERIAL AND/OR WELD FAILURES | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [30 empty] | WRINKLE BEND | [11 empty] | CONSTRUCTION DEFECT | POOR CONSTRUCTION PROCEDURES | NO | YES | 7 | 14 | 1996 | WATER |  | 8 | 823 | [12 empty] | CLEBURNE COUNTY (ALABAMA) EMA REPORTED A SUSPECTED NATURAL GAS RELEASE IN THE VICINITY OF SOUTHERN NATURAL GAS (SNG) COMPANY'S 24" NORTH MAIN LOOP PIPELINE ON DECEMBER 31, 2009. DISPATCHED SNG PERSONNEL CONFIRMED THE EXISTENCE OF THE GAS RELEASE AT APPROXIMATE PIPELINE MILEPOST 399.631, ABOUT 835 FEET EAST OF CLEBURNE COUNTY ROAD 488. THE 24-INCH NORTH MAIN LOOP LINE LEAKED DUE THE CUMULATIVE EFFECTS OF STRESSES (TENSILE AND TORSIONAL) ACTING ON A WRINKLE BEND CONTAINING A LONGITUDINAL WELD SEAM. THE FAILURE CONSISTED OF A 2’- 7.5” LONG CIRCUMFERENTIAL CLEAVAGE FRACTURE ALONG THE APEX OF THE CONVOLUTION OF AN UNDER BEND. STRUCTURAL CAPACITY WAS EXCEEDED DUE TO THE FOLLOWING FACTORS: (A) NATURAL SOIL MOVEMENT DUE TO THE GEOLOGICAL CHARACTERISTICS COMBINED WITH THE PRESENCE OF WATER (B) GEOMETRICAL STRESSES INHERENT IN THE BENDING OF THE PIPE MATERIAL AND PROPERTIES OF THE LONGITUDINAL WELD METAL (C) NORMAL INTERNAL PRESSURES ASSOCIATED WITH THE OPERATION OF THE NATURAL GAS PIPELINE (D) EXCAVATIONS AND SOIL DISTURBANCES NEARBY THE PIPELINE’S RIGHT-OF-WAY. THE WRINKLE BEND WAS INSTALLED DURING THE PIPELINE'S ORIGINAL CONSTRUCTION AND WAS USED IN A SAG BEND WITH THE PIPE'S LONGITUDINAL SEAM HAVING BEEN PLACED IN THE INSIDE PORTION OF THE BEND. THE FAILURE SITE WAS REPAIRED BY REPLACEMENT WITH A NEW PIPELINE SEGMENT.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090140 | 2010-01-21 17:00 | SUPPLEMENTAL FINAL | 602 |  | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA, SUITE 1100 | HOUSTON | HARRIS | TX | 77002 | 1342 | 2009-12-22 | 2009 | DODDRIDGE | MILLER | AR | 71834 |  | LINE A 1076+98 | +33.155144 | -93.896736 | ONSHORE | 1 |  |  |  | NO | NO | INTERSTATE | OTHER | FLOODING, DEBRIS SEPARATED PIPELINE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267484 | 150292.7935 | 297736.3952 | 43884 | 23228.7222 | 223600 | 274507.673 | 0 | 0 | NO | NO | NO | NO | 0 |  | 2 | 44 | 926909 | 2009-12-22 | 272 | 350 | NO | NO | YES | NO | NO | NO | JOHNNY L CAVITT , DOT COMPLIANCE MANAGER | 3184293606 | JOHNNY.CAVITT@CENTERPOINTENERGY.COM | TRANSMISSION | JOINT |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1970 | 10 | 0.37 | GRADE B | 35000 | SEAMLESS |  | UNKNOWN |  | UNDER WATER |  |  | NATURAL FORCES | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [12 empty] | OTHER | DAMAGED AND SEPARATED BY DEBRIS | [51 empty] | THIS INCIDENT TOOK PLACE ON ONE OF OUR TWO 10” LINE A RIVER CROSSINGS DURING HIGH WATER AND FLOODING OF THE SUPHUR RIVER IN MILLER COUNTY ARKANSAS. WE LOCATED THE LEAK AND ISOLATED THE NORTH RIVER CROSSING. WHEN THE WATER RETURNED TO A SAFE LEVEL, CONTRACT DIVERS EXAMINED THE LINE AND FOUND IT TO HAVE BEEN DAMAGED AND SEPARATED BY DEBRIS. THE LINE REMAINS OUT OF SERVICE AND IS BEING FED BY WITH THE ONE REMAINING RIVER CROSSING.
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090141 | 2010-01-25 | SUPPLEMENTAL FINAL | 13063 |  | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | ERIE | NY | 14221-5887 | 1130 | 2009-12-21 | 2009 | EDEN | ERIE | NY | 14057 | APPROX 3.2 MILES SOUTH OF | N/A | N42.61020 | W078.81948 | ONSHORE | 2 |  |  |  | NO | NO | INTERSTATE | RUPTURE |  |  |  | CIRCUMFERENTIAL-SEPARATION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84800 | 49124.01 | 76312.2583 | 39800 | 21066.9753 | 40000 | 49106.9182 | 5000 | 6138.3648 | NO | NO | NO | YES | 6 | THREAT TO THE PUBLIC | 1 | 2 | 926772 | 2009-12-21 | 179 | 220 | NO | NO | NO | NO | YES | NO | BRIAN A KEMPSKI SUPERINTENDENT | 7168272131 | KEMPSKIB@NATFUEL.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO | PIPELINE |  | 1910 | 20 | 0.38 | UNKNOWN | 24000 | UNKNOWN | UNKNOWN | UNKNOWN | 1910 | UNDER GROUND |  | 42 | CORROSION | CORROSION, EXTERNAL | CORROSION | EXTERNAL | BARE | LOCALIZED PITTING |  | GALVANIC |  | YES | 1972 | NO | [57 empty] | ON DECEMBER 21,2009, NATIONAL FUEL GAS DISPATCHER RECEIVED A CALL AT APPROXIMATELY 11:30 AM THAT THERE WAS A NATURAL GAS INCIDENT IN THE VICINITY OF 9999 NEW OREGON RD. IN NORTH COLLINS, ERIE COUNTY, NY. DISPATCHER DETERMINED FROM SCADA AND OTHER PHONE CONTACTS, THAT LINE KNY WAS EXPERIENCING GAS LOSS. A REGULATOR CREW WAS DISPATCHED TO CLOSE BLOCK VALVE NCE-5 IN NORTH COLLINS AND SEND A SUPERVISOR TO NORTH BOSTON STATION TO CLOSE VALVES BNE-193 AND 195.VALVES BNE-193 & 195 WERE CLOSED AT 12:12 PM AND THE VALVE NCE-5 WAS CLOSED AT 12:32. AT THAT TIME THE LINE WAS ISOLATED.WHEN THE SITUATION WAS UNDER CONTROL IT WAS DETERMINED THAT A RUPTURE HAD OCCURRED ON LINE KNY APPROXIMATELY 641’ SOUTH OF LOWER KNOLL RD, AND NORTH OF NEW OREGON RD. FURTHER INVESTIGATION REVEALED THAT NO PERSONAL INJURIES OR DEATHS RESULTED FROM THE INCIDENT. THERE WAS SOME PROPERTY DAMAGE AT 9999 NEW OREGON RD. THE PIPELINE WAS PAIRED BY REPLACING APPROXIMATELY 4 FEET OF 20” OD, 0.375" WALL, X-52 GRADE, PRETESTED STEEL PIPE. PART G: NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE EVENT - CONTINUED:INVESTIGATION UPDATE: THE FAILED SECTION WAS DELIVERED TO BATTELLE, COLUMBUS OHIO FOR A COMPLETE METALLURGICAL AND FAILURE ANALYSIS TO DETERMINE THE ROOT CAUSE OF THE FAILURE. BATTELLE CONCLUDED:"THE ORIGIN FOR THE FAILURE WAS IDENTIFIED AS A PAIR OF PITS COINCIDENTALLY LOCATED WITHIN THE CROWN OF THE PIPE IN THE VICINITYOF MAXIMUM AXIAL STRESS. THE UNUSUAL LOCAL AXIAL LOADING ACTED ON THIS PAIR OF COINCIDENTALLY LOCATED PITS CAUSING FAILURE, WHICH WAS FACILITATED BY WINTER TEMPERATURES WORKING IN CONJUNCTION WITH THE INHERENTLY HIGH DBTP' LEADING TO REDUCED FRACTURE TOUGHNESS. DBTT - DUCTILE BRITTLE TRANSITION TEMPERATURE. BATTELLE ALSO CONCLUDED: "THE FAILURE WAS DUE TO A UNIQUE COMBINATION OF FACTORS THAT INVOLVED LOCALLY HIGH BENDING AND AXIAL STRAINS UNIQUE TO THE VICINITY OF OVER BEND ACROSS THE RIDGE WHERE THE FAILURE OCCURRED, FREE OF OTHER CONTRIBUTORY OR CAUSATIVE FACTORS."
2022-01-31 10:32 | NO | NO | GT (Gas Transmission) | 20090142 | 2013-04-19 | ORIGINAL FINAL | 4060 |  | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | CUYAHOGA | OH | 44101 | 2042 | 2006-09-26 | 2006 | CANTON | STARK | OH | 44718 |  |  | 41.51834 | -81.27896 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78995 | 46023.9223 | 100962.7536 | 2095 | 834.5935 | 76900 | 100128.1601 | 0 | 0 | YES | NO | YES | NO | 0 |  | 0 | 6 | 812854 | 2006-09-27 | 1472 | 1600 | NO | NO | YES | NO | NO | NO | PAMELA MICHALSKI, PROGRAM AMANGER | 2167366849 | PAM.MICHALSKI@DOM.COM | TRANSMISSION | COMPONENT |  | OTHER | BRASS SEAL | NO | NO | NO | COMPRESSOR |  | 1998 | [8 empty] | INSIDE/UNDER BUILDING |  |  | EQUIPMENT | RUPTURED OR LEAKING SEAL/PUMP PACKING | MATERIAL/WELD/EQUIP FAILURE | RUPTURED OR LEAKING SEAL/PUMP PACKING | [65 empty] | ON SEPTEMBER 26, 2006 AT APPROXIMATELY 8:42 PM A FIRE/EXPLOSION OCCURED AT DOMINION EAST OHIO'S ROBINSON COMPRESSOR FACILITY LOCATED AT 5433 WEST BLVD IN CANTON, OH. EMERGENCY SHUTDOWN DEVICES WERE ACTIVATED AUTOMATICALLY BY STATION FIRE ALARMS AND MAUALLY BY DOMINION EASTOHIO GAS PERSONNEL ON SITE AT APPROXIMATELY 8:48 PM SHUTTING DOWN ALL FOUR RECIPROCATING COMPRESSORS AT THE FACILITY. A COURTESY CALL WAS MADE TO THE PUBLIC TILITIES COMMISSION OF OHIO AT 9:30 PM ON SEPTEMBER 26,2006 UNTIL DAMAGE ASSESSMENT COULD BE CONDUCTED TO DETERMINE THE ORIGIN OF THE EXPLOSION AND AMOUNT OF PROPERTY DAMAGES. PRELIMINARY DAMAGE ASSESSMENT INDICATED DAMAGE TO THE #4 COMPRESSOR UNIT AIR INTAKE, SCAVENGING UNITL LOWER CONVERS ON #4 AND #5 COMPRESSOR CYLINDERS AND THE TURBO-CHARGER. ALL FOUR COMPRESSOR UNITS REMAINED SHUT-DOWN FOR THE NIGHT UNTIL FURTHER INVESTIGATION. AN INVESTIGATION WS CONDUCTED BY DOMINION EAST OHIO AND THE PUBLIC UTILITIES COMMISSION OF OHIO ON SEPTEMBER 27, 2006 AT APPROXIMATELY 3:00 PM TO THE NATIONAL RESPONSE CENTER AND TO THE PUBLIC UTILITIES COMMISSION OF OHIO BY TELEPHONE. NRC #812542 WAS ASSIGHNED TO THIS EVENT AT THAT TIME. FURTHER INVESTIGATION REVEALED THAT THE #4 COMPRESSOR UNIT HAD SHUT DOWN ON SEPTEMBER 26, 2006 AT APPROXIMATELY 6:58 PM DUE TO AN OVER-SPEED CONDITION. THE COMPRESSOR OPERATOR ATTEMPTED TO RE-START THE UNIT, THE UNIT BACKFIRED. THE COMPRESSOR OOPERATOR SUSPECTED FUEL IN THE AIR INTAKE, PURGED THE INTAKE WITH AIR AND RE-STARTED THE UNIT. JACKSON TOWNSHIP FIRE DEPARTMENT RESPONDED TO AN EXPLOSION CALL FROM A LOCAL RESIDENT AT APPROXIMATELY 7:30 PM. FIRE DEPARTMENT PERSONNEL SPOKE WITH THE COMPRESSOR OPERATOR AND DETERMINED THE RESIDENT HAD HEARD THE BACK-FIRE OF #4 COMPRESSOR UNIT. ALL FOUR COMPRESSORS OPERATING NORMAL AT THIS TIME. AT APPROXIMATELY 8:32 PM ON SEPTEMBER 26, 2006, #4 COMPRESSOR UNIT SHUTS-DOWN FOR A SECOND TIME DUE TO AN OVER-SPEED CONDITION. COMPRESSOR OPERATOR PURGES AIR INTAKE AND ATTEMPTS TO RESTART THE COMPRESSOR UNIT WHEN THE EXPLOSION OCCURRED. EMERGENCY SHUTDOWN DEVICES WERE ACTIVATED AUTOMATICALLY BY STATION FIRE ALARMS AND MANUALLY BY DOMINION EAST OHIO GAS PERSONNEL ON SITE AT APPROXIMATELY 8:48 PM. JACKSON TOWNSHIP FIRE DEPARTMENT ARRIVED ON SCENE WITHIN MINUTES AND NOTED A SMALL FIRE IN THE AIR INTAKE AND AROUND THE BASE OF #4 COMPRESSOR UNIT ENGINE. INVESTIGATION ON SEPTEMBER 27, 2006 INDICATED THE #3 COMPRESSOR CYLINDER OF #4 COMPRESSOR UNIT HAD LEAKAGE THROUGH THE INNER HEAD PISTON SEAL CAUSING GAS TO BE RELEASED THROUGH THE 2" VENT LINE. THE AIR INTAKE AND 2" VENT ARE BOTH LOCATED ON THE SOUTH SIDE OF THE COMPRESSOR BUILDING. DURING THE RESTART, GAS WAS PULLED INTO THE AIR INTAKE AND CREATED AN EXPLOSIVE MIXTURE IN THE INTAKE SYSTEM. THE FOLLOWING STEPS HAVE BEEN TAKEN BY DOMINION EAST OHIO TO PREVENT RECCURRENCE. AN IGNITON LOCK-OUT TIMER HAS BEEN INSTALLED TO PREVENT IGNITION FROM BEING OPERATED PRIOR TO A TEN-SECOND PURGE OF THE AIR INTAKE, THIS IS AN INCREASE FROM A MANUAL 3-5 SECOND COUNT PRIOR TO IGNITION. AN ADDITIONAL 3’ OF 2" PIPE HAS BEEN INSTALLED ON THE VENTS TO PROVIDE ADDITIONAL SAFETY FOR GAS BEING VENTED FROM THE COMPRESSORS. OPERATING PROCEDURES HAVE BEEN MODIFIED TO INCLUDE A COMPLETE BLOW-DOWN OF INLET AND OUTLET GAS AT COMPRESSORS DURING SHUTDOWN AND PRIOR TO RESTART.
2022-01-31 10:32 | YES | NO | GT (Gas Transmission) | 20090143 | 2013-05-07 | SUPPLEMENTAL | 1088 |  | BALTIMORE GAS & ELECTRIC CO | 1699 LEADENHALL ST | BALTIMORE | BALTIMORE | MD | 21230 | 1340 | 2004-08-23 | 2004 | BALTIMORE | BALTIMORE | MD | 21229 |  |  | 39.303 | -76.7 | ONSHORE | 3 |  |  |  | NO | NO | INTRASTATE | OTHER | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176000 | 108046.7947 | 195051.1531 | 56000 | 28884.2105 | 120000 | 166166.9425 | 0 | 0 | YES | NO | NO | YES | 75 | PRECAUTIONARY | 15 |  | 732780 | 2004-08-23 | 187.5 | 200 | YES | NO | NO | NO | NO | NO | STEVE TROCH | 4104709560 | STEVE.TROCH@BGE.COM | TRANSMISSION | BODY OF PIPE |  | STEEL |  | NO | NO | NO |  |  | 1949 | 26 | 0.25 | ATSM A 139-46 B | 35000 | EFW BUTT WELD |  | UNKNOWN |  | UNDER GROUND |  | 36 | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [16 empty] | GOVERNMENT | WATER |  | YES | 7 | 27 | 2004 | ONE-CALL SYSTEM | YES | PAINT | YES | ACCURATE | YES | [36 empty] | ON AUGUST 23, 2004, AT APPROXIMATELY 1:30 PM, AN EXCAVATOR WORKING TO INSTALL A NEW 42 INCH WATER LINE IN THE 1100 BLOCK OF COOKS LANE IN BALTIMORE CITY, STRUCK A BALTIMORE GAS AND ELECTRIC COMPANY (BGE) 26” NATURAL GAS PIPELINE WITH A HIGHHOE BUCKET. THE STRIKE PRODUCED A HOLE APPROXIMATELY 4” BY 6” IN THE MAIN RESULTING IN THE RELEASE OF NATURAL GAS. THIS INCIDENT RESULTED IN THE EVACUATION OF MORE THAN 20 HOMES IN THE 1000 AND 1100 BLOCKS OF COOKS LANE AND THE 1100 BLOCK OF WEDGEWOOD ROAD. BGE HAD TO SHUT OFF ELECTRICITY TO APPROXIMATELY 1500 HOMES WHEN THEY DE-ENERGIZED THE FEEDER THAT WAS NEARLY DIRECTLY OVER THE STRIKE (FOR SAFETY). BGE MET WITH CONTRACTOR REPRESENTATIVES AND THE BALTIMORE CITY PUBLIC WORKS DEPARTMENT AT THE WORK SITE SEVERAL TIMES (ON AUGUST 16,17 AND 18) PRIOR TO THE INCIDENT. THE MARKINGS OF EACH UTILITY’S UNDERGROUND FACILITIES MET ALL THE REQUIREMENTS OF THE MARYLAND PUBLIC UTILITY ARTICLE (PUC), § 12-110. FURTHER, BGE REQUESTED THAT IT BE NOTIFIED BEFORE ANY EXCAVATION TOOK PLACE NEAR THE NATURAL GAS TRANSMISSION LINE. THE CONTRACTOR DID NOT NOTIFY BGE OF THEIR INTENT TO START EVACUATION OF THE SITE ON AUGUST 23. * NOTE: THIS REPORT IS A REPLACEMENT TO THE ORIGINAL REPORT SUBMITTED IN 2004. THE ORIGINAL REPORT WAS INCORRECTLY SUBMITTED AS A DISTRIBUTION INCIDENT, HOWEVER THE INCIDENT ACTUALLY OCCURRED ON A TRANSMISSION MAIN. OTHER THAN THE RECLASSIFICATION FROM DISTRIBUTION TO TRANSMISSION ALL THE INFORMATION ON THE THIS INCIDENT REMAINS THE SAME, NO DETAILS HAVE BEEN CHANGED. THIS RECLASSIFIED REPORT WAS APPROVED AND SIGNED IN MAY, 2013 BUT WILL REMAIN AS A 2004 TRANSMISSION INCIDENT REPORT.